## Sheet1
COMMISSIONING CHLORINATION RECORD
PROJECT NUMBER: |  |  |  | TESTING COMPANY:
LOCATION:
CONTRACTOR:
INSPECTOR:
DATE CHLORINATED: |  |  |  | DATE OF DECHLORINATION:
DISINFECTION METHOD:
TABLET OR CONTINOUS FEED
SLUG
SPRAY
RESIDUALS AT SOURCE PRIOR TO FLUSHING: |  |  |  | Total Cl1 : |  |  | Free Cl2 :
SOURCE LOCATION:
SAMPLE POINT |  |  | CHLORINATED |  | 24 HR CONTACT |  | POST CT FLUSH (mg/L) |  |  | POST 16HR CL2 (mg/L)
|  |  | TIME | Cl2 | TIME | Cl2 | TIME | TOTAL Cl1 | FREE Cl2 | TIME | FREE Cl2
MOECC: Chlorine Concentrations and Contact Times for New Watermains
Disinfection Method |  | Minimum Contact Time |  | Initial Chlorine Concentration |  |  |  | Maximum Allowable Decrease in Chlorine Concentration
Tablet or Continuous Feed |  | 24 hours |  | ≥ 25 mg/L |  |  |  | 40% of the Initial Chlorine Concentration to a Maximum of 50 mg/L
Slug |  | 3 hours |  | ≥ 100 mg/L |  |  |  | 25 mg/L
Spray |  | 30 minutes |  | ≥ 200 mg/L |  |  |  | Measurement Not Required
Note: This form is to be scanned and placed into the corresponding Project file folder