Regional Municipality of Halton

SCADA Standards Manual

Section 2 Tagname Convention

SCADA STANDARDS 2022

Table of Contents

SECTION 2 Tagname Convention	1

2.1	Intent of this Section	1

2.2	Equipment Coding System Fragments and Fragment Separators	1

2.3	Equipment Coding System for Treatment Plants	1

Drawing Generation	2

HMI and PLC Program Tag Generation	3

2.4	Equipment Coding System for Remote Water & Wastewater Facilities	3

2.5	Fragment Six	5

2.6	Tagname Convention Identification Codes	5

2.7	Alarm and Events Strategy	5

Fragment 4,5 - SCADA	6

Fragment 4, 5 – Priorities Waste	6

Fragment 4, 5 – Priorities Water	7

Appendix A – Tagname Convention	8

List of Tables

Table 2.1	Tagname Structure	1

Table 2.2	Example of Plant Device Tag	2

Table 2.3	Example of Plant Instrument Tag	2

Table 2.4	Example of Plant Signal Tag	3

Table 2.5	Example Tag for Equipment with No Subset	3

Table 2.6	Example Control Signal Tag	3

Table 2.7	Equipment Tag for Water and Wastewater Pumping Stations	3

Table 2.8	Example Wastewater Pumping Station Pump Motor Tag	4

Table 2.9	Example Booster Station Pump Tag with No Equipment Subset	4

Table 2.10	Example Loop Drawing Tag	5

Table 2.11	Example Fragment Seven Tags	5

# Tagname Convention

## Intent of this Section

#### The intent of this section is to present Halton Region’s tagname convention.  This section should be read by PLC and HMI programmers and those that will be identifying major pieces of equipment on the drawings.

#### Halton Region’s equipment coding system has 2 major functions. The first one is for the generation of equipment identification tags on the drawings. The second one is for the creation of PLC program and HMI tags.

#### All pieces of equipment that will have SCADA tags associated with them must be shown on a P&ID drawing. The equipment must have a tag based on this tagname convention. The tag can be used on any of the drawings to identify the piece of equipment.

#### Field wire labeling does not use the tagging system described in this section. Field wire labeling is presented in Section 3 Control Panel Design and on the loop drawings.

#### If a programmer needs to develop a tag that has codes that are not defined in the SCADA Standards, then the programmer is to contact the Region’s SCADA group and request that a new tag fragment be created and added to the SCADA Standards.

#### If the Consultant determines that Fragment 4 or any other fragment does not apply they must use “000” as a place holder instead of skipping the fragment.

## Equipment Coding System Fragments and Fragment Separators

#### Halton Region’s equipment coding system is used to generate tagnames that are used inside the PLC programs and the HMI software programs.

#### The tagnames are generated by assembling a series of codes that are sorted into fragments. Those fragments are then combined in a logical hierarchical order to make a tagname.

#### Each fragment is separated by an underscore “_”.

## Equipment Coding System for Treatment Plants

#### For information on the equipment coding system for Remote Sites see Section 2.4.

#### The HMI and PLC programming tag coding system used in Halton Region consists of six "fragments" of information.

#### The equipment tagname consists of up to three fragments; the first three fragments represent the device; the last three fragments represent SCADA details.

#### The typical structure of the tagname is as follows:

| FRAGM’T 1 | FRAGM’T 2 | FRAGM’T 3 | FRAGM’T 4 | FRAGM’T 5 | FRAGM’T 6 |
| --- | --- | --- | --- | --- | --- |
| ACC | CCCCOO | CCCOO | AA | CO | AA |

- Tagname Structure

Where:

###### A	Denotes Alpha (Letter)

###### B	Denotes Numeric (Number)

###### C	Denotes Character (Either alpha or numeric)

###### O	Denotes an optional character to be used as required but it is not mandatory

and where:

###### Fragment 1- Represents the Plant AND the process area by one (1) alpha characters followed by 2 alpha or numeric characters.

###### Fragment 2 - Identifies main equipment and is represented by anywhere from 4 to 6 alpha or numeric characters.

###### Fragment 3 - Identifies a subset of main equipment and is represented by three (3) to five (5) characters. If the signal is related to the main equipment, then “000” is used.

###### Fragment 4 - For PLC database and HMI tags and loop drawings are as follows:

            - Digital Input (status)		DI

            - Digital Input (alarm)		DA

            - Digital Output			PB

            - Analog Input 			AI

            - Analog Output			AO

###### Fragment 5 - Identifies signal type and is represented by two (2) characters.

###### Fragment 6 - Is only used for Alarm enablement and disablement and stand-alone digital alarm inputs – refer to Section 2.5 for details.  In all other cases this is not used.

### Drawing Generation

#### When identifying equipment on drawings, only the first 2 or 3 fragments are to be used as required. If the piece of equipment can be identified with only 2 fragments, then the third fragment can be left off the drawing.

#### An example of a major piece of equipment that can be identified with 2 fragments is High Lift Pump 1 at the Burlington Water Plant is shown below. The tagname is "BWJ_HLP1" which is as follows:

| FRAGMENT 1 | FRAGMENT 2 | FRAGMENT 3 |
| --- | --- | --- |
| ACC | CCCCOO | CCCOO |
| BWJ | HLP1 | Blank |
| Burlington Water Purification Plant High Lift Pump 1 | High Lift Pump No.1 |  |

- Example of Plant Device Tag

#### An example of a major piece of equipment that can be identified with 3 fragments is the flow meter associated with Primary Clarification Raw Sludge Pump 1 at the Oakville South East Plant which is shown below. The tagname is "SEE_RSP1_FI1" which is as follows:

| FRAGMENT 1 | FRAGMENT 2 | FRAGMENT 3 |
| --- | --- | --- |
| ACC | CCCCOO | CCCOO |
| SEE | RSP1 | FI1 |
| Oakville Southeast Wastewater Treatment Plant Raw Sludge Pumping Area | Raw Sludge Pump No.1 | Flow Instrument No. 1 |

- Example of Plant Instrument Tag

### HMI and PLC Program Tag Generation

#### For PLC Program and HMI tags, the temperature alarm associated with High Lift Pump 1 at the Burlington Water Plant may be shown as "BWJ_HLP1_DM1_DA_TA” which is represented by the five fragments as follows:

| FRAGM’T 1 | FRAGM’T 2 | FRAGM’T 3 | FRAGM’T 4 | FRAGM’T 5 |
| --- | --- | --- | --- | --- |
| ACC | CCCCOO | CCCOO | AA | CCO |
| BWJ | HLP1 | DM1 | DA | TA |
| Burlington Water Purification Plant High Lift Area | High Lift Pump No.1 | Drive Motor 1 of HLP1 | Digital Input Alarm | Temperature Alarm |

- Example of Plant Signal Tag

#### For PLC Program and HMI tags; the following examples are for an aeration tank 3 at Mid-Halton that has multiple D.O. sensors in the same tank. This is an example where fragment 3 would use the third or fourth character as a number.

| FRAGM’T 1 | FRAGM’T 2 | FRAGM’T 3 | FRAGM’T 4 | FRAGM’T 5 |
| --- | --- | --- | --- | --- |
| ACC | CCCCOO | CCCOO | AA | CCO |
| MHI | ATK3 | OX1 | AI | CV |
| MHI | ATK3 | OX2 | AI | CV |
| Mid-Halton WWTP Aeration Area | Aeration Tank No.3 | Dissolved Oxygen Sensor 1 &2 | Analog Input | Current Value |

#### For HMI tags, the equipment tagname "OWJ_HLP1" may have a raw digital input signal represented by "OWJ_HLP1_000_DA_GA” and the five fragments are then as follows:

| FRAGM’T 1 | FRAGM’T 2 | FRAGM’T 3 | FRAGM’T 4 | FRAGM’T 5 |
| --- | --- | --- | --- | --- |
| ACC | CCCCOO | CCCOO | AA | CCO |
| OWJ | HLP1 | 000 | DA | GA |
| Oakville Water Purification Plant High Lift Area | High Lift Pump No.1 | NONE | Digital Input Alarm | General Alarm |

- Example Tag for Equipment with No Subset

#### Or an analog control signal which is represented by "OWJ_HLP1_DV1_AO_CT":

| FRAGM’T 1 | FRAGM’T 2 | FRAGM’T 3 | FRAGM’T 4 | FRAGM’T 5 |
| --- | --- | --- | --- | --- |
| ACC | CCCCOO | CCCOO | AA | CCO |
| OWJ | HLP1 | DV1 | AO | CT |
| Oakville Water Purification Plant | High Lift Pump No.1 | Discharge Valve 1 | Analog Output | Setpoint (4-20mA analog signal) |

- Example Control Signal Tag

#### Or an stand-alone discrete alarm which is represented by "OWJ_STN1_CP1_DA_JR":

| FRAGM’T 1 | FRAGM’T 2 | FRAGM’T 3 | FRAGM’T 4 | FRAGM’T 5 |
| --- | --- | --- | --- | --- |
| ACC | CCCCOO | CCCOO | AA | CCO |
| OWJ | STN | CP1 | DA | JR |
| Oakville Water Purification Plant Highlift | Station | Control Panel | Digital Input Alarm | Power Failed |

- Example Control Signal Tag

## Equipment Coding System for Remote Water & Wastewater Facilities

#### The equipment tagname for remote water and wastewater facilities is similar to the plant except for a minor difference.  At remote facilities, there is not process area so Fragment 1 only represents the facility. The tag is then composed of the 6 (six) basic fragments. Note that the sixth fragment is only used if the tag has alarm enable/disable functionality associated with it.

| FRAGM’T 1 | FRAGM’T 2 | FRAGM’T 3 | FRAGM’T 4 | FRAGM’T 5 | FRAGM’T 6 |
| --- | --- | --- | --- | --- | --- |
| ACC | CCCCOO | CCCOO | AA | CCO | AA |

- Equipment Tag for Water and Wastewater Pumping Stations

Where:

###### A 	Denotes Alpha (Letter)

###### B	Denotes Numeric (Number)

###### C	Denotes Character (Alpha or Numeric)

###### O	Denotes an optional character to be used as required but it is not mandatory

And where:

###### Fragment 1 - Represents a water or wastewater pumping station or remote facility and has a three (3) character tagname.  Water remote facilities are represented by three (3) alpha characters.  Wastewater pumping stations are represented by a leading alpha character followed by two (2) numeric characters. Also included in this are PRV locations and leachate pumping stations at closed landfill sites.

###### Fragment 2 - Identifies main equipment and is represented by anywhere from 4 to 6 alpha or numeric characters.

###### Fragment 3 - Identifies subset of main equipment and is represented by three (3) to five (5) characters. If there is no subset, then “000” is used.

###### Fragment 4 – Is used for the PLC database and HMI tags as follows:

            - Digital Input (status)		DI

            - Digital Input (alarm)		DA

            - Digital Output			PB

            - Analog Input (status)		AI

            - Analog Output			AO

###### Fragment 5 - Identifies signal type and is represented by two characters.

###### Fragment 6 - Is only used for Alarm enablement and disablement – refer to Section 2.5 for details.  In all other cases fragment 6 is not used.

#### When developing equipment tags for remote water and wastewater facilities, the same rules apply as plants.

#### Example of a drive motor in a wastewater pumping station and the tagname is "B01_SLP1_DM1" where:

| FRAGMENT 1 | FRAGMENT 2 | FRAGMENT 3 |
| --- | --- | --- |
| ACC | CCCCOO | CCCOO |
| B01 | SLP1 | DM1 |
| Junction St. Pumping Station | Sewage Lift Pump No.1 | Drive Motor No. 1 |

- Example Wastewater Pumping Station Pump Motor Tag

#### Another example of a UPS in a water pumping station which has no subset equipment "DRB_UPS1_000" is as follows:

| FRAGMENT 1 | FRAGMENT 2 | FRAGMENT 3 |
| --- | --- | --- |
| ACC | CCCCCC | CCCOO |
| DRB | HBP1 | 000 |
| Davis Road Booster Pumping Station | UPS No.1 | NONE |

- Example Booster Station Pump Tag with No Equipment Subset

#### An example of HMI tag is "DRB_HBP1_00_DA_GA" which is represented by the five fragments as follows:

| FRAGMENT 1 | FRAGMENT 2 | FRAGMENT 3 | FRAGMENT 4 | FRAGMENT 5 |
| --- | --- | --- | --- | --- |
| ACC | CCCCOO | CCCOO | AA | CCO |
| DRB | HBP1 | DM1 | DA | GA |
| Davis Road Booster Pumping Station | High Lift Booster Pump No.1 | Main Equipment | Digital Input Alarm | General Alarm |

- Example Loop Drawing Tag

## Fragment Six

#### Fragment Six has been created specifically for HMI enabling and disabling of Raw and Autodialer alarms.

#### This fragment is for SCADA only and does not appear on drawings.

#### A specific window has been developed that allow users to enable and disable Raw and Autodialer alarms.

#### Fragment Six is appended to the equipment alarm tag with either a RE or DE.

#### As an example the Davis Road High Lift Booster Pump No. 1 General Alarm Raw and Dialer Alarm tags are:

| FRAGM’T 1 | FRAGM’T 2 | FRAGM’T 3 | FRAGM’T 4 | FRAGM’T 5 | FRAGM’T 6 |
| --- | --- | --- | --- | --- | --- |
| ACC | CCCCOO | CCCOO | AA | CCO | AA |
| DRB | HBP1 | DM1 | PB | GA | _RE |
| Davis Road Booster Pumping Station | High Lift Booster Pump No.1 | Drive Motor No.1 | Push Button From HMI | General Alarm | Raw Alarm Enable |
| DRB | HBP1 | DM1 | PB | GA | DE |
| Davis Road Booster Pumping Station | High Lift Booster Pump No.1 | Drive Motor No.1 | Push Button From HMI | General Alarm | Autodialer Alarm Enable |

- Example Fragment Seven Tags

## Tagname Convention Identification Codes

#### The Tagname Convention identification codes are presented in Appendix 2A as an Excel file.

#### For ease of tag creation, the fragments have been broken into separate worksheet tabs.

#### No new codes or fragments should be developed without the involvement of Halton Region.

## Alarm and Events Strategy

#### To assist Consultants in the proper assignment of Alarm and Event priorities, Fragments 4 and 5 in Halton SCADA Tagname Convention provides specific instructions on how to assign tag alarming and logging properties. This is covered over three (3) worksheets in the Excel file; Fragment 4,5 -  SCADA, Fragment 4,5 - Priorities Waste and Fragment 4,5 - Priorities Water.

### Fragment 4,5 - SCADA

#### The first and second columns are for fragment 4.  The first column indicates the tag type.  The second column indicates the fragment 4 code.

#### The third and forth columns are for fragment 5.  The third column contains the description for the fragment 5 description.  The fourth contains the fragment 5 code.

#### The fifth column indicates if “log events” should be checked off in the tag properties.  A “” indicates that the Consultant is required to “check” the “Log Events” field when creating the tag.  “Uncheck” indicates the Consultant is to leave the field “unchecked” when creating the tag.

#### The sixth column indicates the Alarm state, which is selected when creating the tag.  Tags can have one of three states, “On”, “Off” and “None.” All alarms must have a state of “On” Halton does not allow alarms with a state of “Off”. To maintain consistency, the manipulation of alarms states is always done in the PLC.  A state of “On” indicates that the tag is in its alarm state when the tag is true.  A tag with an alarm state of “None” indicates that the tag does not have an alarm state.

#### The last column indicates if the tag is logged by the Wonderware Historians. A “” indicates that the Consultant is required to “check” the “Log Data” field when creating the tag.  “Uncheck” indicates the Consultant is to leave the field “unchecked” when creating the tag.

#### In some cases, the “Log Data” column for a few digital inputs indicates “Variable.”  This indicates that some status such as “Running,” or “Opened,” or “Closed” needs to be logged but other statuses do not require to be logged.

#### When “Variable” appears, consultants should review all I/O related for the device.  The Consultant should create all of the tags for the device with their recommendation on which events should be logged and which should not.  The Consultant should contact the SCADA group through the use of a Standards deviation memo and submit a CSV containing the device tags they have created with the memo.  The SCADA group will review the Consultants recommended tags, and provide feedback.

### Fragment 4, 5 – Priorities Waste

#### The first column indicates the tag type.

#### The second column indicates the fragment 5 description.

#### The third column indicates the priority the event should be logged at.  If the field indicates “N/A” it indicates “Not Applicable” and the tag is not set as a logged event.

#### The fourth column indicates the alarm priority.  A priority of N/A indicates that the tag has an alarm state of “None.”  Wonderware reports alarms of the lowest priority first.  For Wastewater applications, alarming tags with a priority of 1 – 10 are considered Critical Alarms, and generate the Critical Alarm Notice.  Consultants should refer to Section 6, Critical Alarms Notification for more information on Critical Alarming.

### Fragment 4, 5 – Priorities Water

#### The first column indicates the severity of the tag. There are three (3) levels of severity; Non-Critical, Critical Non-Compliance and Critical Compliance. The severity of a signal is specific to individual instance.

#### The second column indicates the type or category of the signal.

#### The third column indicates the priority the event should be logged at.  If the field indicates “N/A” it indicates “Not Applicable” and the tag is not set as a logged event.

#### The fourth column indicates the alarm priority.  A priority of N/A indicates that the tag has an alarm state of “None.”  Wonderware reports alarms of the lowest priority first.  For Water applications, alarming tags with a priority of 1 – 99 are considered Critical Alarms, and generate the Critical Alarm Notice.  Consultants should refer to Section 6, Critical Alarms Notification for more information on Critical Alarming.

#### When Consultants identify tags that do not have Critical Alarming priorities and recommend the priority be Critical, the Consultant is required to contact the SCADA group using the Standards Deviation Memo.

## Appendix A – Tagname Convention

| # | Document Name |
| --- | --- |
| 1 | Halton SCADA Tagname Convention |
| 2 |  |
| 3 |  |
| 4 |  |