## Fragment 1 - Plants & Aggregrat
WASTEWATER TREATMENT PLANTS - FRAGMENT 1 CODES
PROCESS AREA | CODE | Burlington WWTP | Oakville Southwest WWTP | Mid-Halton WWTP | Oakville Southeast WWTP | Georgetown WWTP | Acton WWTP | Milton WWTP
Pumping Station | A,B | BSA, BSB | SWA, SWB | MHA, MHB | SEA, SEB | GSA, GSB | ASA, ASB | MSA, MSB
Inlet | C,D | BSC, BSD | SWC, SWD | MHC, MHD | SEC, SED | GSC, GSD | ASC, ASD | MSC, MSD
Primary Clarifier | E,F,G,H | BSE, BSF, BSG, BSH | SWE, SWF, SWG, SWH | MHE, MHF, MHG, MHH | SEE, SEF, SEG, SEH | GSE, GSF, GSG, GSH | ASE, ASF, ASG, ASH | MSE, MSF, MSG, MSH
Aeration | I,J,K,L | BSI, BSJ, BSK, BSL | SWI, SWJ, SWK, SWL | MHI, MHJ, MHK, MHL | SEI, SEJ, SEK, SEL | GSI, GSJ, GSK, GSL | ASI, ASJ, ASK, ASL | MSI, MSJ, MSK, MSL
Final Clarifier | M,N,O,P | BSM, BSN, BSO, BSP | SWM, SWN, SWO, SWP | MHM, MHN, MHO, MHP | SEM, SEN, SEO, SEP | GSM, GSN, GSO, GSP | ASM, ASN, ASO, ASP | MSM, MSN, MSO, MSP
Chemical | Q,R | BSQ, BSR | SWQ, SWR | MHQ, MHR | SEQ, SER | GSQ, GSR | ASQ, ASR | MSQ, MSR
Digester | S,T | BSS, BST | SWS, SWT | MHS, MHT | SES, SET | GSS, GST | ASS, AST | MSS, MST
Solids Handling | U | BSU | SWU | MHU | SEU | GSU | ASU | MSU
Tertiary | V | BSV | SWV | MHV | SEV | GSV | ASV | MSV
Effluent Disinfection | W | BSW | SWW | MHW | SEW | GSW | ASW | MSW
Adminstration | X | BSX | SWX | MHX | SEX | GSX | ASX | MSX
General | Y | BSY | SWY | MHY | SEY | GSY | ASY | MSY
Energy Centre | Z | BSZ | SWZ | MHZ | SEZ | GSZ | ASZ | MSZ
WATER TREATMENT PLANTS - FRAGMENT 1 CODES
PROCESS AREA | CODE | Burlington WTP | Oakville WTP | Burloak WTP | Georgetown WTP | Prospect Park WTP | Kelso WTP
Low Lift | A,B | BWA, BWB | OWA, OWB | BLA, BLB | GWA, GWB | PWA, PWB | KWA, KWB
Chemical | C,D,E | BWC, BWD, BWE | OWC, OWD, OWE | BLC, BLD, BLE | GWC, GWD, GWE | PWC, PWD, PWE | KWC, KWD, KWE
Filtration/Membranes | F,G,H,I | BWF, BWG, BWH, BWI | OWF, OWG, OWH, OWI | BLF, BLG, BLH, BLI | GWF, GWG, GWH, GWI | PWF, PWP, PWH, PWI | KWF, KWK, KWH, KWI
High Lift | J,K | BWJ, BWK | OWJ, OWK | BLJ, BLK | GWJ, GWK | PWJ, PWK | KWJ, KWK
Clearwell | L,M | BWL, BWM | OWL, OWM | BLL, BLM | GWL, GWM | PWL, PWM | KWL, KWM
Sedimentation/Floculation | N,O | BWN, BWO | OWN, OWO | BLN, BLO | GWN, GWO | PWN, PWO | KWN, KWO
Waste Handling | P | BWP, | OWP, | BLP, | GWP, | PWP, | KWP,
Uv Disinfection | T | BWT, | OWT, | BLT, | GWT, | PWT, | KWT,
Ozone | W | BWW, | OWW, | BLW, | GWW, | PWW, | KWW,
Administration | X | BWX, | OWX, | BLX, | GWX, | PWX, | KWX,
General | Y | BWY, | OWY, | BLY, | GWY, | PWY, | KWY,
Energy Centre | Z | BWZ, | OWZ, | BLZ, | GWZ, | PWZ, | KWZ,
Geographical Aggregations |  |  | W.A. Johnson Biosolids Facility - FRAGMENT 1
Burlington | BTN |  | Centrate Pumping | BFA
Oakville | OKV |  | Sludge Storage | BFS
Milton | MTN |  | Solids Handling | BFU
Halton Hills | HHL
Georgetown | GTN
Acton | ATN
South | STH
North | NTH
Halton Region | HAL
Global | GLB

## Fragment 1 - Remotes
TABLE 2A-1.1 FRAGMENT ONE REMOTES
SKYWAY WWTP | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Lakeshore Road, Junction St. | B01 | Junction St PS
Danforth Place | B03 | Danforth PS
Lasalle Park | B04 | Lasalle Park PS
North Shore Blvd., Stn. 5 | B05 | North Shore Blvd Stn PS
Lakeshore Road, Stn. 6 | B06 | Bromley Park PS
Indian Road | B07 | Indian Road PS
Elizabeth Gardens | B08 | Elizabeth PS
Lakeshore Road, Stn. 9 | B09 | Roseland Creek PS
Lakeshore Road, Stn. 10 | B10 | Paletta Gardens PS
Bellview Street | B11 | Bellview Street PS
Edgewater Cresesent | B12 | Edgewater Crescent PS
Cardinal | B13 | Cardinal Avenue PS
North Shore Blvd., Stn. 14 | B14 | Stillwater Crescent PS
Unsworth Avenue | B15 | Unsworth Avenue PS
Stillwater Cresent | B16 | Stillwater Crescent PS
Appleby Place | B17 | Appleby Place PS
Bayshore Blvd | B18 | Bayshore Bourlevard PS
Grand View Avenue | B19 | Grandview Avenue PS
Spring Garden Road, Stn 20 | B20 | Spring Garden Road PS
Pinedale Stn. 21 (New St) | B21 | Pinedale PS
Oakland (Park Dr) | B22 | Oaklands Park PS
Bridgeview | B23 | Bridgeview PS | Listed as Pump Station 24 in GIS and P.S. website
Garden Trails | B24 | Garden Trails PS
Appleby Line Stormwater PS | B25 | Not on Lito's list as of Dec 2019
Fairview Stormwater Ps | B26 | Not on Lito's list as of Dec 2019
OAKVILLE SOUTH WEST WWTP | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
West River | W01 | West River PS
Bronte Yacht Club | W02 | Bronte Yacht Club PS
Marine Drive | W03 | Marine Drive PS
Sheldon Creek | W04 | Sheldon Creek PS
Timber Lane | W05 |  | Decommissioned
Belvedere Drive | W06 | Belvedere Drive PS
Stirling Drive | W07 | Stirling Drive PS
Westdale Drive | W08 | Westdale Road PS
Birch Hill Lane | W09 | Birch Hill Lane PS
Lakewood Drive | W10 | Laekwood Drive PS
Forsyth Drive | W11 |  | Decommissioned
Walker Street | W12 | Walker Street PS
Water Street | W13 | Water Street PS
Riverside Drive | W14 | Riverside Drive PS
Shepherd Road (Queenmary St) | W15 | Shepherd Road PS
Hixon Street | W16 | Hixon Street PS
Coronation Park | W17 | Coronation Park PS
Lakeshore Road Stn. 18 | W18 |  | Decommissioned - Raw sewage pumping is now part of the plant and not conidered a pump station
Rebecca Street 4 Th Line Bypass | W19 | Not on Lito's list as of Dec 2019
Rebecca Street Storm Retention Tank | W20 | Not on Lito's list as of Dec 2019
Shorewood Place | W21 | Not on Lito's list as of Dec 2019
OAKVILLE SOUTH EAST WWTP | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Navy Street | E01 | Navy Street PS
First Street | E02 | First Street PS
Raymar Place | E03 | Raymar Place PS
Chartwell Road | E04 | Chartwell Road PS
Argyle Drive | E05 | Argyle Drive PS
Bel Air Drive | E06 | Bel Air Estates PS
Gairlock Gardens | E07 | Garilock Gardens PS
Ennisclare Drive | E08 | Ennisclaire Drive PS
Lakeshore Road Stn. 9 (Ninth Line) | E09 | Ninth Line PS | Part of the South East Plant's application
Chancery Lane | E10 | Chancery Lane PS
Carrington Drive | E11 | Carrington Place PS
Cedarberry Drive | E12 | Cedarberry Court PS
Weaver Ave. | E13 | Weaver Avenue PS
Cumnock Crescent | E14 | Cumnock Crescent PS
Morrison Heights | E15 | Morrison Heights PS
Rock Point Drive (Joshua Creek) | E16 | Joshua Creek PS
MID-HALTON WWTP | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Third Line | H01 | Third Line PS
North Service Road Stn. 2 (North Pump Stn) | H02 | North Service Road PS
Overton Place | H03 | Overton Place PS
Winding Woods Drive (River Oaks) | H04 |  | Decommissioned
Sixteen Mile Creek (Upper Middle Rd) | H05 | Sixteen Mile Creek PS
River Bank Way | H06 | River Bank Way PS
| H07 |  | Nothing Assigned
Providence Road | H08 | Providence Road PS
Dundas Pump Station (Formerly the Boyne PS) | H09 | Dundas Pump Station | In order to align with Waste Collections ECA and the the SAP database, the North Oakville East WWPS was renamed to the Dundas Pump Station and the SCADA tag was changed to H09
Mid-Block | H10 | MidBlock PS | The facility ID on Lito's list is M-2
Do not use in order to align with SAP | H11 | Do not use
Dundas East Pump Station | H12 | Dundas East PS
ACTON | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Agnes Street | A01 | Agnes Street PS
Lakeview (Elizabeth) | A02 | Lakeview PS
Kingham Hill | A03 | Kingham PS
GEORGETOWN | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Armstrong Avenue | G01 | Armstrong Ave PS
John Street | G02 | Norval PS
Lynden Circle | G03 | Lynden Circle PS
Park Lane (Gardiner Cr) | G04 | Gardiner Drive PS
Cinderbarke Terrace | G05 | Cinderbarke Terrace PS
Moore Park Cres | G06 | Moore Park PS
Gollop Cres | G07 | Gollop Crescent PS
Mccullough Cres (Banting St) | G08 |  | Decommissioned
Main Street | G09 | Main Street PS
Norval | G10 | Norval PS
Robinson Road | G11 |  | Decommissioned
Ten Side Road | G12 | 10 Side PS
Glen Williams | G13 | Glen Williams PS
Double 10 | G14 | Double Ten PS
Mountainvew Road | G15 | TBD | This is the station that will remain at the current site of the Georgetown WWTP once the plant is closed
MILTON | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Laurier | M01 | Laurier Avenue PS
Halton Hills Pump Station #1 | M02 | Halton Hills #1 PS | The facility ID on Lito's list is M-4
Halton Hills Pump Station #2 | M03 | Halton Hills #2 PS | The facility ID on Lito's list is M-5
M04
M05
Tremaine Road | M06 | Tremaine Road PS
Halton Hills #3 | M07 | Halton Hills #3 PS
James Snow Parkway Storm Water | M08 | James Snow Parkway Storm Water
Britannia Pump Station | M09 | Not on Lito's list as of Dec 2019
Derry Road Grade Separation | M10 | Not on Lito's list as of Dec 2019
Fulton Pump Station | M11 | Fulton ST PS | This has become part of wasetwater collections since the Milton WWTP is closed
Place holder to align Drumquin with SAP | M12
Place holder to align Drumquin with SAP | M13
Drumquin Pumping Station | M14 | Not on Lito's list as of Dec 2019
WATER DISTRIBUTION OAKVILLE | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Davis Road | DRB
Eighth Line Booster Stn | ELS
Eighth Line Reservoir | ELR | Eighth Line Glenashton RBS
Zone 4 Booster Stn. (8Th Line) | ZBS
Mccraney Dr. | MCR
Moore Res. (6Th Line) | MOR
Upper Middle Road | UMR | Kitchen RBS
Bronte Crossing Valve Chamber | BCV |  | Bronte Creek Crossing on Rebecca
Dundas Crossing Valve Chamber #2 | BC2 |  | Bronte Creek Crossing on Dundas
Hazel McClary | HMV |  | PRV Chamber
Ninth Line | NLV | Joshua Creek | PRV Chamber
Bulk Water - Trafalger Road | TRM
Royal Windsor Drive | RWV |  | PRV Chamber
Prince John Circle | PJV |  | PRV Chamber
Burnhamthorpe Rd Tower | BDT | Burnhamthorpe Tower
Neyagawa Zone 4 Pumping Station | NPB | Neyagawa BS
Zone 1 Watermain Valve House | Z1B
North Park PRV | N1V |  | PRV Chamber in front of Neyagawa Pump Station
Settelers Rd PRV | N3V |  | PRV Chamber on Settelers Road west of Neyagawa
Burnhamthorpe PRV | N4V |  | PRV Chamber on Neyagawa south of Burnhamthorpe
Trafalgar PRV | N2V |  | PRV Chamber at corner of Burnhamthorpe and Trafalgar
WATE DISTRIBUTION BURLINGTON | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Bailie | BAS | Bailie RBS
Washburn | WBS | Washburn RBS
Beaufort | BES | Beaufort RBS
Mount Forest | MFS | Mt. Forest RBS | Being decommisioned in 2020
Brant St. | BRS | Brant St. RBS
Tyandaga | TYS | Tyandaga RBS
Waterdown Road | WDS | Waterdown Reservoir
Kingsway Drive | KIB | Kingsway BS
Headon Reservoir | HER | Headon Reservoir
Appleby Line Reservoir and Pumping Station | ALR | Appleby Line RBS
Appleby Line PRV | ALV |  | At the corner of Appleby Line and Upper Middle Road
Bulk Water - Plains Road | PRM
Bulk Water - Guelph Line | GLM
WATER DISTRIBUTION MILTON | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Walkers Line Well | WL1 | Walkers Line Wells
Walkers Line Well | WL2 |  | Decommissioned
Kelso Well | KE3 | Kelso WPP | Wrong section this is now in the water plants section
Kelso Well | KE4
Kelso Well | KE5
Kelso Well | KE6
Kelso Pumping Station | KES
Main Street Reservoir | MSR | Milton Reservoir
Twelve Side Road Reservoir | TSR | Milton Surge Tank
Steeles Ave Tower | SAT | Milton Tower
Zone 5 Reservoir | TLR | Third Line Reservoir
Fourth Line Zone 5 Pumping Station | FLB | Fourth Line BS
Nippising Road Coin St. | NRM |  | Decommissioned
Fifth Line Bulk Water Station | BWS
Ashgrove Reservoir and Booster Station | AGR | Not on Lito's list as of Dec 2019 | This is the code for the reservoir PLC
| AGB | Not on Lito's list as of Dec 2019 | This is the code for the booster station PLC
Britannia Road PRV | BAV |  | PRV Chamber
CAMPBELLVILLE WATER | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Campbellville Well | CB1 | Campbellville Wells
Campbellville Well | CB2 |  | Doesn't exist
GEORGETOWN WATER | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Cedarvale Park Well 1 | CV1 | Cedervale Well Field
Cedarvale Park Well | CV2 |  | Decommissioned
Cedarvale Park Well 3 | CV3
Cedarvale Park Well 4 | CV4
Cedarvale Park Well 4A | CV5
Princess Anne #5 | PA5 | Princess Anne Well Field
Princess Anne #6 | PA6
Tenth Line Well | TLW |  | Decommissioned
Lindsay Court Well | LCW | Linsday Court Wells
Moore Park Station | MPS | Moore Park BS
Norval Stand Pipe | NVT | Norval Stand Pipe
Todd Road Tower | TRT | Todd Road Tower
Creek Monitoring | CK1
Twenty Two Side Road Res. | TTR | 22nd SR Reservoir
Georgetown Bulk Water Station (Todd Rd) | TRM
ACTON WATER | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Hufnagel Well | HFW |  | Decommissioned
Davidson Well | DV1 | Davidson Well Field
Davidson UV 1 | DV2 |  | This fragment is used for WLP2 and UV1 the WLP2 needs to be changed to DV1
Davidson UV 2 | DV3
Waren Grove Well | WGW |  | Decommissioned
Fourth Line Well | FL1 | Fourth Line Well Field
Fourth Line Well UV 1 | FL2
Fourth Line Well UV 2 | FL3
Churchill Road Res. | CHR | Acton Reservoir
LANDFILL SITES | FRAGEMENT 1 | Official Name as of Dec 2019 | Comments
Highway #25 - Milton | MI1
Armstrong Ave. - Georgetown | AR1
Fourth Line - Oakville | FLO
Bayview West - Burlington | BVW
Bayview East - Burlington | BVE
North Service Road Burlington | NS1

## WData (hidden)
2026-07-30 08:48
TRUE
2026-07-30 08:48
6:00

## Fragment 2 - Major Equipment
TABLE 2A-2 FRAGMENT 2 MAJOR EQUIPMENT ALPHANUMERIC CODES
FRAGMENT 3 | DESCRIPTION
ACC | Accelator
ACE | Access Gallery
ACF | Actiflow Unit
ACH | Activated Carbon Header
ACT | Activated Carbon Storage Tank
AMB | Administration Building
ABL | Air Blower / Aeration Blower
ADC | Aeration Distribution Chamber
ATK | Aeration Tank
ATI | Aeration Tank Inlet (Gate)
ATR | Aeration Tank Return Sludge
AER | Aerator (Mechanical)
AGH | Agitator Head
ACP | Air Compressor
ACN | Air Conditioner
AIT | Air Cushion Tank
ARD | Air Diffuser
ADH | Air Discharge Header
AHU | Air Handling Unit
ARH | Air Heater
AIS | Air Intake System
ARS | Air Silencer
ASB | Air Scour Blower
ALD | Alarm Dialer
AFP | Alum Feed Pump
ALH | Alum Header
APD | Alum Pump Discharge
AST | Alum Storage Tank
ATA | Alum Tank Area
ATS | Automatic Transfer Switch
AMH | Ammonia Header
AMT | Ammonia Storage Tank
AMN | Ammoniator - Ammonia Injection Device
ANR | Analyzer
AUT | Autoclave
AWP | Acid Wash Pump
A1A | Aeration Tank 1 - Inlet Air
A2A | Aeration Tank 2 - Inlet Air
A1D | Aeration Tank 1 - Density
A2D | Aeration Tank 2 - Density
A1I | Aeration Tank 1 - Inlet Weir
A2I | Aeration Tank 2 - Inlet Weir
A1O | Aeration Tank 1 - Outlet Weir
A2O | Aeration Tank 2 - Outlet Weir
A1X | Aeration Tank 1 - Oxygen
A2X | Aeration Tank 2 - Oxygen
AVR | Automatic Voltage Regulator
BAR | Barminutor
BEP | Backwash Equalization Pump
BFP | Activated Carbon Feed Pump
BOS | Biofilter Odour Control System
BOC | Biofilter Odour Control System Cell
BLP | Biofilter Odour Control System Leachate Pump
BLE | Building Exterior Lights
BLR | Blender Or Boiler
BLS | Backup Level
BLI | Blender Inclinded Conveyor
BMS | Bottom Mixing System
BPA | Biosolids Processing Area
BPC | Bypass Controller
BPF | Bypass Flow
BPG | Bypass Gate
BPH | Bypass Header
BSR | Bar Screen Rake
BTS | Building Temperature Sensor/Switch
BWS | Backwash
BWH | Backwash Header
BWP | Backwash Pump
BWT | Backwash Equalization Tank
BWW | Backwash Wash Well
BWP1F1 | Backwash Pump 1, Filter 1
BWP1F2 | Backwash Pump 1, Filter 2
BWP2F1 | Backwash Pump 2, Filter 1 Etc.
BWP2F12 | Backwash Pump 2, Filter 12 (Used Only On Filters Higher Than #9)
CAH | Compressed Air Header
CAT | Current Tonner
CBL | Channel Blower
CCC | Chlorine Contact Chamber
CEN | Centrifuge
CEP | Centrifuge Feed Pump
CEV | Chlorine Evaporator
CFB | Chlorine Facilities Building
CFP | Chlorine Feed Pump
CGS | Chlorine Gas Scrubber
CHD | Chlorine Gas Detector
CHH | Chlorine Header
CHI | Chlorine Injector
CHL | Chlorinator
CHM | Chemical Mixer
CHR | Chlorine Room
CHS | Chlorine Seal
CLP | Cleaning Pump
CLW | Clearwell
CNP | Centrate Pump
COM | Comminutor
CPA | Chemical Pump Area
CPD | Chlorine Pump Discharge
CPP | Sludge Cake Pump
CPU | Server - Polling Node
CRA | Chlorine Residual Analyser
CRN | Crane
CSF | Cake Screw Feeder
CST | Chlorine Storage Tank
CTA | Chlorine Tank Area
CTM | Chemical Tank Mixer
CWA | Containment Wall Area
CWP | Cooling Water Pump
DEC | Decantor
DDT | Diesel Day Tank
DET | Detritor
DFP | Diesel Fuel Pump
DFT | Diesel Fuel Tank
DGD | Digester Gas Discharge
DGS | Digester Gas System
DHL | Dechlorinator
DHU | Dehumidifier
DIB | Digester Building
DIG | Digester
DIH | Discharge Header
DMX | Digested Mixer
DRN | Drain Pump
DTY | Duty Pump
DOR | Door
DSD | Digester Sludge Discharge
DSF | Door System Off
DSP | Digested Sludge Pump
DLR | Device Level Ring
DSO | Door System On
DST | Drainage Sump Tank
DVC | Division Chamber
DWL | Dry Well
DWP | Dewatering Pump
DWS | Dewatering Press
EBR | Emergency Breaker
ECB | Energy Center Building
EXF | Exhaust Fan
EFN | Electric Furnace
EGS | Exhaust Gas Scrubber
EGP | Exhaust Gas Plate Settler
EST | Exhaust Gas Scrubber Recycled Water Tank
ESP | Exhaust Gas Scrubber Recycled Water Pump
ENL | Entrance Lights
ELR | Electrical Room
ELT | Elevated Tank
EFV | Effluent Valve
ELV | Elevator
EXT | Expansion Tank
ETK | Equilization Tank
ETP | Equilization Tank Pump
ETM | Equilization Tank Mixer
EWD | Effluent Water Discharge
EWP | Effluent Water Pump
EWS | Effluent Water Strainer
EWW | Effluent Water Well
FAP | Fire Alarm Panel
FAN | Fan
FBH | Filter - Bypass Header
FCP | Ferric Chloride Pump
FCT | Ferric Chloride Storage Tank
FDD | Fluoride Detection Device
FDP | Footing Drain Pumps
FEC | Front End Controller
FEF | Final Effluent
FFP | Fluoride Feed Pump
FLG | Filter - Gravity
FHO | Fume Hood
FLH | Fluorine Header
FLN | Fluorinator
FLT | Floc Tank (Used For The Actiflow Untis At BWPP)
FMI | Flash Mixer
FLP | Filter - Pressure
FPP | Pressure Filter Feed Pump
FRP | Filtrate Pump
FSA | Fire/Smoke Alarm Switch
FST | Fluoride Storage Tank
FTP | Fuel Transfer Pump
FWL | Flushing Water Line
FWP | Flushing Water Pump
FWS | Flushing Water Strainer
FXB | Filter Building
FXP | Ferric Transfer Pump
FT1I | Floc Tank 1 - Inlet
FT2I | Floc Tank 2 - Inlet
FT1M | Floc Tank 1 - Mixer
FT2M | Floc Tank 2 - Mixer
FT1O | Floc Tank 1 - Outlet
FT2O | Floc Tank 2 - Outlet
GAG | Grit Tank Agitator
GBO | Gas Booster
GBP | Digester Gas Booster Pump
GCD | Gas Compressor Discharge
GCL | Grit Classifier
GCO | Grit Conveyor
GCP | Gas Compressor
GCS | Gas Compressor Suction
GDR | Grinder
GDS | Gas Detection System
GEN | Generator
GNR | Generator Room
GFR | Gas Furnace
GHP | Grit Tank Hopper
GHU | Glycol Heating Unit
GLP | Glycol Heating Unit Feed Pump
GOX | Gasous Oxygen
GRB | Grit Tank Air Blower
GRC | Gas Recirculating Compressor
GRP | Grit Pump
GRS | Grit Sequencer
GRT | Grit Tank
GRU | Gear Unit
GUS | Gas Utilization System
GWP | Ground Water Pump
G1A | Grit Tank 1 - Air Diffuser
G2A | Grit Tank 2 - Air Diffuser
G1C | Grit Tank 1 - Cross Collector
G2C | Grit Tank 2 - Cross Collector
G1F | Grit Tank 1 - Flyt Horizontal Collector
G2F | Grit Tank 2 - Flyt Horizontal Collector
G1S | Grit Tank 1 - Sweep Collector
G2S | Grit Tank 2 - Sweep Collector
HBP | High Lift Booster Pump
HCP | Hydraulic Cake Pump
HEX | Heat Exchanger
HFP | Hydrogen Peroxide Feed Pump
HLP | High Lift Pump
HLS | High Lift Suction Flume
HMD | Humidity
HPC | Hydrogen Peroxide Containment Area
HPL | Hot Plates
HPR | Hydrogen Peroxide
HPS | Hydrogen Peroxide System
HPU | Hudraulic Power Unit
HVC | Heating Ventillating And Air Conditining System
HWB | Hot Water Boiler
HWP | Hot Water Circulation Pump
HWR | Hot Water Return Line
HWS | Hot Water Supply Line
HWT | Hot Water Tank
HXS | Heat Exchanger - Sludge
HXW | Heat Exchanger - Water
H1I | Ozone Generator 1 Di Conductivity
H2I | Ozone Generator 2 Di Conductivity
H1O | Ozone Generatror 1 Di Cooling Water Temperature
H2O | Ozone Generatror 2 Di Cooling Water Temperature
ICP | Inlet Chamber
INF | Intake Fan
INC | Incubator
INT | Intake Gravity
INV | Inverter
IRP | Inlet Riser Pipe
IWB | Inlet Works Building
LAB | Laboratory
LAK | Lake
LLC | Low Water Level Cut Off Line (Piping)
LLP | Low Lift Pump
LSO | Lighting System On
LSF | Lighting System Off
SWS | Sewage Lift Station
LSS | Lime Storage Silo
LSC | Lime Storage Silo Transfer Conveyor
LDT | Lime Storage Day Tank
LMC | Lime Storage Metering Conveyor
LIC | Lime Feed Inclinded Conveyor
LOX | Liquid Oxygen Tank
LVL | Level
MAS | Monster Auger System
MAU | Make Up Air Unit
MBA | Bar Screen Auger / Auger
MBC | Bar Screen Conveyor
MBR | Main Breaker
MBS | Mechanical Bar Screen
MBT | Main Bus Transformer
MCC | Motor Control Centre
MDA | Modudata
MDD | Potassium Detection Device
MDP | Modudata Panel
MFI | Potassium Permanganate (Kmno4) Injector
MFU | Memebrane Filtaraion Unit
MFP | Potassium Permanganate (Kmno4) Feed Pump
MGS | Methane Gas Sphere
MHL | Man Hole
MHS | Main Incoming Hydro Supply
MLP | Mixed Liquor Pump
MSL | Potassium Permanganate (Kmno4) Solution Line
MOD | Mode
MSP | Mixer Sludge Pump
MSS | Mechanical Step Screen
MIT | Mist Eliminator (On An Odour Control System)
MST | Potassium Permanganate (Kmno4) Storage Tank
MTC | Master Transfer Controller
MUF | Muffle Furnace
MVF | Maintenance Ventilation Fan
MXP | Mixing Pump
MXR | Mixer
MXV | Mixing Valve
MUX | Multiplexer
M1M1 | Potassium Permanganate (Kmno4) Tank 1 Mixer 1
NBP | Sodium Bisulphate Pump
NBS | Sodium Bisulphate System
NBT | Sodium Bisuphate Storage Tank
NBR | Normal Breaker
NFA | Night Fill
NGH | Natural Gas Header
NGS | Nitrogen Generator System
NHC | Sodium Hydroxide Containment
NHP | Sodium Hydroxide Pump
NHS | Sodium Hydroxide System
NHT | Sodium Hydroxide Storage Tank
OAK | Oakville
OFG | Overflow Gate
OFC | Overflow Channel
OFM | Overflow Manhole
OBW | Observation Well
OCB | Operations Center Building
OCR | Odour Control Room
OCU | Odour Control Unit
OCW | Cooling Water Valve
OGI | Ozone Generator Inlet
OGO | Ozone Generator Outlet
GOD | Gasous Oxygen Dew Point
OUT | Outlet Gravity
ORP | Outlet Riser Pipe
OWAS | Operator Working Alone System
OWF | Oakville Water Filter
OVD | Overhead Door
OZC | Ozone Contactor
OZD | Ozone Destruct System
OZG | Ambient Ozone Detector
PAC | Poly Aluminum Chlorite Header
PAL | Process Air Line
PAT | Poly Aluminum Chlorite Storage Tank
PBL | Polymer System Blower
PBS | Pribusin System
PBP | Pressure Booster Pump
PCL | Primary Clarifiers
PCH | Prechlorination
PDG | Primary Digester
PDU | Polymer Dry Feed Unit
PEF | Primary Effluent
PFC | Pre Filter Water Conduit
PFP | Polymer Feed Pump
PFS | Polymer Feed System
PFH | Polymer Feed Header
PGL | Pilot Gas Line
PID | Pid Loop Parameters
PIF | Primary Influent
PIN | Plant Influent
PIP | Pipe Gallery
PLC | Programmable Logic Controller
PKL | Parking Lot
PLT | Plant
PMT | Polymer Mixing System
PMX | Polymer System Mixer
POH | Polymer Header
POL | Polymer Area
PRES | Pressue
PRL | Polymer Return Line
PMS | Pumping Station
PSU | Power Supply Unit
PSB | Pumping Station Building
PSF | Polymer System Screw Feeder
PSR | Polymer Storage Room
PST | Polymer Storage Tank
PTP | Polymer Transfer Pump
PWL | Potable Water Line
PWM | Power Monitor
P1C | Primary Tank 1 - Cross Collector
P2C | Primary Tank 2 - Cross Collector
P1F | Primary Tank 1 - Flyt Horizontal Collector
P2F | Primary Tank 2 - Flyt Horizontal Collector
P1S | Primary Tank 1 - Sweep Collector
P2S | Primary Tank 2 - Sweep Collector
RAD | Return Activated Discharge
RAP | Return Activated Sludge Pump
RAS | Return Activated Sludge Suction
RDR | Rotary Dryer
RDI | Rotary Dryer Inclined Conveyor
RDF | Rotary Dryer Heat Pulse Feed Conveyor
RDC | Rotary Dryer Discharge Conveyor
RPC | Rotary Dryer Heat Pulse Cell
RDT | Rotary Drum Thickener
RDP | Rotary Drum Thickener Discharge Pump
RFP | Rotary Drum Thickener Feed Pump
RTP | Rotary Drum Thickener Thickened Sludge Pump
RBH | Raw Water Bypass Header
RCN | Rate Controller
RCP | Recirculation Pump
RES | Reservoir
RFG | Refrigerator
RNG | Range (For Duty Pumps)
RDL | Roadway Lights
RPU | Remote Processing Unit
RSG | Return Activated Sludge Gallery
RSH | Raw Sludge Hopper
RSP | Raw Sludge Pump
RSS | Raw Sludge System
RSW | Raw Sewage
RSY | Return Activated Sludge System
RTXX | Remote Terminal Unit
RTR | Remote Terminal Unit - Remote Rack
RWG | Raw Water Gates
RWH | Raw Water Header
R1V | Ras Suction Header 1, Valve 1
R2V | Ras Suction Header 2, Valve 1
R1P | Actiflo Unit 1 - Recirc Pump 1
R2P | Actiflo Unit 2 - Recirc Pump 1
R3P | Actiflo Unit 3 - Recirc Pump 1
RGE | Range
RG01D1 | Range 1, Duty Pump 1 (Used In Combination With Fragment 4)
RG02D1 | Range 2, Duty Pump 1 (Used In Combination With Fragment 4)
RG10D2 | Range 10, Duty Pump 2 (Used In Combination With Fragment 4)
SAC | Sulphuric Acid Containment
SAM | Sampler
SAP | Sample Pump
SAR | Sulphuric Acid Room Temp
SAS | Sulphuric Acid System
SAT | Sulphuric Acid Storage Tank
SBP | Sewage Booster Pump
SBR | Sodium Bisulphite Room
SBT | Sodium Bisulphite Storage Tank
SBS
SCL | Secondary Clarifiers
SCB | Secondary Clarifier Bank
SCH | Scum Hopper
SCP | Scum Pump
SCR | Screen (Room)
SDG | Secondary Digester
SDH | Raw Sewage Discharge Header
SDR | Sphere Drain Room
SED | Sedimentation Tank
SCE | Secondary Effluent
SER | Sludge Gas Relief Line
SPT | Setpoint
SFC | Silo Feed Conveyor
SFP | Sulphuric Acid Pump
SFS | Silica Handling System
SGR | Sludge Grinder
SHR | Sodium Hydroxide Room Temp
SCO | Sludge Collectors
SLC | Sludge Cake
SLG | Sludge Gallery
SLH | Sewage Lift Potable Water
SLP | Sewage Lift Pump
SLS | Sludge Loading System
SMC | Sludge Metering Conveyor
SMT | Sludge Mixing Tank
SND | Supernatant Discharge
SNP | Supernatant Pump
SNT | Supernatant Tank
SOD | Sulphanator System
SON | Sulphanator
SOH | Sulphur Dioxide Header
SOT | Sulphur Dioxide Storage Tank
SPE | Standpipe
SPP | Spray Water Pump
SRH | Surge Header
SRP | Sludge Recirculation Pump
SRS | Sludge Recirculating System
SRT | Sludge Retention Time Control System (Wastewater)
SGT | Surge Tank (Water)
SRB | Sludge Receiving Bin
SSE | Sludge Storage Silo Extraction Conveyor
SSH | Sludge Storage Silo Hydraulic Power Pack
SSL | Sludge Sampling Line
SST | Sludge Storage Tank
SSS | Sludge Storage Silo
SSP | Sludge Storage Silo Spreader
SSY | Security System
STC | Suldge Transfer Conveyor
STD | Sludge Transfer Discharge
STM | Storm Tank
STN | Station
STB | Station Burlington
STE | Station East
STO | Station Oakville
STW | Station West
STP | Sludge Transfer/Loading Pump
STS | Sludge Transfer System
SET | Settling Test
STT | Settling Tank
SRW | Stairwell
SUH | Suction Supply Header
SUP | Sump Pump
SVH | Service Water Header
SOM | ??? Something In The Bwpp App
SWA | Alum System Service Water
SHO | Swap Hours At Mount Forest
SWC | Settled Water Conduit
SWD | Settled Water Distribution System
SWF | Flouride System Service Water
SWH | Seal Water Header
SWP | Seal Water Pump
PSW | Polymer System Service Water
SWG | Switchgear
SWW | Sewage Valve (Particular To Water Plants)
S1C | Secondary Tank 1 - Cross Collector
S2C | Secondary Tank 2 - Cross Collector
S1F | Secondary Tank 1 - Flyt Horizontal Collector
S2F | Secondary Tank 2 - Flyt Horizontal Collector
S1S | Secondary Tank 1 - Sweep Collector
S2S | Secondary Tank 2 - Sweep Collector
TBG | Turbine Generator
TKL | Tank Light
TLP | Tertiary Lift Pump
TPB | Tipping Bucket
TBR | Travelling Bridge
TRA | Truck Receiving Area
TRB | Turbine
TSC | Travelling Screen
TSR | Transformer
TMP | Temperature
TWS | Thickened Waste Activated Sludge
UDL | Under Drain Line
UFN | Unit Furnace
UHT | Unit Heater
UPS | Uninterruptable Power Supply
UVD | Ultra Violet Disinfection System
UVB | Ultra Violet Disinfection Blower
VAC | Vacuum System
VAP | Vacuum (Priming) Pump
VAS | Loss Of Vacuum
VCH | Valve Chamber
VCR | Venturi Chamber
VNF | Ventilation Fan
VFD | Variable Frequency Drive
VSY | Ventilaton System
WAD | Waste Activated Discharge
WAP | Waste Activated Sludge Pump
WAS | Waste Activated Suction
WBX | Weir Box
WDH | Waste Equalization Discharge
WDR | Wind Direction
WGB | Waste Gas Burner
WGL | Waste Gas Line
WHT | Hot Water Heater
WLP | Well Lift Pump
WMS | Wind Speed/Direction
WSS | Waste Activated Sludge System
WKS | Work Station
WSP | Wind Speed
WSY | Waste Sludge System
WTI | Waste Actiflo Inlet
WTN | Weather Station
WEW | Wet Well
WIN | Generator Winding
WWH | Waste Water Header
WWP | Waste Water Pump
WWT | Waste Water Tank
YHY | Yard Hydrant
ZOH | Zone Header

## Fragment 3 - Major Equip. Sub.
TABLE 2A-3 FRAGMENT 3 MAJOR EQUIPMENT SUBSET
FRAGMENT 3 | DESCRIPTION
00 | Main Piece Of Equipment
01 | Valves On A Multi-Valve Header;
03 | Inlet Isolating Valve
06 | Outlet Isolating Valve
07 | Backwash Inlet Valve
08 | Backwash Outlet Valve
09 | Rinse Outlet Valve
10 | Slow Refill Valve
11 | Air Wash Inlet Valve
12 | Draindown Valve
99 | Sluice Gate
A1 | Priority One Alarm
A2 | Priority Two Alarm
A3 | Priority Three Alarm
A4 | Priority Four Alarm
A5 | Priority Five Alarm
A6 | Priority Six Alarm
A7 | Priority Seven Alarm
A8 | Priority Eight Alarm
AC | Actuator
AD | Adjustment Factor
AF | Air Filter
AG | Alternate Gate
AI | Residual
AM | Auxiliary Drive Motor
AN | Ammonia
AP | Air Pressurizing Valve
AR | Auto Rate Or
AU | Ammonia (Un-Ionized)
AV | Alternate Valve
AZ | Canada Day (For Operator Notification System)
BA | Uv Ballast
BC | Battery Charger
BD | Boxing Day (For Operator Notification System)
BE | Burner Pilot Gas Energized
BF | Backwash Flow
BG | Bypass Gate
BK | Bank
BL | Backwash Length
BN | B Value
BP | Burner Pilot On
BR | Burner/Firing Rate
BT | Battery
BV | Bypass Valve
BW | Backwash
BX | Burner Purge On
C1 | Cell 1
C10 | Cell 10
C11 | Cell 11
C12 | Cell 12
C13 | Cell 13
C14 | Cell 14
C2 | Cell 2
C3 | Cell 3
C4 | Cell 4
C5 | Cell 5
C6 | Cell 6
C7 | Cell 7
C8 | Cell 8
C9 | Cell 9
CC | Concentration Setpoint
CD | Closed
CE | Christmas Eve Day (For Operator Notification System)
CF | Counter - Faults
CH | Cathodic Protection
CI | Conductivity
CK | Clock/Date
CN | Ozone Residual
CP | Control Panel
CR | Chlorine Residual
CS | Constant Mode
CT | Concentration And Time Disinfection (Used At Water Plants)
CV | Check Valve
CY | Cycles
CZ | Christmas Day (For Operator Notification System)
D1 | Duty 1
D2 | Duty 2
D3 | Duty 3
D4 | Duty 4
DB | Timer Deadband
DC | Discharge
DD | DAF Mode
DE | Diesel Engine
DF | Dust Filter
DG | Drain Gate
DI | Density
DL | Differential Strainer
DM | Drive Motor
DN | Drain Timer
DO | Dosage Setpoint
DP | Duty Pump
DR | Dosing Ratio (Water Plant Chemical Dosage)
DS | Duty Setpoint
DT | Drip Trap
DV | Discharge Valve
DW | Dew Point
DY | Derivatve Setting
EF | Efficiency Factor
EI | Voltage
EV | Effluent Valve
EY | Eyewash
FA | Flame Arrestors
FC | Feed Conveyor
FD | Flood
FE | Exhaust Fan
FH | High Flow Temperature
FI,FX | Flow (X=Calculated Point)
FL | Low Flow Flare Temperature
FN | Fan
FP | Finish Position
FR | Falling Flow/Rising Flow (Burlington Water Plant Low Lifts)
FS | Flushing Water Strainer
FT | Flow Setpoint
FV | Flow Valve/Rate Control Valve
FZ | Family Day (For Operator Notification System)
GW | IP Gateway
GD | Gear Drive
GE | Gas Engine
GF | Good Friday (For Operator Notification System)
GI | Gas Indicator
GL | Goal
GS | Gas
GV | Isolating Valve
HE | Heat Exchanger
HI | Ph
HN | Horn / Alarm
HO | High Position (Oakville Water Plant Filter Valve)
HP | High Position
HR | Heater
HS | Hydrogen Sulfide
HT | Heat Tracing
HV | Thermal Valve
HZ | Frequency
IB | Timer Interval
IF | Intake Filter (Air)
IG | Inlet Gate
II | Current (Amps)
IJ | Flexible Inlet Joint
IN | Integrator
IO | Io Server
IP | Inlet Presure or IP Address
IR | Integral Gain
IS | Inlet Strainer
IT | Inlet Temperature
IV | Inlet Valve
IY | Intensity
JH | Power Consumption
JI | Power (Hydro)
KS | Key Switch
LB | Lab
LD | Loading
LE | Level Element (Digital Input)
LH | Level High
LI | Level
LL | Level Low
LM | Lamp
LP | Lighting Panel
LS | Level Setpoint
LV | Air Release Valve
LZ | Labour Day (For Operator Notification System)
MA | Milliamps
MC | Master Control
MD | Motion Detector
MF | Mass Flow
MG | Methane Gas
MH | Master Switch Of Device
MI | Mass
ML | Multilin
MM | Modulating Motor
MN | M Value
MO | Mode/Step (Water Plant Filter Controls)
MP | Motor Protection / Motor Management Relay
MR | Master Rate
MS | Mechanical Strainer
MV | Modulating (Control) Valve
N1 | Ozone Generator Inverter 1
N2 | Ozone Generator Inverter 2
NI | Turbidity
NL | Using Natural Gas
NT | Night Mode/Duty
NV | Drain Valve
OB | Obstruction Beacon
OF | Oil Filter
OG | Outlet Gate
OI | D.O. Meter
OJ | Flexible Outlet Joint
OP | Ortho-Phosphate
OR | Override
OT | Outlet Temperature
OV | Outlet Valve
OX | Oxygen
PA | Particle Analyzer
PB | Panel Board
PC | Primary Clarifier Co-Thickening Mode
PD | Pid Loop Control
PE | Pressure Element
PF | Pilot Fail
PG | Pressure Gauge
PI | Pressure
PL | Pilot Light
PN | Proportional Gain
PO | Outlet Pressure
PR | Probe
PR | Protection Relay
PS | Pressure Setpoint
PT | Primary Air Temperature
PU | Purge
PV | Backflow Preventer Valve
QV | Equalizing Valve
RE | Recorder
RF | Residual Free
RG | Regulator
RM | Remote Mode
RO | Ratio Mode
RP | Power Factor
RR | Remote Rack
RT | Residual Total
RV | Relief Valve
S1,S2,S3 | Filter Agitator Sweep
SC | Stroke Positioner
SD | Shut Down
SF | Supply Fan
SG | Slide Gate
SI | Speed
SK | Stroke
SL | Servicing Panel
SM | Sms (Unique To The Burlington Water Treatment Plant Pumps) or Subnet Mask
SN | Sign Of B Value (Negative Or Positive)
SP | Stop
SQ | Sequence
SR | Sediment Trap
SS | Speed Setpoint
ST | Start
SU | Sump Pump
SV | Solenoid Valve
SW | Switch Gear
SX | Square Root Extractor
SY | Specific Gravity
SZ | Start Position
TD | Total Suspended Solids (Lab Value)
TF | Transfer
TI | Temperature
TK | Tank
TL | Total
TM | Time(R)
TN | Uv Transmittance
TO | Entry Door Switch
TP | Time(R) Setpoint
TR | Time - Runtime
TS | Temperature Setpoint
TV | Agitator Valve
TZ | Thanksgiving Day (For Operator Notification System)
UG | Using Digester Gas
UI | Uv Intensity Sensors
UL | Uv Lamp
UR | Uv Reator
UV | Surge Valve
VD | Victoria Day (For Operator Notification System)
VE | Variable Speed Drive - Electrical
VF | Variable Frequency Drive
VG | Variable Speed Drive - Magnetic
VL | Volume Mode
VM | Variable Speed Drive - Mechanical
VS | Volume Setpoint
VT | Volatile
VU | Volume
VV | Vent Valve
VZ | Civic Holiday (For Operator Notification System)
WG | Weir Gate
WP | Uv Wipers
WS | Weight Scale
WV | Cooling Water Valve
XD | Vibration - Drive End
XG | Isolation Gate
XI | Vibration
XN | Vibration - Non Drive End
XP | Oxidation Reduction Potential
XV | Diverting Valve
YD | New Year Day (For Operator Notification System)
YE | New Year Eve'S Day (For Operator Notification System)
YV | Air Scour Valve
Z1 | Analyzer 1 (Ozone System In Water Plants)
Z2 | Analyzer 2 (Ozone System In Water Plants)
Z3 | Analyzer 3 (Ozone System In Water Plants)
Z4 | Analyzer 4 (Ozone System In Water Plants)
ZD | Day Position
ZI | Position
ZM | Manual Position
ZN | Night Position
ZV | Backwash Valve

## Fragment 4,5 - SCADA
TABLE 2A-4.1 FRAGMENT 4 & 5
FRAGMENT 4 | FRAG 4 CODE | FRAGMENT 5 DESCRIPTION | FRAG 5 CODE | LOG EVENTS | ALARM STATE (ON/OFF/NONE) | LOG DATA
DIGITAL OUTPUT | PB | Abort | AB | P | None | Uncheck
DIGITAL OUTPUT | PB | Advance | AD | P | None | Uncheck
DIGITAL OUTPUT | PB | Alarm Enable | AE | P | None | Uncheck
DIGITAL OUTPUT | PB | Alarm Acknowledge (Reset) | AR | P | None | Uncheck
DIGITAL OUTPUT | PB | Automatic Voltage Mode Select | AV | P | None | Uncheck
DIGITAL OUTPUT | PB | Active Mode Raise | AM | P | None | Uncheck
DIGITAL OUTPUT | PB | Active Mode Lower | AL | P | None | Uncheck
DIGITAL OUTPUT | PB | Close | CE | P | None | Uncheck
DIGITAL OUTPUT | PB | Constant Mode/Speed | CS | P | None | Uncheck
DIGITAL OUTPUT | PB | Down | DN | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Discharge Request | DT | P | None | Uncheck
DIGITAL OUTPUT | PB | Enable | EN | P | None | Uncheck
DIGITAL OUTPUT | PB | Signal Error Alarm Enable | ER | P | None | Uncheck
DIGITAL OUTPUT | PB | Forward | FD | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Fast Request | FT | P | None | Uncheck
DIGITAL OUTPUT | PB | FCR Mode Select | FC | P | None | Uncheck
DIGITAL OUTPUT | PB | Hold | HO | P | None | Uncheck
DIGITAL OUTPUT | PB | Open | ON | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Close Request | PC | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Fill Request | PF | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Mode Request | PM | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Stroke Request | MS | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Open Request | PO | P | None | Uncheck
DIGITAL OUTPUT | PB | Runtime Reset | RT | P | None | Uncheck
DIGITAL OUTPUT | PB | No Flow Alarm Enable | FA | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Stop Request | PP | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Start Request | PT | P | None | Uncheck
DIGITAL OUTPUT | PB | Level 1 Lockout Reset | R1 | P | None | Uncheck
DIGITAL OUTPUT | PB | Level 2 Lockout Reset | R2 | P | None | Uncheck
DIGITAL OUTPUT | PB | Level 3 Lockout Reset | R3 | P | None | Uncheck
DIGITAL OUTPUT | PB | Reverse | RE | P | None | Uncheck
DIGITAL OUTPUT | PB | Ratio Mode | RO | P | None | Uncheck
DIGITAL OUTPUT | PB | Loss Of Pressure Enable | PL | P | None | Uncheck
DIGITAL OUTPUT | PB | Emergency Stop Enable | ES | P | None | Uncheck
DIGITAL OUTPUT | PB | Loss Of Prime Enable | PH | P | None | Uncheck
DIGITAL OUTPUT | PB | Hihi Alarm Enable | HH | P | None | Uncheck
DIGITAL OUTPUT | PB | Hi Alarm Enable | HI | P | None | Uncheck
DIGITAL OUTPUT | PB | Lo Alarm Enable | LO | P | None | Uncheck
DIGITAL OUTPUT | PB | Lolo Alarm Enable | LL | P | None | Uncheck
DIGITAL OUTPUT | PB | Temperature/Leakage Alarm Enable | TA | P | None | Uncheck
DIGITAL OUTPUT | PB | Speed Deviation Alarm Enable | ZA | P | None | Uncheck
DIGITAL OUTPUT | PB | Vfd Or Device Failure Enable | GA | P | None | Uncheck
DIGITAL OUTPUT | PB | Min/Max Enable | MM | P | None | Uncheck
DIGITAL OUTPUT | PB | Not Ready Enable | DF | P | None | Uncheck
DIGITAL OUTPUT | PB | Vacuum Alarm Enable | VM | P | None | Uncheck
DIGITAL OUTPUT | PB | Runtime Reset | RP | P | None | Uncheck
DIGITAL OUTPUT | PB | Overload Enable | RA | P | None | Uncheck
DIGITAL OUTPUT | PB | Device Reset | RS | P | None | Uncheck
DIGITAL OUTPUT | PB | Resume | RZ | P | None | Uncheck
DIGITAL OUTPUT | PB | Device Scan Enable | SC | P | None | Uncheck
DIGITAL OUTPUT | PB | Silence Alarms | SL | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Suction Request | SR | P | None | Uncheck
DIGITAL OUTPUT | PB | Status | SS | P | None | Uncheck
DIGITAL OUTPUT | PB | Setpoints Update | SU | P | None | Uncheck
DIGITAL OUTPUT | PB | Plant Manual Slow Request | SW | P | None | Uncheck
DIGITAL OUTPUT | PB | Test Mode | TM | P | None | Uncheck
DIGITAL OUTPUT | PB | Up | UP | P | None | Uncheck
DIGITAL OUTPUT | PB | VAR/PF Control | VP | P | None | Uncheck
DIGITAL OUTPUT | PB | Enable Input Power | IN | P | None | Uncheck
DIGITAL OUTPUT | PB | Duty Assignment Update | AU | P | None | Uncheck
FRAGMENT 4 | FRAG 4 CODE | FRAGMENT 5 DESCRIPTION | FRAG 5 CODE | LOG EVENTS | ALARM STATE (ON/OFF/NONE) | LOG DATA
ANALOG OUTPUT | AO | High High Setpoint | HH | P | None | Uncheck
ANALOG OUTPUT | AO | High Setpoint | HI | P | None | Uncheck
ANALOG OUTPUT | AO | Stroke Setpoint | SK | P | None | Uncheck
ANALOG OUTPUT | AO | Low Setpoint | LO | P | None | Uncheck
ANALOG OUTPUT | AO | Low Low Setpoint | LL | P | None | Uncheck
ANALOG OUTPUT | AO | Span | EU | P | None | Uncheck
ANALOG OUTPUT | AO | Seconds Timer | SN | P | None | Uncheck
ANALOG OUTPUT | AO | Minutes Timer | MS | P | None | Uncheck
ANALOG OUTPUT | AO | Hours Timer | HS | P | None | Uncheck
ANALOG OUTPUT | AO | Day Timer | DY | P | None | Uncheck
ANALOG OUTPUT | AO | Week Timer | WK | P | None | Uncheck
ANALOG OUTPUT | AO | Month Timer | MM | P | None | Uncheck
ANALOG OUTPUT | AO | Year Timer | YY | P | None | Uncheck
ANALOG OUTPUT | AO | Quantity Added/Received | QR | P | None | Uncheck
ANALOG OUTPUT | AO | Start Setpoint (Entry) | TS | P | None | Uncheck
ANALOG OUTPUT | AO | Stop Setpoint (Entry) | PS | P | None | Uncheck
ANALOG OUTPUT | AO | Setpoint Entry | CT | P | None | Uncheck
ANALOG OUTPUT | AO | Calibration Factor | CF | P | None | Uncheck
ANALOG OUTPUT | AO | Open Setpoint | ON | P | None | Uncheck
ANALOG OUTPUT | AO | Closed Setpoint | CE | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) High Time Setpoint | HG | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Finish Time Setpoint Entry | FH | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Start Flow Setpoint Entry | SB | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Finish Flow Setpoint Entry | FL | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) High Flow Setpoint Entry | HF | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Air Scour Time Setpiint Entry | AS | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Stratification Time Setpoint | SY | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Drain Time Setpoint Entry | DR | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Valve High Position Setpoint Entry | VH | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Valve Start Position Setpoint Entry | VS | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Valve Finish Position Setpoint | VF | P | None | Uncheck
ANALOG OUTPUT | AO | (Backwash) Agitation Time Setpoint Entry | BA | P | None | Uncheck
ANALOG OUTPUT | AO | Backwash Length | BL | P | None | Uncheck
FRAGMENT 4 | FRAG 4 CODE | FRAGMENT 5 DESCRIPTION | FRAG 5 CODE | LOG EVENTS | ALARM STATE (ON/OFF/NONE) | LOG DATA
DIGITAL INPUT STATUS | DI | Control Mode | CL | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Plant Manual Mode Stroke | MS | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Plant Auto Mode Stroke | AS | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Normal Power | JN | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Normal Power Availabe | JX | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Emergency Power Available | EP | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Test Mode | TM | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Closed Status | CD | P | None | Variable
DIGITAL INPUT STATUS | DI | Opened Status | OD | P | None | Variable
DIGITAL INPUT STATUS | DI | Open (Status Of Command) | ON | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Close (Status Of Command) | CE | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Low Low Level | LL | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Low Level | LO | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Mid Level | ML | P | None | Uncheck
DIGITAL INPUT STATUS | DI | High Level | HI | P | None | Uncheck
DIGITAL INPUT STATUS | DI | High High Level | HH | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Status | SS | P | None | Variable
DIGITAL INPUT STATUS | DI | Reverse | RE | P | None | Variable
DIGITAL INPUT STATUS | DI | Forward | FD | P | None | Variable
DIGITAL INPUT STATUS | DI | Off | OF | Uncheck | None | Uncheck
DIGITAL INPUT STATUS | DI | EStop Status | ES | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Plant Auto Mode | AA | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Scan Status | SC | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Group Unacknowledged | GU | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Plant Manual Mode Status | PM | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Legal Entry | SE | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Device Enabled | DE | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Slow | SW | P | None | Variable
DIGITAL INPUT STATUS | DI | Fast | FT | P | None | Variable
DIGITAL INPUT STATUS | DI | Digital Level | LE | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Vacuum Alarm (Raw) | VM | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Discharge Position Status | DP | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Enable | EN | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Constant Speed | CS | P | None | Variable
DIGITAL INPUT STATUS | DI | Suction Position Status | SR | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Auxillary Status | AX | P | None | Uncheck
DIGITAL INPUT STATUS | DI | VFD On Bypass | BP | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Name (HMI) | NM | Uncheck | None | Uncheck
DIGITAL INPUT STATUS | DI | Backup Stop Relay | SP | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Backup Start Relay | ST | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Duty Assignment Update Error | UE | Uncheck | None | Uncheck
DIGITAL INPUT STATUS | DI | Watch Dog | WD | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Increase Voltage | IV | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Decrease Voltage | DV | P | None | Uncheck
DIGITAL INPUT STATUS | DI | DC Voltage | DC | P | None | Uncheck
DIGITAL INPUT STATUS | DI | Pump Not Ready | RD | P | None | Uncheck
INTERNAL TO PROCESSOR | DI | Download To Processor | DD | P | None | Uncheck
INTERNAL TO PROCESSOR | DI | Processor In Program Mode | PR | P | None | Uncheck
INTERNAL TO PROCESSOR | DI | Processor In Run Mode | RU | P | None | Uncheck
INTERNAL TO PROCESSOR | DI | Online Edit In Process | OE | P | None | Uncheck
FRAGMENT 4 | FRAG 4 CODE | FRAGMENT 5 DESCRIPTION | FRAG 5 CODE | LOG EVENTS | ALARM STATE (ON/OFF/NONE) | LOG DATA
ANALOG INPUT | AI | Phase 1 Current | I1 | Uncheck | None | P
ANALOG INPUT | AI | Phase 2 Current | I2 | Uncheck | None | P
ANALOG INPUT | AI | Phase 3 Current | I3 | Uncheck | None | P
ANALOG INPUT | AI | Average Current | I4 | Uncheck | None | P
ANALOG INPUT | AI | Hottest Stator Temperature | T1 | Uncheck | None | P
ANALOG INPUT | AI | Ground Fault Current | I5 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 1 | R1 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 2 | R2 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 3 | R3 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 4 | R4 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 5 | R5 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 6 | R6 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 7 | R7 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 8 | R8 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 9 | R9 | Uncheck | None | P
ANALOG INPUT | AI | Rtd Temperature 10 | R0 | Uncheck | None | P
ANALOG INPUT | AI | Motor Load | M1 | Uncheck | None | P
ANALOG INPUT | AI | Motor Current Status | M2 | Uncheck | None | P
ANALOG INPUT | AI | Motor Alarm | M3 | Uncheck | None | P
ANALOG INPUT | AI | Motor Trip | M4 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Average Current | I9 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Ground Fault Current | I0 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Hottest Stator Number | T2 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Hottest Stator Temperature | T3 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Average Voltage | V5 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Actual Watts | E3 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Voltamps Reactive | P3 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Power Factor | C3 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Power Factor Sign | C4 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Frequency | H2 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Watts Sign | E4 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Voltamps Reactive Sign | P4 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Phase 1 Current | I6 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Phase 2 Current | I7 | Uncheck | None | P
ANALOG INPUT | AI | Pre Trip Phase 3 Current | I8 | Uncheck | None | P
ANALOG INPUT | AI | Voltage Average | V4 | Uncheck | None | P
ANALOG INPUT | AI | Voltage A-B | V1 | Uncheck | None | P
ANALOG INPUT | AI | Voltage B-C | V2 | Uncheck | None | P
ANALOG INPUT | AI | Voltage C-A | V3 | Uncheck | None | P
ANALOG INPUT | AI | Actual Watts | E1 | Uncheck | None | P
ANALOG INPUT | AI | Voltamps Reactive | P1 | Uncheck | None | P
ANALOG INPUT | AI | Power Factor | C1 | Uncheck | None | P
ANALOG INPUT | AI | Power Factor Sign | C2 | Uncheck | None | P
ANALOG INPUT | AI | Reactive Power | JJ | Uncheck | None | P
ANALOG INPUT | AI | Frequency | H1 | Uncheck | None | P
ANALOG INPUT | AI | Watts Sign | E2 | Uncheck | None | P
ANALOG INPUT | AI | Voltamps Reactive Sign | P2 | Uncheck | None | P
ANALOG INPUT | AI | Lockout Time | L1 | Uncheck | None | Uncheck
ANALOG INPUT | AI | Current Value | CV | Uncheck | None | P
ANALOG INPUT | AI | Current Last Value (Turbiidity Reports) | LV | Uncheck | None | P
ANALOG INPUT | AI | Hour Timer | HS | Uncheck | None | Uncheck
ANALOG INPUT | AI | Minutes Timer | MS | Uncheck | None | Uncheck
ANALOG INPUT | AI | SVI Test | SV | Uncheck | None | Uncheck
ANALOG INPUT | AI | Tare Weight | TR | Uncheck | None | Uncheck
ANALOG INPUT | AI | Total Weight | WG | Uncheck | None | Uncheck
ANALOG INPUT | AI | Sample Weight | WS | Uncheck | None | Uncheck
ANALOG INPUT | AI | Seconds Timer | SN | Uncheck | None | Uncheck
ANALOG INPUT | AI | Year Timer | YY | Uncheck | None | Uncheck
ANALOG INPUT | AI | Day Timer | DY | Uncheck | None | Uncheck
ANALOG INPUT | AI | Runtime Since Last Reset | RT | Uncheck | None | P
ANALOG INPUT | AI | Month Timer | MM | Uncheck | None | Uncheck
ANALOG INPUT | AI | Cycle Time | CT | Uncheck | None | Uncheck
ANALOG INPUT | AI | Night Timer | NT | Uncheck | None | Uncheck
ANALOG INPUT | AI | Pause Time | PT | Uncheck | None | Uncheck
ANALOG INPUT | AI | Minimum Today | ND | Uncheck | None | Uncheck
ANALOG INPUT | AI | Minimum Yesterday | NP | Uncheck | None | Uncheck
ANALOG INPUT | AI | Total Today | TD | Uncheck | None | P
ANALOG INPUT | AI | Total Yesterday | YT | Uncheck | None | P
ANALOG INPUT | AI | Total 2 Days Ago | Y2 | Uncheck | None | Uncheck
ANALOG INPUT | AI | Total 3 Days Ago | Y3 | Uncheck | None | Uncheck
ANALOG INPUT | AI | Total 4 Days Ago | Y4 | Uncheck | None | Uncheck
ANALOG INPUT | AI | Total 5 Days Ago | Y5 | Uncheck | None | Uncheck
ANALOG INPUT | AI | Total 6 Days Ago | Y6 | Uncheck | None | Uncheck
ANALOG INPUT | AI | Total 7 Days Ago | Y7 | Uncheck | None | Uncheck
ANALOG INPUT | AI | Maximum Today | XD | Uncheck | None | P
ANALOG INPUT | AI | Maximum Yesterday | XP | Uncheck | None | Uncheck
ANALOG INPUT | AI | Average Today | AT | Uncheck | None | Variable
ANALOG INPUT | AI | Average Yesterday | AY | Uncheck | None | Variable
ANALOG INPUT | AI | Present Month'S Total | MT | Uncheck | None | Variable
ANALOG INPUT | AI | Previous Month'S Total | YM | Uncheck | None | Variable
ANALOG INPUT | AI | Start | TS | P | None | Uncheck
ANALOG INPUT | AI | Stop | PS | P | None | Uncheck
ANALOG INPUT | AI | (Back Wash) High Time Setpoint | HG | P | None | Uncheck
ANALOG INPUT | AI | (Back Wash) Finish Time Setpoint Entry | FH | P | None | Uncheck
ANALOG INPUT | AI | (Back Wash) Start Flow Setpoint Entry | SB | P | None | Uncheck
ANALOG INPUT | AI | (Back Wash) Finish Flow Setpoint Entry | FL | P | None | Uncheck
ANALOG INPUT | AI | (Back Wash) High Flow Setpoint Entry | HF | P | None | Uncheck
ANALOG INPUT | AI | (Back Wash) Air Scour Time Setpiint Entry | AS | P | None | Uncheck
ANALOG INPUT | AI | (Back Wash) Stratification Time Setpoint | SY | P | None | Uncheck
ANALOG INPUT | AI | (Backwash) Drain Time Setpoint Entry | DR | P | None | Uncheck
ANALOG INPUT | AI | (Backwash) Valve High Position Setpoint Entry | VH | P | None | Uncheck
ANALOG INPUT | AI | (Backwash) Valve Start Position Setpoint Entry | VS | P | None | Uncheck
ANALOG INPUT | AI | (Backwash) Valve Finish Position Setpoint | VF | P | None | Uncheck
ANALOG INPUT | AI | (Backwash) Agitation Time Setpoint Entry | BA | P | None | Uncheck
ANALOG INPUT | AI | IP/Subnet/Gateway Address Segment | IP | Uncheck | None | Uncheck
ANALOG INPUT | AI | Backwash Length | BL | P | None | Uncheck
ANALOG INPUT | AI | Maximum Weekly | XW | Uncheck | None | Variable
ANALOG INPUT | AI | Minimum Weekly | NW | Uncheck | None | Variable
ANALOG INPUT | AI | Maximum Monthly | XM | Uncheck | None | Variable
ANALOG INPUT | AI | Minimum Monthly | NM | Uncheck | None | Variable
ANALOG INPUT | AI | Maximum Yearly | XY | Uncheck | None | Variable
ANALOG INPUT | AI | Minimum Yearly | NY | Uncheck | None | Variable
ANALOG INPUT | AI | Quantity Received/Added | QR | Uncheck | None | P
ANALOG INPUT | AI | Setpoint Value | AI | P | None | Uncheck
ANALOG INPUT | AI | Current Hour Total | HT | Uncheck | None | Variable
ANALOG INPUT | AI | Current Week Total | WT | Uncheck | None | Variable
ANALOG INPUT | AI | Current Year Total | TY | Uncheck | None | Variable
ANALOG INPUT | AI | Last Hour Total | YH | Uncheck | None | Variable
ANALOG INPUT | AI | Last Week Total | YW | Uncheck | None | Variable
ANALOG INPUT | AI | Last Year Total | YL | Uncheck | None | Variable
ANALOG INPUT | AI | Current Five Minute Total | C5 | Uncheck | None | Uncheck
ANALOG INPUT | AI | Last Five Minute Total | L5 | Uncheck | None | P
ANALOG INPUT | AI | Current Quarter | QT | Uncheck | None | Variable
ANALOG INPUT | AI | Last Quarter | YQ | Uncheck | None | Variable
ANALOG INPUT | AI | Current Half-Year | TB | Uncheck | None | Variable
ANALOG INPUT | AI | Last Half-Year | YB | Uncheck | None | Variable
ANALOG INPUT | AI | Current Minute Total | 1C | Uncheck | None | Variable
ANALOG INPUT | AI | Last Minute Total | L1 | Uncheck | None | Variable
FRAGMENT 4 | FRAG 4 CODE | FRAGMENT 5 DESCRIPTION | FRAG 5 CODE | LOG EVENTS | ALARM STATE (ON/OFF/NONE) | LOG DATA
ANALOG INPUT ALARM | DA | High High Alarm | HH | Uncheck | ON | Uncheck
ANALOG INPUT ALARM | DA | High Alarm | HI | Uncheck | ON | Uncheck
ANALOG INPUT ALARM | DA | Low Alarm | LO | Uncheck | ON | Uncheck
ANALOG INPUT ALARM | DA | Low Low Alarm | LL | Uncheck | ON | Uncheck
ANALOG INPUT ALARM | DA | Rate Of Change | RC | Uncheck | ON | Uncheck
FRAGMENT 4 | FRAG 4 CODE | FRAGMENT 5 DESCRIPTION | FRAG 5 CODE | LOG EVENTS | ALARM STATE (ON/OFF/NONE) | LOG DATA
DIGITAL INPUT ALARM | DA | Abnornal Fault | AF | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Signal Error Alarm ( Outside Of Range) | ER | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Analog Signal Open Circiut | OC | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Stroke Deviation Alarm | SA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Analog Signal Loss Of Echo | EL | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Temperature High | TH | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Temperature Low | TL | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Temperature Alarm | TA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Temp/Leak Alarm (Flyght Minicas Alarm) | TK | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Temperature Warning | TW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Bearing Temp | BT | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Winding Temp | WA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Pressure High | PH | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Pressure Low | PL | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Pressure Alarm | PA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Backup Start Relay | SP | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Backup Stop Relay | ST | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Level High | LH | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Level Low | LL | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Level Alarm | LA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Level Warning | LW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Flow Alarm | FA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Flow Warning | FW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Density High | DH | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Density Low | DL | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Density Alarm | DA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Density Warning | DW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Oxygen High | OH | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Oxygen Low | OL | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Oxygen Alarm | OA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Oxygen Failure | OF | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Oxygen Warning | OW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | General Alarm | GA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | General Fault | GF | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | General Failure | GR | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | General Warning/Pre-Alarm | GW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Ground Alarm | NA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Ground Fault | NF | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Ground Failure | NR | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Overload Alarm | RA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Overload Warning | RW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Overcurrent Alarm | IA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Overcurrent Warning | IW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Over Volt Alarm | EA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Over Volt Warning | EW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Gas Detector Alarm | AG | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Gas Detector Failure | AR | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Gas Detector Warning | AW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Motion Fail/ No Motion | MF | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Power High | JH | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Power Low | JL | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Power Alarm | JA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Power Output | JO | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Power Failure | JR | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Power Warning | JW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Trip | TP | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Over Torque Alarm | HA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Over Torque Warning | HW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Vibrator Alarm | VA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Vibrator Failure | VR | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Vibrator Warning | VW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Illegal Entry Alarm | SI | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Limit Alarm | LT | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Loss Of Seal Water Alarm | QA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Loss Of Seal Water Warning | QW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Loss Of Prime Alarm | MA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Loss Of Prime Warning | MW | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Flood Alarm | KA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Fail To Start/Open | SF | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Fail To Stop/Close | XF | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Uncommanded Start/Open | SU | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Uncommanded Stop/Close | XU | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Emergency Stop Button | ES | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Discharge Fail | DF | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Uncommanded Discharge | DU | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Fire/Smoke Alarm | YA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Out Of Balance Alarm | UA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Dv Valve Position Alarm | PN | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Alarm - Pump On - Valve Not Opened | VN | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Setpoint Entry Error | EE | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Communication Alarm | CN | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Setpoint Deviation (Calibration)Alm | ZA | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Vacuum Alarm | VM | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Suction Fail | SR | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Advance Fail | AD | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Runtime Warning | WN | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Timing Fault | TX | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Maximum Allowable Starts | MX | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Downstream Motor/Pump Not Running | MN | Uncheck | ON | Uncheck
DIGITAL INPUT STATUS | DA | Emergency Power | JE | Uncheck | ON | Uncheck
DIGITAL INPUT STATUS | DA | Dasabtcp Server Failed | IP | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Dasabcip Server Failed | CP | Uncheck | ON | Uncheck
DIGITAL INPUT ALARM | DA | Lockout | LK | Uncheck | ON | Uncheck
INTERNAL TO PROCESSOR | DA | Download To Processor Alarm | DD | Uncheck | ON | Uncheck
INTERNAL TO PROCESSOR | DA | Processor Not In Run Mode Alarm | RU | Uncheck | ON | Uncheck
INTERNAL TO PROCESSOR | DA | Online Edit In Process Alarm | OE | Uncheck | ON | Uncheck

## Fragment 4,5 - Priorities Waste
TABLE 2A-4.2 FRAGMENT 4 AND 5 WASTEWATER ALARMS AND EVENTS PRIORITIES
TAG TYPE | SIGNAL TYPE | EVENT PRIORITY | ALARM PRIORITY
DIGITAL OUTPUT | Abort | 600 | N/A
DIGITAL OUTPUT | Advance | 600 | N/A
DIGITAL OUTPUT | Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Alarm Acknowledge (Reset) | 600 | N/A
DIGITAL OUTPUT | Close | 600 | N/A
DIGITAL OUTPUT | Constant Mode/Speed | 600 | N/A
DIGITAL OUTPUT | Down | 600 | N/A
DIGITAL OUTPUT | Plant Manual Discharge Request | 600 | N/A
DIGITAL OUTPUT | Enable | 600 | N/A
DIGITAL OUTPUT | Signal Error Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Forward | 600 | N/A
DIGITAL OUTPUT | Plant Manual Fast Request | 600 | N/A
DIGITAL OUTPUT | Hold | 600 | N/A
DIGITAL OUTPUT | Open | 600 | N/A
DIGITAL OUTPUT | Plant Manual Close Request | 600 | N/A
DIGITAL OUTPUT | Plant Manual Fill Request | 600 | N/A
DIGITAL OUTPUT | Plant Manual Mode Request | 600 | N/A
DIGITAL OUTPUT | Plant Manual Stroke Request | 600 | N/A
DIGITAL OUTPUT | Plant Manual Open Request | 600 | N/A
DIGITAL OUTPUT | Runtime Reset | 600 | N/A
DIGITAL OUTPUT | No Flow Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Plant Manual Stop Request | 600 | N/A
DIGITAL OUTPUT | Plant Manual Start Request | 600 | N/A
DIGITAL OUTPUT | Level 1 Lockout Reset | 600 | N/A
DIGITAL OUTPUT | Level 2 Lockout Reset | 600 | N/A
DIGITAL OUTPUT | Level 3 Lockout Reset | 600 | N/A
DIGITAL OUTPUT | Reverse | 600 | N/A
DIGITAL OUTPUT | Ratio Mode | 600 | N/A
DIGITAL OUTPUT | Loss Of Pressure Enable | 600 | N/A
DIGITAL OUTPUT | Emergency Stop Enable | 600 | N/A
DIGITAL OUTPUT | Loss Of Prime Enable | 600 | N/A
DIGITAL OUTPUT | Hihi Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Hi Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Lo Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Lolo Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Temperature/Leakage Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Speed Deviation Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Vfd Or Device Failure Enable | 600 | N/A
DIGITAL OUTPUT | Min/Max Enable | 600 | N/A
DIGITAL OUTPUT | Pump Not Ready Enable | 600 | N/A
DIGITAL OUTPUT | Vacuum Alarm Enable | 600 | N/A
DIGITAL OUTPUT | Runtime Reset | 600 | N/A
DIGITAL OUTPUT | Overload Enable | 600 | N/A
DIGITAL OUTPUT | Device Reset | 600 | N/A
DIGITAL OUTPUT | Resume | 600 | N/A
DIGITAL OUTPUT | Device Scan Enable | 600 | N/A
DIGITAL OUTPUT | Silence Alarms | 600 | N/A
DIGITAL OUTPUT | Stop | 600 | N/A
DIGITAL OUTPUT | Plant Manual Suction Request | 600 | N/A
DIGITAL OUTPUT | Status | 600 | N/A
DIGITAL OUTPUT | Start | 600 | N/A
DIGITAL OUTPUT | Setpoints Update | 600 | N/A
DIGITAL OUTPUT | Plant Manual Slow Request | 600 | N/A
DIGITAL OUTPUT | Test Mode | 600 | N/A
DIGITAL OUTPUT | Up | 600 | N/A
DIGITAL OUTPUT | Duty Assignment Update | 600 | N/A
TAG TYPE | SIGNAL TYPE | EVENT PRIORITY | ALARM PRIORITY
ANALOG OUTPUT | High High Setpoint | 900 | N/A
ANALOG OUTPUT | High Setpoint | 900 | N/A
ANALOG OUTPUT | Stroke Setpoint | 900 | N/A
ANALOG OUTPUT | Low Setpoint | 900 | N/A
ANALOG OUTPUT | Low Low Setpoint | 900 | N/A
ANALOG OUTPUT | Span | 900 | N/A
ANALOG OUTPUT | Seconds Timer | 900 | N/A
ANALOG OUTPUT | Minutes Timer | 900 | N/A
ANALOG OUTPUT | Hours Timer | 900 | N/A
ANALOG OUTPUT | Day Timer | 900 | N/A
ANALOG OUTPUT | Week Timer | 900 | N/A
ANALOG OUTPUT | Month Timer | 900 | N/A
ANALOG OUTPUT | Year Timer | 900 | N/A
ANALOG OUTPUT | Quantity Added/Received | 900 | N/A
ANALOG OUTPUT | Start Setpoint (Entry) | 900 | N/A
ANALOG OUTPUT | Stop Setpoint (Entry) | 900 | N/A
ANALOG OUTPUT | Setpoint Entry | 900 | N/A
ANALOG OUTPUT | Open Setpoint | 900 | N/A
ANALOG OUTPUT | Closed Setpoint | 900 | N/A
ANALOG OUTPUT | (Backwash) High Time Setpoint | 900 | N/A
ANALOG OUTPUT | (Backwash) Finish Time Setpoint Entry | 900 | N/A
ANALOG OUTPUT | (Backwash) Start Flow Setpoint Entry | 900 | N/A
ANALOG OUTPUT | (Backwash) Finish Flow Setpoint Entry | 900 | N/A
ANALOG OUTPUT | (Backwash) High Flow Setpoint Entry | 900 | N/A
ANALOG OUTPUT | (Backwash) Air Scour Time Setpiint Entry | 900 | N/A
ANALOG OUTPUT | (Backwash) Stratification Time Setpoint | 900 | N/A
ANALOG OUTPUT | (Backwash) Drain Time Setpoint Entry | 900 | N/A
ANALOG OUTPUT | (Backwash) Valve High Position Setpoint Entry | 900 | N/A
ANALOG OUTPUT | (Backwash) Valve Start Position Setpoint Entry | 900 | N/A
ANALOG OUTPUT | (Backwash) Valve Finish Position Setpoint | 900 | N/A
ANALOG OUTPUT | (Backwash) Agitation Time Setpoint Entry | 900 | N/A
ANALOG OUTPUT | Backwash Length | 900 | N/A
TAG TYPE | SIGNAL TYPE | EVENT PRIORITY | ALARM PRIORITY
DIGITAL INPUT STATUS | Control Mode Status | 700 | N/A
DIGITAL INPUT STATUS | Plant Manual Mode Stroke | 700 | N/A
DIGITAL INPUT STATUS | Plant Auto Mode Stroke | 700 | N/A
DIGITAL INPUT STATUS | Normal Power | 700 | N/A
DIGITAL INPUT STATUS | Normal Power Availabe | 700 | N/A
DIGITAL INPUT STATUS | Emergency Power Available | 700 | N/A
DIGITAL INPUT STATUS | Test Mode | 700 | N/A
DIGITAL INPUT STATUS | Closed | 700 | N/A
DIGITAL INPUT STATUS | Opened | 700 | N/A
DIGITAL INPUT STATUS | Open (Status Of Command) | 700 | N/A
DIGITAL INPUT STATUS | Close (Status Of Command) | 700 | N/A
DIGITAL INPUT STATUS | Low Low Level | 700 | N/A
DIGITAL INPUT STATUS | Low Level | 700 | N/A
DIGITAL INPUT STATUS | Mid Level | 700 | N/A
DIGITAL INPUT STATUS | High Level | 700 | N/A
DIGITAL INPUT STATUS | High High Level | 700 | N/A
DIGITAL INPUT STATUS | Status | 700 | N/A
DIGITAL INPUT STATUS | Reverse | 700 | N/A
DIGITAL INPUT STATUS | Forward | 700 | N/A
DIGITAL INPUT STATUS | Off | N/A | N/A
DIGITAL INPUT STATUS | Estop Status | 700 | N/A
DIGITAL INPUT STATUS | Plant Auto Mode | 700 | N/A
DIGITAL INPUT STATUS | Scan Status | 700 | N/A
DIGITAL INPUT STATUS | Group Unacknowledged | 700 | N/A
DIGITAL INPUT STATUS | Plant Manual Mode Status | 700 | N/A
DIGITAL INPUT STATUS | Legal Entry | 700 | N/A
DIGITAL INPUT STATUS | Device Enabled | 700 | N/A
DIGITAL INPUT STATUS | Slow | 700 | N/A
DIGITAL INPUT STATUS | Fast | 700 | N/A
DIGITAL INPUT STATUS | Digital Level | 700 | N/A
DIGITAL INPUT STATUS | Vacuum Alarm (Raw) | 700 | N/A
DIGITAL INPUT STATUS | Discharge Position Status | 700 | N/A
DIGITAL INPUT STATUS | Enable | 700 | N/A
DIGITAL INPUT STATUS | Constant Speed | 700 | N/A
DIGITAL INPUT STATUS | Suction Position Status | 700 | N/A
DIGITAL INPUT STATUS | Auxillary Status | 700 | N/A
DIGITAL INPUT STATUS | VFD On Bypass | 700 | N/A
DIGITAL INPUT STATUS | Name (HMI) | 700 | N/A
DIGITAL INPUT STATUS | Duty Assignment Update Error | 700 | N/A
DIGITAL INPUT STATUS | Pump Stop Float/Stop Relay Hardwired To Equipment | 700 | N/A
DIGITAL INPUT STATUS | Pump Start Float/Start Relay Hardwired To Equipment | 700 | N/A
DIGITAL INPUT STATUS | Download To Processor | 700 | N/A
DIGITAL INPUT STATUS | Processor In Program Mode | 700 | N/A
DIGITAL INPUT STATUS | Processor In Run Mode | 700 | N/A
DIGITAL INPUT STATUS | Online Edit In Process | 700 | N/A
FRAGMENT 5 | SIGNAL TYPE | EVENT PRIORITY | ALARM PRIORITY
ANALOG INPUT ALARM | High High Alarm | N/A | 90
ANALOG INPUT ALARM | High Alarm | N/A | 90
ANALOG INPUT ALARM | Low Alarm | N/A | 90
ANALOG INPUT ALARM | Low Low Alarm | N/A | 90
ANALOG INPUT ALARM | Rate Of Change | N/A | 190
FRAGMENT 5 | SIGNAL TYPE | EVENT PRIORITY | ALARM PRIORITY
DIGITAL INPUT ALARM | Signal Error Alarm ( Outside Of Range) | N/A | 94
DIGITAL INPUT ALARM | Analog Signal Open Circiut | N/A | 9
DIGITAL INPUT ALARM | Stroke Deviation Alarm | N/A | 330
DIGITAL INPUT ALARM | Analog Signal Loss Of Echo | N/A | 9
DIGITAL INPUT ALARM | Temperature High | N/A | 56
DIGITAL INPUT ALARM | Temperature Low | N/A | 57
DIGITAL INPUT ALARM | Temperature Alarm | N/A | 58
DIGITAL INPUT ALARM | Temp/Leak Alarm (Flyght Minicas Alarm) | N/A | 58
DIGITAL INPUT ALARM | Temperature Warning | N/A | 322
DIGITAL INPUT ALARM | Bearing Temp | N/A | 200
DIGITAL INPUT ALARM | Winding Temp | N/A | 200
DIGITAL INPUT ALARM | Pressure High | N/A | 59
DIGITAL INPUT ALARM | Pressure Low | N/A | 60
DIGITAL INPUT ALARM | Pressure Alarm | N/A | 62
DIGITAL INPUT ALARM | Backup Stop Relay | N/A | 9
DIGITAL INPUT ALARM | Backup Start Relay | N/A | 9
DIGITAL INPUT ALARM | Level High | N/A | 61
DIGITAL INPUT ALARM | Level Low | N/A | 68
DIGITAL INPUT ALARM | Level Alarm | N/A | 69
DIGITAL INPUT ALARM | Level Warning | N/A | 356
DIGITAL INPUT ALARM | Flow Alarm | N/A | 80
DIGITAL INPUT ALARM | Flow Warning | N/A | 360
DIGITAL INPUT ALARM | Density High | N/A | 169
DIGITAL INPUT ALARM | Density Low | N/A | 168
DIGITAL INPUT ALARM | Density Alarm | N/A | 170
DIGITAL INPUT ALARM | Density Warning | N/A | 362
DIGITAL INPUT ALARM | Oxygen High | N/A | 240
DIGITAL INPUT ALARM | Oxygen Low | N/A | 242
DIGITAL INPUT ALARM | Oxygen Alarm | N/A | 172
DIGITAL INPUT ALARM | Oxygen Failure | N/A | 174
DIGITAL INPUT ALARM | Oxygen Warning | N/A | 364
DIGITAL INPUT ALARM | General Alarm | N/A | 55
DIGITAL INPUT ALARM | General Fault | N/A | 112
DIGITAL INPUT ALARM | General Failure | N/A | 114
DIGITAL INPUT ALARM | General Warning/Pre-Alarm | N/A | 200
DIGITAL INPUT ALARM | Ground Alarm | N/A | 72
DIGITAL INPUT ALARM | Ground Fault | N/A | 132
DIGITAL INPUT ALARM | Ground Failure | N/A | 130
DIGITAL INPUT ALARM | Overload Alarm | N/A | 63
DIGITAL INPUT ALARM | Overload Warning | N/A | 352
DIGITAL INPUT ALARM | Overcurrent Alarm | N/A | 74
DIGITAL INPUT ALARM | Overcurrent Warning | N/A | 340
DIGITAL INPUT ALARM | Over Volt Alarm | N/A | 76
DIGITAL INPUT ALARM | Over Volt Warning | N/A | 342
DIGITAL INPUT ALARM | Gas Detector Alarm | N/A | 10
DIGITAL INPUT ALARM | Gas Detector Fault | N/A | 12
DIGITAL INPUT ALARM | Gas Detector Warning | N/A | 310
DIGITAL INPUT ALARM | Motion Fail/ No Motion | N/A | 200
DIGITAL INPUT ALARM | Power High | N/A | 47
DIGITAL INPUT ALARM | Power Low | N/A | 210
DIGITAL INPUT ALARM | Power Alarm | N/A | 49
DIGITAL INPUT ALARM | Power Output | N/A | 140
DIGITAL INPUT ALARM | Power Failure | N/A | 48
DIGITAL INPUT ALARM | Power Warning | N/A | 350
DIGITAL INPUT ALARM | Over Torque Alarm | N/A | 66
DIGITAL INPUT ALARM | Over Torque Warning | N/A | 324
DIGITAL INPUT ALARM | Vibrator Alarm | N/A | 67
DIGITAL INPUT ALARM | Vibrator Failure | N/A | 120
DIGITAL INPUT ALARM | Vibrator Warning | N/A | 326
DIGITAL INPUT ALARM | Entry/Exit Illegal | N/A | 9
DIGITAL INPUT ALARM | Loss Of Seal Water Alarm | N/A | 77
DIGITAL INPUT ALARM | Loss Of Seal Water Warning | N/A | 330
DIGITAL INPUT ALARM | Loss Of Prime Alarm | N/A | 64
DIGITAL INPUT ALARM | Loss Of Prime Warning | N/A | 332
DIGITAL INPUT ALARM | Flood Alarm | N/A | 9
DIGITAL INPUT ALARM | Fail To Start/Open | N/A | 51
DIGITAL INPUT ALARM | Fail To Stop/Close | N/A | 52
DIGITAL INPUT ALARM | Uncommanded Start/Open | N/A | 53
DIGITAL INPUT ALARM | Uncommanded Stop/Close | N/A | 54
DIGITAL INPUT ALARM | Emergency Stop Button | N/A | 50
DIGITAL INPUT ALARM | Discharge Fail | N/A | 95
DIGITAL INPUT ALARM | Uncommanded Discharge | N/A | 154
DIGITAL INPUT ALARM | Fire/Smoke Alarm | N/A | 1
DIGITAL INPUT ALARM | Out Of Balance Alarm | N/A | 97
DIGITAL INPUT ALARM | Dv Valve Position Alarm | N/A | 86
DIGITAL INPUT ALARM | Alarm - Pump On - Valve Not Opened | N/A | 84
DIGITAL INPUT ALARM | Setpoint Entry Error | N/A | 350
DIGITAL INPUT ALARM | Communication Alarm | N/A | 9
DIGITAL INPUT ALARM | Setpoint Deviation (Calibration)Alm | N/A | 108
DIGITAL INPUT ALARM | Vacuum Alarm | N/A | 65
DIGITAL INPUT ALARM | Suction Fail | N/A | 96
DIGITAL INPUT ALARM | Advance Fail | N/A | 98
DIGITAL INPUT ALARM | Runtime Warning | N/A | 350
DIGITAL INPUT ALARM | Timing Fault | N/A | 180
DIGITAL INPUT ALARM | Maximum Allowable Starts | N/A | 370
DIGITAL INPUT STATUS | Emergency Power | N/A | 20
DIGITAL INPUT STATUS | Dasabtcp Server Failed | N/A | 20
DIGITAL INPUT ALARM | Dasabcip Server Failed | N/A | 20
DIGITAL INPUT ALARM | Lockout | N/A | 374
DIGITAL INPUT ALARM | Download To Processor Alarm | N/A | 50
DIGITAL INPUT ALARM | Processor Not In Run Mode Alarm | N/A | 50
DIGITAL INPUT ALARM | Online Edit In Process Alarm | N/A | 50

## Fragment 4,5 - Priorities Water
TABLE 2A-4.3 FRAGMENT 4 AND 5 WATER ALARMS AND EVENTS PRIORITIES
SEVERITY | ALARM/CATEGORY | EVENT PRIORITY | ALARM PRIORITY
CRITICAL - COMPLIANCE | Chlorine Low Low Alarm | N/A | 1
CRITICAL - COMPLIANCE | Chlorine High High Alarm | N/A | 2
CRITICAL - COMPLIANCE | Turbidity High High Alarm | N/A | 3
CRITICAL - COMPLIANCE | Fluoride Low Low Alarm | N/A | 4
CRITICAL - COMPLIANCE | Fluoride High High Alarm | N/A | 5
CRITICAL - COMPLIANCE | Ozone Low Low Alarm | N/A | 6
CRITICAL - COMPLIANCE | Ozone High High Alarm | N/A | 7
CRITICAL - COMPLIANCE | Flow Low Low Alarm | N/A | 8
CRITICAL - COMPLIANCE | Flow High High Alarm | N/A | 9
CRITICAL - COMPLIANCE | Uv Dose Low Low Alarm | N/A | 10
CRITICAL - COMPLIANCE | Transmittance Low Low Alarm | N/A | 11
CRITICAL - COMPLIANCE | Uv Intensity Low Low Alarm | N/A | 12
CRITICAL - COMPLIANCE | Inactivation Virus Low Low Alarm | N/A | 13
CRITICAL - COMPLIANCE | Inactivation Giardi Low Low Alarm | N/A | 14
CRITICAL - COMPLIANCE | Inactivation Crypto Low Low Alarm | N/A | 15
CRITICAL - COMPLIANCE | Ct Giardi Low Low Alarm | N/A | 16
CRITICAL - COMPLIANCE | Ct Crypto Low Low Alarm | N/A | 17
CRITICAL - COMPLIANCE | Coagulant Dose Low Low Alarm | N/A | 18
CRITICAL - COMPLIANCE | Level HH | N/A | 19
CRITICAL - COMPLIANCE | Level LL | N/A | 20
CRITICAL - COMPLIANCE | Not Used | N/A | 21
CRITICAL - COMPLIANCE | Not Used | N/A | 22
CRITICAL - COMPLIANCE | Not Used | N/A | 23
CRITICAL - COMPLIANCE | Not Used | N/A | 24
CRITICAL - COMPLIANCE | Not Used | N/A | 25
CRITICAL - COMPLIANCE | Not Used | N/A | 26
CRITICAL - COMPLIANCE | Not Used | N/A | 27
CRITICAL - COMPLIANCE | Not Used | N/A | 28
CRITICAL - COMPLIANCE | Not Used | N/A | 29
CRITICAL - COMPLIANCE | Not Used | N/A | 30
CRITICAL - COMPLIANCE | Not Used | N/A | 31
CRITICAL - COMPLIANCE | Not Used | N/A | 32
CRITICAL - COMPLIANCE | Not Used | N/A | 33
CRITICAL - COMPLIANCE | Not Used | N/A | 34
CRITICAL - COMPLIANCE | Not Used | N/A | 35
CRITICAL - COMPLIANCE | Not Used | N/A | 36
CRITICAL - COMPLIANCE | Not Used | N/A | 37
CRITICAL - COMPLIANCE | Not Used | N/A | 38
CRITICAL - COMPLIANCE | Not Used | N/A | 39
CRITICAL - COMPLIANCE | Not Used | N/A | 40
CRITICAL - COMPLIANCE | Not Used | N/A | 41
CRITICAL - COMPLIANCE | Not Used | N/A | 42
CRITICAL - COMPLIANCE | Not Used | N/A | 43
CRITICAL - COMPLIANCE | Not Used | N/A | 44
CRITICAL - COMPLIANCE | Not Used | N/A | 45
CRITICAL - COMPLIANCE | Not Used | N/A | 46
CRITICAL - COMPLIANCE | Not Used | N/A | 47
CRITICAL - COMPLIANCE | Not Used | N/A | 48
CRITICAL - COMPLIANCE | Not Used | N/A | 49
CRITICAL - COMPLIANCE | Not Used | N/A | 50
CRITICAL - NON-COMPLIANCE | Blower | N/A | 51
CRITICAL - NON-COMPLIANCE | Chlorination System | N/A | 52
CRITICAL - NON-COMPLIANCE | Chlorine Residual | N/A | 53
CRITICAL - NON-COMPLIANCE | Coagulant | N/A | 54
CRITICAL - NON-COMPLIANCE | Communication | N/A | 55
CRITICAL - NON-COMPLIANCE | Dialer Channel Active | N/A | 56
CRITICAL - NON-COMPLIANCE | Dialer Verification System | N/A | 57
CRITICAL - NON-COMPLIANCE | Filter | N/A | 58
CRITICAL - NON-COMPLIANCE | Fire / Smoke | N/A | 59
CRITICAL - NON-COMPLIANCE | Flood | N/A | 60
CRITICAL - NON-COMPLIANCE | Flow | N/A | 61
CRITICAL - NON-COMPLIANCE | Flow Total | N/A | 62
CRITICAL - NON-COMPLIANCE | Fluoridation System | N/A | 63
CRITICAL - NON-COMPLIANCE | Fluoride Residual | N/A | 64
CRITICAL - NON-COMPLIANCE | Gas Detection | N/A | 65
CRITICAL - NON-COMPLIANCE | Generator / Ats | N/A | 66
CRITICAL - NON-COMPLIANCE | Level | N/A | 67
CRITICAL - NON-COMPLIANCE | Membrane System | N/A | 68
CRITICAL - NON-COMPLIANCE | Ozone | N/A | 69
CRITICAL - NON-COMPLIANCE | Particle Counter | N/A | 70
CRITICAL - NON-COMPLIANCE | Plant Shut Down | N/A | 71
CRITICAL - NON-COMPLIANCE | PLC | N/A | 72
CRITICAL - NON-COMPLIANCE | Potasium System | N/A | 73
CRITICAL - NON-COMPLIANCE | Power | N/A | 74
CRITICAL - NON-COMPLIANCE | Pressure | N/A | 75
CRITICAL - NON-COMPLIANCE | Pump | N/A | 76
CRITICAL - NON-COMPLIANCE | Hlp | N/A | 77
CRITICAL - NON-COMPLIANCE | Llp | N/A | 78
CRITICAL - NON-COMPLIANCE | Security (Health/ Safety) | N/A | 79
CRITICAL - NON-COMPLIANCE | Server / Workstation | N/A | 80
CRITICAL - NON-COMPLIANCE | Temperature | N/A | 81
CRITICAL - NON-COMPLIANCE | Turbidity | N/A | 82
CRITICAL - NON-COMPLIANCE | UV | N/A | 83
CRITICAL - NON-COMPLIANCE | Valve | N/A | 84
CRITICAL - NON-COMPLIANCE | Waste System | N/A | 85
CRITICAL - NON-COMPLIANCE | Weight | N/A | 86
CRITICAL - NON-COMPLIANCE | pH | N/A | 87
CRITICAL - NON-COMPLIANCE | Environmental | N/A | 88
CRITICAL - NON-COMPLIANCE | Weather | N/A | 89
CRITICAL - NON-COMPLIANCE | Health And Safety | N/A | 90
CRITICAL - NON-COMPLIANCE | Dechlorination | N/A | 91
CRITICAL - NON-COMPLIANCE | Actiflo | N/A | 92
CRITICAL - NON-COMPLIANCE | Not Used | N/A | 93
CRITICAL - NON-COMPLIANCE | Not Used | N/A | 94
CRITICAL - NON-COMPLIANCE | Not Used | N/A | 95
CRITICAL - NON-COMPLIANCE | Not Used | N/A | 96
CRITICAL - NON-COMPLIANCE | Not Used | N/A | 97
CRITICAL - NON-COMPLIANCE | Not Used | N/A | 98
CRITICAL - NON-COMPLIANCE | Not Used | N/A | 99
SEVERITY | ALARM/CATEGORY | EVENT PRIORITY | ALARM PRIORITY
Actiflow
NON-CRITICAL | Setpoint Non-Critical | 200 | N/A
NON-CRITICAL | Not Used | 201
NON-CRITICAL | Not Used | 202
NON-CRITICAL | Digital Inputs/Pushbuttons | 203 | N/A
NON-CRITICAL | Not Used | 204
NON-CRITICAL | Not Used | 205
NON-CRITICAL | Digital Outputs | 206 | N/A
NON-CRITICAL | Not Used | 207
NON-CRITICAL | Not Used | 208
NON-CRITICAL | Analog Alarms | N/A | 209
NON-CRITICAL | Not Used | 210
NON-CRITICAL | Not Used | 211
NON-CRITICAL | Alarm Inputs | N/A | 212
NON-CRITICAL | Not Used | 213
NON-CRITICAL | Not Used | 214
Alarm Enable
NON-CRITICAL | Alarm Enable Non-Critical | 215 | N/A
NON-CRITICAL | Not Used | 216
NON-CRITICAL | Not Used | 217
NON-CRITICAL | Alarm Enable Critical | N/A | 218
NON-CRITICAL | Not Used | 219
NON-CRITICAL | Not Used | 220
Blower
NON-CRITICAL | Setpoint Non-Critical | 221 | N/A
NON-CRITICAL | Not Used | 222
NON-CRITICAL | Not Used | 223
NON-CRITICAL | Digital Inputs/Pushbuttons | 224 | N/A
NON-CRITICAL | Not Used | 225
NON-CRITICAL | Not Used | 226
NON-CRITICAL | Digital Outputs | 227 | N/A
NON-CRITICAL | Not Used | 228
NON-CRITICAL | Not Used | 229
NON-CRITICAL | Analog Alarms | N/A | 230
NON-CRITICAL | Not Used | 231
NON-CRITICAL | Not Used | 232
NON-CRITICAL | Alarm Inputs | N/A | 233
NON-CRITICAL | Not Used | 234
NON-CRITICAL | Not Used | 235
Chlorination System
NON-CRITICAL | Setpoint Non-Critical | 236 | N/A
NON-CRITICAL | Not Used | 237
NON-CRITICAL | Not Used | 238
NON-CRITICAL | Digital Inputs/Pushbuttons | 239 | N/A
NON-CRITICAL | Not Used | 240
NON-CRITICAL | Not Used | 241
NON-CRITICAL | Digital Outputs | 242 | N/A
NON-CRITICAL | Not Used | 243
NON-CRITICAL | Not Used | 244
NON-CRITICAL | Analog Alarms | N/A | 245
NON-CRITICAL | Not Used | 246
NON-CRITICAL | Not Used | 247
NON-CRITICAL | Alarm Inputs | N/A | 248
NON-CRITICAL | Not Used | 249
NON-CRITICAL | Not Used | 250
Chlorine Residual
NON-CRITICAL | Setpoint Non-Critical | 251 | N/A
NON-CRITICAL | Not Used | 252
NON-CRITICAL | Not Used | 253
NON-CRITICAL | Digital Inputs/Pushbuttons | 254 | N/A
NON-CRITICAL | Not Used | 255
NON-CRITICAL | Not Used | 256
NON-CRITICAL | Digital Outputs | 257 | N/A
NON-CRITICAL | Not Used | 258
NON-CRITICAL | Not Used | 259
NON-CRITICAL | Analog Alarms | N/A | 260
NON-CRITICAL | Not Used | 261
NON-CRITICAL | Not Used | 262
NON-CRITICAL | Alarm Inputs | N/A | 263
NON-CRITICAL | Not Used | 264
NON-CRITICAL | Not Used | 265
Coagulant
NON-CRITICAL | Setpoint Non-Critical | 266 | N/A
NON-CRITICAL | Not Used | 267
NON-CRITICAL | Not Used | 268
NON-CRITICAL | Digital Inputs/Pushbuttons | 269 | N/A
NON-CRITICAL | Not Used | 270
NON-CRITICAL | Not Used | 271
NON-CRITICAL | Digital Outputs | 272 | N/A
NON-CRITICAL | Not Used | 273
NON-CRITICAL | Not Used | 274
NON-CRITICAL | Analog Alarms | N/A | 275
NON-CRITICAL | Not Used | 276
NON-CRITICAL | Not Used | 277
NON-CRITICAL | Alarm Inputs | N/A | 278
NON-CRITICAL | Not Used | 279
NON-CRITICAL | Not Used | 280
Communication
NON-CRITICAL | PLC - PLC Alarms | N/A | 281
NON-CRITICAL | Not Used | 282
NON-CRITICAL | Not Used | 283
NON-CRITICAL | Io Server Alarms | N/A | 284
NON-CRITICAL | Not Used | 285
NON-CRITICAL | Not Used | 286
NON-CRITICAL | Hmi - Plc Alarms | N/A | 287
NON-CRITICAL | Not Used | 288
NON-CRITICAL | Not Used | 289
Density
NON-CRITICAL | Setpoint Non-Critical | 290 | N/A
NON-CRITICAL | Not Used | 291
NON-CRITICAL | Not Used | 292
NON-CRITICAL | Digital Inputs/Pushbuttons | 293 | N/A
NON-CRITICAL | Not Used | 294
NON-CRITICAL | Not Used | 295
NON-CRITICAL | Digital Outputs | 296 | N/A
NON-CRITICAL | Not Used | 297
NON-CRITICAL | Not Used | 298
NON-CRITICAL | Analog Alarms | N/A | 299
NON-CRITICAL | Not Used | 300
NON-CRITICAL | Not Used | 301
NON-CRITICAL | Alarm Inputs | N/A | 302
NON-CRITICAL | Not Used | 303
NON-CRITICAL | Not Used | 304
Dialer Enable
NON-CRITICAL | Dialer Enable | 305 | N/A
NON-CRITICAL | Not Used | 306
NON-CRITICAL | Not Used | 307
Dialer Channel
NON-CRITICAL | Dialer Enable | 308 | N/A
NON-CRITICAL | Not Used | 309
NON-CRITICAL | Not Used | 310
NON-CRITICAL | Raw Enable | 311 | N/A
NON-CRITICAL | Dialer Channel Active | N/A | 312
NON-CRITICAL | Not Used | 313
Dialer Verification System
NON-CRITICAL | Setpoint Non-Critical | 314 | N/A
NON-CRITICAL | Not Used | 315
NON-CRITICAL | Not Used | 316
NON-CRITICAL | Digital Inputs/Pushbuttons | 317 | N/A
NON-CRITICAL | Not Used | 318
NON-CRITICAL | Not Used | 319
NON-CRITICAL | Digital Outputs | 320 | N/A
NON-CRITICAL | Not Used | 321
NON-CRITICAL | Not Used | 322
NON-CRITICAL | Analog Alarms | N/A | 323
NON-CRITICAL | Not Used | 324
NON-CRITICAL | Not Used | 325
NON-CRITICAL | Alarm Inputs | N/A | 326
NON-CRITICAL | Not Used | 327
NON-CRITICAL | Not Used | 328
Filter
NON-CRITICAL | Setpoint Non-Critical | 329 | N/A
NON-CRITICAL | Not Used | 330
NON-CRITICAL | Not Used | 331
NON-CRITICAL | Digital Inputs/Pushbuttons | 332 | N/A
NON-CRITICAL | Not Used | 333
NON-CRITICAL | Not Used | 334
NON-CRITICAL | Digital Outputs | 335 | N/A
NON-CRITICAL | Not Used | 336
NON-CRITICAL | Not Used | 337
NON-CRITICAL | Analog Alarms | N/A | 338
NON-CRITICAL | Not Used | 339
NON-CRITICAL | Not Used | 340
NON-CRITICAL | Alarm Inputs | N/A | 341
NON-CRITICAL | Not Used | 342
NON-CRITICAL | Not Used | 343
Fire / Smoke
NON-CRITICAL | Setpoint Non-Critical | 344 | N/A
NON-CRITICAL | Not Used | 345
NON-CRITICAL | Not Used | 346
NON-CRITICAL | Digital Inputs/Pushbuttons | 347 | N/A
NON-CRITICAL | Not Used | 348
NON-CRITICAL | Not Used | 349
NON-CRITICAL | Digital Outputs | 350 | N/A
NON-CRITICAL | Not Used | 351
NON-CRITICAL | Not Used | 352
NON-CRITICAL | Analog Alarms | N/A | 353
NON-CRITICAL | Not Used | 354
NON-CRITICAL | Not Used | 355
NON-CRITICAL | Alarm Inputs | N/A | 356
NON-CRITICAL | Not Used | 357
NON-CRITICAL | Not Used | 358
Flood
NON-CRITICAL | Setpoint Non-Critical | 359 | N/A
NON-CRITICAL | Not Used | 360
NON-CRITICAL | Not Used | 361
NON-CRITICAL | Digital Inputs/Pushbuttons | 362 | N/A
NON-CRITICAL | Not Used | 363
NON-CRITICAL | Not Used | 364
NON-CRITICAL | Digital Outputs | 365 | N/A
NON-CRITICAL | Not Used | 366
NON-CRITICAL | Not Used | 367
NON-CRITICAL | Analog Alarms | N/A | 368
NON-CRITICAL | Not Used | 369
NON-CRITICAL | Not Used | 370
NON-CRITICAL | Alarm Inputs | N/A | 371
NON-CRITICAL | Not Used | 372
NON-CRITICAL | Not Used | 373
Flow
NON-CRITICAL | Setpoint Non-Critical | 374 | N/A
NON-CRITICAL | Not Used | 375
NON-CRITICAL | Not Used | 376
NON-CRITICAL | Digital Inputs/Pushbuttons | 377 | N/A
NON-CRITICAL | Not Used | 378
NON-CRITICAL | Not Used | 379
NON-CRITICAL | Digital Outputs | 380 | N/A
NON-CRITICAL | Not Used | 381
NON-CRITICAL | Not Used | 382
NON-CRITICAL | Analog Alarms | N/A | 383
NON-CRITICAL | Not Used | 384
NON-CRITICAL | Not Used | 385
NON-CRITICAL | Alarm Inputs | N/A | 386
NON-CRITICAL | Not Used | 387
NON-CRITICAL | Not Used | 388
Flow Total
NON-CRITICAL | Setpoint Non-Critical | 389 | N/A
NON-CRITICAL | Not Used | 390
NON-CRITICAL | Not Used | 391
NON-CRITICAL | Digital Inputs/Pushbuttons | 392 | N/A
NON-CRITICAL | Not Used | 393
NON-CRITICAL | Not Used | 394
NON-CRITICAL | Digital Outputs | 395 | N/A
NON-CRITICAL | Not Used | 396
NON-CRITICAL | Not Used | 397
NON-CRITICAL | Analog Alarms | N/A | 398
NON-CRITICAL | Not Used | 399
NON-CRITICAL | Not Used | 400
NON-CRITICAL | Alarm Inputs | N/A | 401
NON-CRITICAL | Not Used | 402
NON-CRITICAL | Not Used | 403
Fluoridation System
NON-CRITICAL | Setpoint Non-Critical | 404 | N/A
NON-CRITICAL | Not Used | 405
NON-CRITICAL | Not Used | 406
NON-CRITICAL | Digital Inputs/Pushbuttons | 407 | N/A
NON-CRITICAL | Not Used | 408
NON-CRITICAL | Not Used | 409
NON-CRITICAL | Digital Outputs | 410 | N/A
NON-CRITICAL | Not Used | 411
NON-CRITICAL | Not Used | 412
NON-CRITICAL | Analog Alarms | N/A | 413
NON-CRITICAL | Not Used | 414
NON-CRITICAL | Not Used | 415
NON-CRITICAL | Alarm Inputs | N/A | 416
NON-CRITICAL | Not Used | 417
NON-CRITICAL | Not Used | 418
Fluoride Residual
NON-CRITICAL | Setpoint Non-Critical | 419 | N/A
NON-CRITICAL | Not Used | 420
NON-CRITICAL | Not Used | 421
NON-CRITICAL | Digital Inputs/Pushbuttons | 422 | N/A
NON-CRITICAL | Not Used | 423
NON-CRITICAL | Not Used | 424
NON-CRITICAL | Digital Outputs | 425 | N/A
NON-CRITICAL | Not Used | 426
NON-CRITICAL | Not Used | 427
NON-CRITICAL | Analog Alarms | N/A | 428
NON-CRITICAL | Not Used | 429
NON-CRITICAL | Not Used | 430
NON-CRITICAL | Alarm Inputs | N/A | 431
NON-CRITICAL | Not Used | 432
NON-CRITICAL | Not Used | 433
Gas Detection
NON-CRITICAL | Setpoint Non-Critical | 434 | N/A
NON-CRITICAL | Not Used | 435
NON-CRITICAL | Not Used | 436
NON-CRITICAL | Digital Inputs/Pushbuttons | 437 | N/A
NON-CRITICAL | Not Used | 438
NON-CRITICAL | Not Used | 439
NON-CRITICAL | Digital Outputs | 440 | N/A
NON-CRITICAL | Not Used | 441
NON-CRITICAL | Not Used | 442
NON-CRITICAL | Analog Alarms | N/A | 443
NON-CRITICAL | Not Used | 444
NON-CRITICAL | Not Used | 445
NON-CRITICAL | Alarm Inputs | N/A | 446
NON-CRITICAL | Not Used | 447
NON-CRITICAL | Not Used | 448
Generator / Ats
NON-CRITICAL | Setpoint Non-Critical | 449 | N/A
NON-CRITICAL | Not Used | 450
NON-CRITICAL | Not Used | 451
NON-CRITICAL | Digital Inputs/Pushbuttons | 452 | N/A
NON-CRITICAL | Not Used | 453
NON-CRITICAL | Not Used | 454
NON-CRITICAL | Digital Outputs | 455 | N/A
NON-CRITICAL | Not Used | 456
NON-CRITICAL | Not Used | 457
NON-CRITICAL | Analog Alarms | N/A | 458
NON-CRITICAL | Not Used | 459
NON-CRITICAL | Not Used | 460
NON-CRITICAL | Alarm Inputs | N/A | 461
NON-CRITICAL | Not Used | 462
NON-CRITICAL | Not Used | 463
Hydrogen Peroxide
NON-CRITICAL | Setpoint Non-Critical | 464 | N/A
NON-CRITICAL | Not Used | 465
NON-CRITICAL | Not Used | 466
NON-CRITICAL | Digital Inputs/Pushbuttons | 467 | N/A
NON-CRITICAL | Not Used | 468
NON-CRITICAL | Not Used | 469
NON-CRITICAL | Digital Outputs | 470 | N/A
NON-CRITICAL | Not Used | 471
NON-CRITICAL | Not Used | 472
NON-CRITICAL | Analog Alarms | N/A | 473
NON-CRITICAL | Not Used | 474
NON-CRITICAL | Not Used | 475
NON-CRITICAL | Alarm Inputs | N/A | 476
NON-CRITICAL | Not Used | 477
NON-CRITICAL | Not Used | 478
Level
NON-CRITICAL | Setpoint Non-Critical | 479 | N/A
NON-CRITICAL | Not Used | 480
NON-CRITICAL | Not Used | 481
NON-CRITICAL | Digital Inputs/Pushbuttons | 482 | N/A
NON-CRITICAL | Not Used | 483
NON-CRITICAL | Not Used | 484
NON-CRITICAL | Digital Outputs | 485 | N/A
NON-CRITICAL | Not Used | 486
NON-CRITICAL | Not Used | 487
NON-CRITICAL | Analog Alarms | N/A | 488
NON-CRITICAL | Not Used | 489
NON-CRITICAL | Not Used | 490
NON-CRITICAL | Alarm Inputs | N/A | 491
NON-CRITICAL | Not Used | 492
NON-CRITICAL | Not Used | 493
Membrane System
NON-CRITICAL | Setpoint Non-Critical | 494 | N/A
NON-CRITICAL | Not Used | 495
NON-CRITICAL | Not Used | 496
NON-CRITICAL | Digital Inputs/Pushbuttons | 497 | N/A
NON-CRITICAL | Not Used | 498
NON-CRITICAL | Not Used | 499
NON-CRITICAL | Digital Outputs | 500 | N/A
NON-CRITICAL | Not Used | 501
NON-CRITICAL | Not Used | 502
NON-CRITICAL | Analog Alarms | N/A | 503
NON-CRITICAL | Not Used | 504
NON-CRITICAL | Not Used | 505
NON-CRITICAL | Alarm Inputs | N/A | 506
NON-CRITICAL | Not Used | 507
NON-CRITICAL | Not Used | 508
Motor
NON-CRITICAL | Setpoint Non-Critical | 509 | N/A
NON-CRITICAL | Not Used | 510
NON-CRITICAL | Not Used | 511
NON-CRITICAL | Digital Inputs/Pushbuttons | 512 | N/A
NON-CRITICAL | Not Used | 513
NON-CRITICAL | Not Used | 514
NON-CRITICAL | Digital Outputs | 515 | N/A
NON-CRITICAL | Not Used | 516
NON-CRITICAL | Not Used | 517
NON-CRITICAL | Analog Alarms | N/A | 518
NON-CRITICAL | Not Used | 519
NON-CRITICAL | Not Used | 520
NON-CRITICAL | Alarm Inputs | N/A | 521
NON-CRITICAL | Not Used | 522
NON-CRITICAL | Not Used | 523
Ozone
NON-CRITICAL | Setpoint Non-Critical | 524 | N/A
NON-CRITICAL | Not Used | 525
NON-CRITICAL | Not Used | 526
NON-CRITICAL | Digital Inputs/Pushbuttons | 527 | N/A
NON-CRITICAL | Not Used | 528
NON-CRITICAL | Not Used | 205
NON-CRITICAL | Digital Outputs | 530 | N/A
NON-CRITICAL | Not Used | 531
NON-CRITICAL | Not Used | 532
NON-CRITICAL | Analog Alarms | N/A | 533
NON-CRITICAL | Not Used | 534
NON-CRITICAL | Not Used | 535
NON-CRITICAL | Alarm Inputs | N/A | 536
NON-CRITICAL | Not Used | 537
NON-CRITICAL | Not Used | 538
Particle Counter
NON-CRITICAL | Setpoint Non-Critical | 539 | N/A
NON-CRITICAL | Not Used | 540
NON-CRITICAL | Not Used | 541
NON-CRITICAL | Digital Inputs/Pushbuttons | 542 | N/A
NON-CRITICAL | Not Used | 543
NON-CRITICAL | Not Used | 544
NON-CRITICAL | Digital Outputs | 545 | N/A
NON-CRITICAL | Not Used | 546
NON-CRITICAL | Not Used | 547
NON-CRITICAL | Analog Alarms | N/A | 548
NON-CRITICAL | Not Used | 549
NON-CRITICAL | Not Used | 550
NON-CRITICAL | Alarm Inputs | N/A | 551
NON-CRITICAL | Not Used | 552
NON-CRITICAL | Not Used | 553
Plant Shut Down
NON-CRITICAL | Setpoint Non-Critical | 554 | N/A
NON-CRITICAL | Not Used | 555
NON-CRITICAL | Not Used | 556
NON-CRITICAL | Digital Inputs/Pushbuttons | 557 | N/A
NON-CRITICAL | Not Used | 558
NON-CRITICAL | Not Used | 559
NON-CRITICAL | Digital Outputs | 560 | N/A
NON-CRITICAL | Not Used | 561
NON-CRITICAL | Not Used | 562
NON-CRITICAL | Analog Alarms | N/A | 563
NON-CRITICAL | Not Used | 564
NON-CRITICAL | Not Used | 565
NON-CRITICAL | Alarm Inputs | N/A | 566
NON-CRITICAL | Not Used | 567
NON-CRITICAL | Not Used | 568
PLC
NON-CRITICAL | Setpoint Non-Critical | 569 | N/A
NON-CRITICAL | Not Used | 570
NON-CRITICAL | Not Used | 571
NON-CRITICAL | Digital Inputs/Pushbuttons | 572 | N/A
NON-CRITICAL | Not Used | 573
NON-CRITICAL | Not Used | 574
NON-CRITICAL | Digital Outputs | 575 | N/A
NON-CRITICAL | Not Used | 576
NON-CRITICAL | Not Used | 577
NON-CRITICAL | Analog Alarms | N/A | 578
NON-CRITICAL | Not Used | 579
NON-CRITICAL | Not Used | 580
NON-CRITICAL | Alarm Inputs | N/A | 581
NON-CRITICAL | Not Used | 582
NON-CRITICAL | Not Used | 583
Potasium System
NON-CRITICAL | Setpoint Non-Critical | 584 | N/A
NON-CRITICAL | Not Used | 585
NON-CRITICAL | Not Used | 586
NON-CRITICAL | Digital Inputs/Pushbuttons | 587 | N/A
NON-CRITICAL | Not Used | 588
NON-CRITICAL | Not Used | 589
NON-CRITICAL | Digital Outputs | 590 | N/A
NON-CRITICAL | Not Used | 591
NON-CRITICAL | Not Used | 592
NON-CRITICAL | Analog Alarms | N/A | 593
NON-CRITICAL | Not Used | 594
NON-CRITICAL | Not Used | 595
NON-CRITICAL | Alarm Inputs | N/A | 596
NON-CRITICAL | Not Used | 597
NON-CRITICAL | Not Used | 598
Power
NON-CRITICAL | Setpoint Non-Critical | 599 | N/A
NON-CRITICAL | Not Used | 600
NON-CRITICAL | Not Used | 601
NON-CRITICAL | Digital Inputs/Pushbuttons | 602 | N/A
NON-CRITICAL | Not Used | 603
NON-CRITICAL | Not Used | 604
NON-CRITICAL | Digital Outputs | 605 | N/A
NON-CRITICAL | Not Used | 606
NON-CRITICAL | Not Used | 607
NON-CRITICAL | Analog Alarms | N/A | 608
NON-CRITICAL | Not Used | 609
NON-CRITICAL | Not Used | 610
NON-CRITICAL | Alarm Inputs | N/A | 611
NON-CRITICAL | Not Used | 612
NON-CRITICAL | Not Used | 613
Pressure
NON-CRITICAL | Setpoint Non-Critical | 614 | N/A
NON-CRITICAL | Not Used | 615
NON-CRITICAL | Not Used | 616
NON-CRITICAL | Digital Inputs/Pushbuttons | 617 | N/A
NON-CRITICAL | Not Used | 618
NON-CRITICAL | Not Used | 619
NON-CRITICAL | Digital Outputs | 620 | N/A
NON-CRITICAL | Not Used | 621
NON-CRITICAL | Not Used | 622
NON-CRITICAL | Analog Alarms | N/A | 623
NON-CRITICAL | Not Used | 624
NON-CRITICAL | Not Used | 625
NON-CRITICAL | Alarm Inputs | N/A | 626
NON-CRITICAL | Not Used | 627
NON-CRITICAL | Not Used | 628
Pump
NON-CRITICAL | Setpoint Non-Critical | 629 | N/A
NON-CRITICAL | Not Used | 630
NON-CRITICAL | Not Used | 631
NON-CRITICAL | Digital Inputs/Pushbuttons | 632 | N/A
NON-CRITICAL | Not Used | 633
NON-CRITICAL | Not Used | 634
NON-CRITICAL | Digital Outputs | 635 | N/A
NON-CRITICAL | Not Used | 636
NON-CRITICAL | Not Used | 637
NON-CRITICAL | Analog Alarms | N/A | 638
NON-CRITICAL | Not Used | 639
NON-CRITICAL | Not Used | 640
NON-CRITICAL | Alarm Inputs | N/A | 641
NON-CRITICAL | Not Used | 642
NON-CRITICAL | Not Used | 643
HLP
NON-CRITICAL | Setpoint Non-Critical | 644 | N/A
NON-CRITICAL | Not Used | 645
NON-CRITICAL | Not Used | 646
NON-CRITICAL | Digital Inputs/Pushbuttons | 647 | N/A
NON-CRITICAL | Not Used | 648
NON-CRITICAL | Not Used | 649
NON-CRITICAL | Digital Outputs | 650 | N/A
NON-CRITICAL | Not Used | 651
NON-CRITICAL | Not Used | 652
NON-CRITICAL | Analog Alarms | N/A | 653
NON-CRITICAL | Not Used | 654
NON-CRITICAL | Not Used | 655
NON-CRITICAL | Alarm Inputs | N/A | 656
NON-CRITICAL | Not Used | 657
NON-CRITICAL | Not Used | 658
LLP
NON-CRITICAL | Setpoint Non-Critical | 659 | N/A
NON-CRITICAL | Not Used | 660
NON-CRITICAL | Not Used | 661
NON-CRITICAL | Digital Inputs/Pushbuttons | 662 | N/A
NON-CRITICAL | Not Used | 663
NON-CRITICAL | Not Used | 664
NON-CRITICAL | Digital Outputs | 665 | N/A
NON-CRITICAL | Not Used | 666
NON-CRITICAL | Not Used | 667
NON-CRITICAL | Analog Alarms | N/A | 668
NON-CRITICAL | Not Used | 669
NON-CRITICAL | Not Used | 670
NON-CRITICAL | Alarm Inputs | N/A | 671
NON-CRITICAL | Not Used | 672
NON-CRITICAL | Not Used | 673
Security
NON-CRITICAL | Setpoint Non-Critical | 674 | N/A
NON-CRITICAL | Not Used | 675
NON-CRITICAL | Not Used | 676
NON-CRITICAL | Digital Inputs/Pushbuttons | 677 | N/A
NON-CRITICAL | Not Used | 678
NON-CRITICAL | Not Used | 679
NON-CRITICAL | Digital Outputs | 680 | N/A
NON-CRITICAL | Not Used | 681
NON-CRITICAL | Not Used | 682
NON-CRITICAL | Analog Alarms | N/A | 683
NON-CRITICAL | Not Used | 684
NON-CRITICAL | Not Used | 685
NON-CRITICAL | Alarm Inputs | N/A | 686
NON-CRITICAL | Not Used | 687
NON-CRITICAL | Not Used | 688
Server / Workstation
NON-CRITICAL | Setpoint Non-Critical | 689 | N/A
NON-CRITICAL | Not Used | 690
NON-CRITICAL | Not Used | 691
NON-CRITICAL | Digital Inputs/Pushbuttons | 692 | N/A
NON-CRITICAL | Not Used | 693
NON-CRITICAL | Not Used | 694
NON-CRITICAL | Digital Outputs | 695 | N/A
NON-CRITICAL | Not Used | 696
NON-CRITICAL | Not Used | 697
NON-CRITICAL | Analog Alarms | N/A | 698
NON-CRITICAL | Not Used | 699
NON-CRITICAL | Not Used | 700
NON-CRITICAL | Alarm Inputs | N/A | 701
NON-CRITICAL | Not Used | 702
NON-CRITICAL | Not Used | 703
Setpoints Critical
NON-CRITICAL | Setpoint Critical | 704 | N/A
NON-CRITICAL | Not Used | 705
NON-CRITICAL | Not Used | 706
NON-CRITICAL | Not Used | 707
NON-CRITICAL | Not Used | 708
NON-CRITICAL | Not Used | 709
NON-CRITICAL | Not Used | 710
NON-CRITICAL | Not Used | 711
NON-CRITICAL | Not Used | 712
NON-CRITICAL | Not Used | 713
NON-CRITICAL | Not Used | 714
NON-CRITICAL | Not Used | 715
NON-CRITICAL | Not Used | 716
NON-CRITICAL | Not Used | 717
NON-CRITICAL | Not Used | 718
Dechlorination
NON-CRITICAL | Setpoint Non-Critical | 719 | N/A
NON-CRITICAL | Not Used | 720
NON-CRITICAL | Not Used | 721
NON-CRITICAL | Digital Inputs/Pushbuttons | 722 | N/A
NON-CRITICAL | Not Used | 723
NON-CRITICAL | Not Used | 724
NON-CRITICAL | Digital Outputs | 725 | N/A
NON-CRITICAL | Not Used | 726
NON-CRITICAL | Not Used | 727
NON-CRITICAL | Analog Alarms | N/A | 728
NON-CRITICAL | Not Used | 729
NON-CRITICAL | Not Used | 730
NON-CRITICAL | Alarm Inputs | N/A | 731
NON-CRITICAL | Not Used | 732
NON-CRITICAL | Not Used | 733
Temperature / Leakage
NON-CRITICAL | Setpoint Non-Critical | 734 | N/A
NON-CRITICAL | Not Used | 735
NON-CRITICAL | Not Used | 736
NON-CRITICAL | Digital Inputs/Pushbuttons | 737 | N/A
NON-CRITICAL | Not Used | 738
NON-CRITICAL | Not Used | 739
NON-CRITICAL | Digital Outputs | 740 | N/A
NON-CRITICAL | Not Used | 741
NON-CRITICAL | Not Used | 742
NON-CRITICAL | Analog Alarms | N/A | 743
NON-CRITICAL | Not Used | 744
NON-CRITICAL | Not Used | 745
NON-CRITICAL | Alarm Inputs | N/A | 746
NON-CRITICAL | Not Used | 747
NON-CRITICAL | Not Used | 748
Temperature
NON-CRITICAL | Setpoint Non-Critical | 749 | N/A
NON-CRITICAL | Not Used | 750
NON-CRITICAL | Not Used | 751
NON-CRITICAL | Digital Inputs/Pushbuttons | 752 | N/A
NON-CRITICAL | Not Used | 753
NON-CRITICAL | Not Used | 754
NON-CRITICAL | Digital Outputs | 755 | N/A
NON-CRITICAL | Not Used | 756
NON-CRITICAL | Not Used | 757
NON-CRITICAL | Analog Alarms | N/A | 758
NON-CRITICAL | Not Used | 759
NON-CRITICAL | Not Used | 760
NON-CRITICAL | Alarm Inputs | N/A | 761
NON-CRITICAL | Not Used | 762
NON-CRITICAL | Not Used | 763
Turbidity
NON-CRITICAL | Setpoint Non-Critical | 764 | N/A
NON-CRITICAL | Not Used | 765
NON-CRITICAL | Not Used | 766
NON-CRITICAL | Digital Inputs/Pushbuttons | 767 | N/A
NON-CRITICAL | Not Used | 768
NON-CRITICAL | Not Used | 769
NON-CRITICAL | Digital Outputs | 770 | N/A
NON-CRITICAL | Not Used | 771
NON-CRITICAL | Not Used | 772
NON-CRITICAL | Analog Alarms | N/A | 773
NON-CRITICAL | Not Used | 774
NON-CRITICAL | Not Used | 775
NON-CRITICAL | Alarm Inputs | N/A | 776
NON-CRITICAL | Not Used | 777
NON-CRITICAL | Not Used | 778
UV
NON-CRITICAL | Setpoint Non-Critical | 779 | N/A
NON-CRITICAL | Not Used | 780
NON-CRITICAL | Not Used | 781
NON-CRITICAL | Digital Inputs/Pushbuttons | 782 | N/A
NON-CRITICAL | Not Used | 783
NON-CRITICAL | Not Used | 784
NON-CRITICAL | Digital Outputs | 785 | N/A
NON-CRITICAL | Not Used | 786
NON-CRITICAL | Not Used | 787
NON-CRITICAL | Analog Alarms | N/A | 788
NON-CRITICAL | Not Used | 789
NON-CRITICAL | Not Used | 790
NON-CRITICAL | Alarm Inputs | N/A | 791
NON-CRITICAL | Not Used | 792
NON-CRITICAL | Not Used | 793
Valve
NON-CRITICAL | Setpoint Non-Critical | 794 | N/A
NON-CRITICAL | Not Used | 795
NON-CRITICAL | Not Used | 796
NON-CRITICAL | Digital Inputs/Pushbuttons | 797 | N/A
NON-CRITICAL | Not Used | 798
NON-CRITICAL | Not Used | 799
NON-CRITICAL | Digital Outputs | 800 | N/A
NON-CRITICAL | Not Used | 801
NON-CRITICAL | Not Used | 802
NON-CRITICAL | Analog Alarms | N/A | 803
NON-CRITICAL | Not Used | 804
NON-CRITICAL | Not Used | 805
NON-CRITICAL | Alarm Inputs | N/A | 806
NON-CRITICAL | Not Used | 807
NON-CRITICAL | Not Used | 808
Waste System
NON-CRITICAL | Setpoint Non-Critical | 809 | N/A
NON-CRITICAL | Not Used | 810
NON-CRITICAL | Not Used | 811
NON-CRITICAL | Digital Inputs/Pushbuttons | 812 | N/A
NON-CRITICAL | Not Used | 813
NON-CRITICAL | Not Used | 814
NON-CRITICAL | Digital Outputs | 815 | N/A
NON-CRITICAL | Not Used | 816
NON-CRITICAL | Not Used | 817
NON-CRITICAL | Analog Alarms | N/A | 818
NON-CRITICAL | Not Used | 819
NON-CRITICAL | Not Used | 820
NON-CRITICAL | Alarm Inputs | N/A | 821
NON-CRITICAL | Not Used | 822
NON-CRITICAL | Not Used | 823
Weight
NON-CRITICAL | Setpoint Non-Critical | 824 | N/A
NON-CRITICAL | Not Used | 825
NON-CRITICAL | Not Used | 826
NON-CRITICAL | Digital Inputs/Pushbuttons | 827 | N/A
NON-CRITICAL | Not Used | 828
NON-CRITICAL | Not Used | 829
NON-CRITICAL | Digital Outputs | 830 | N/A
NON-CRITICAL | Not Used | 831
NON-CRITICAL | Not Used | 832
NON-CRITICAL | Analog Alarms | N/A | 833
NON-CRITICAL | Not Used | 834
NON-CRITICAL | Not Used | 835
NON-CRITICAL | Alarm Inputs | N/A | 836
NON-CRITICAL | Not Used | 837
NON-CRITICAL | Not Used | 838
Ph
NON-CRITICAL | Setpoint Non-Critical | 839 | N/A
NON-CRITICAL | Not Used | 840
NON-CRITICAL | Not Used | 841
NON-CRITICAL | Digital Inputs/Pushbuttons | 842 | N/A
NON-CRITICAL | Not Used | 843
NON-CRITICAL | Not Used | 844
NON-CRITICAL | Digital Outputs | 845 | N/A
NON-CRITICAL | Not Used | 846
NON-CRITICAL | Not Used | 847
NON-CRITICAL | Analog Alarms | N/A | 848
NON-CRITICAL | Not Used | 849
NON-CRITICAL | Not Used | 850
NON-CRITICAL | Alarm Inputs | N/A | 851
NON-CRITICAL | Not Used | 852
NON-CRITICAL | Not Used | 853
Environment
NON-CRITICAL | Setpoint Non-Critical | 854 | N/A
NON-CRITICAL | Not Used | 855
NON-CRITICAL | Not Used | 856
NON-CRITICAL | Digital Inputs/Pushbuttons | 857 | N/A
NON-CRITICAL | Not Used | 858
NON-CRITICAL | Not Used | 859
NON-CRITICAL | Digital Outputs | 860 | N/A
NON-CRITICAL | Not Used | 861
NON-CRITICAL | Not Used | 862
NON-CRITICAL | Analog Alarms | N/A | 863
NON-CRITICAL | Not Used | 864
NON-CRITICAL | Not Used | 865
NON-CRITICAL | Alarm Inputs | N/A | 866
NON-CRITICAL | Not Used | 867
NON-CRITICAL | Not Used | 868
Weather
NON-CRITICAL | Setpoint Non-Critical | 869 | N/A
NON-CRITICAL | Not Used | 870
NON-CRITICAL | Not Used | 871
NON-CRITICAL | Digital Inputs/Pushbuttons | 872 | N/A
NON-CRITICAL | Not Used | 873
NON-CRITICAL | Not Used | 874
NON-CRITICAL | Digital Outputs | 875 | N/A
NON-CRITICAL | Not Used | 876
NON-CRITICAL | Not Used | 877
NON-CRITICAL | Analog Alarms | N/A | 878
NON-CRITICAL | Not Used | 879
NON-CRITICAL | Not Used | 880
NON-CRITICAL | Alarm Inputs | N/A | 881
NON-CRITICAL | Not Used | 882
NON-CRITICAL | Not Used | 883
Health And Safety
NON-CRITICAL | Setpoint Non-Critical | 884 | N/A
NON-CRITICAL | Not Used | 885
NON-CRITICAL | Not Used | 886
NON-CRITICAL | Digital Inputs/Pushbuttons | 887 | N/A
NON-CRITICAL | Not Used | 888
NON-CRITICAL | Not Used | 889
NON-CRITICAL | Digital Outputs | 890 | N/A
NON-CRITICAL | Not Used | 891
NON-CRITICAL | Not Used | 892
NON-CRITICAL | Analog Alarms | N/A | 893
NON-CRITICAL | Not Used | 894
NON-CRITICAL | Not Used | 895
NON-CRITICAL | Alarm Inputs | N/A | 896

## Fragment 6 - Alarm
TABLE 2A-5 FRAGMENT 6 ALARM ENABLE AND DISABLE
FRAGMENT 7 | FIRST CHARACTER | FRAGMENT 6 DESCRIPTION | CODE
DIGITAL OUTPUT | _ | Raw Alarm Enable | RE
DIGITAL OUTPUT | _ | Dialer Alarm Enable | DE
DIGITAL OUTPUT | _ | Alarm Disabled Reason | RN