Table of Contents

PART 1 - GENERAL	1

1.1	Definitions	1

1.2	Purpose	2

1.3	General	3

1.4	Scope of Work	3

1.5	Applicable Documents & Drawings	5

1.6	Submittals	6

1.7	Qualifications	7

1.8	Project Management Requirements	9

1.9	Planning Meetings and Schedule	10

PART 3 - EXECUTION	24

3.1	Cable Installation Specifications	24

3.2	Tagging Convention Standard	29

3.3	Testing and Inspection	33

3.4	Stage 1 Site Acceptance Test (SAT1) - Network Distribution Enclosure	38

3.5	Stage 2 Site Acceptance Test (SAT2)	38

3.6	Test Documentation	40

3.7	Firestop Systems	40

3.8	Grounding and Bonding	41

3.9	Conduit and Ventilated Cable Tray	41

3.10	Penetrations of Walls, Floors and Ceilings	41

3.11	Warranty and Services	42

3.12	Damages	44

DIVISION 17100

CONTRACT SPECIFICATIONS

# GENERAL

## Definitions

### The following definitions shall apply throughout this specification section:

#### “Contractor” refers to the successful Proponent in respect of whose Proposal and Award is made.

#### “Horizontal Subsystem” refers to the Horizontal Subsystem that provides connections from the horizontal cross connect to the Work Area Outlets (WAOs) in the work areas.  It consists of the horizontal transmission media (typically copper Ethernet), the associated connecting hardware terminating the media and IOs in the work area.

#### “Region” refers to The Region’s Municipality of Halton

#### “Region’s Representative” refers to the Region’s employee or Consultant who has been designated to perform supervisory functions with respect to the Agreement and enforcement of the Contract Specifications.

#### “Structured Cabling System (SCS)” refers to the campus telecommunications cabling infrastructure including all required equipment and cabling including hardware, termination blocks, cross connect wire or cordage, patch panels, patch cords, work area outlets, UTP and fibre optic cable installed and configured to provide computer data and voice connectivity from each data or voice device to the network server or voice network/switch designated as the service point of the local area network.

#### “Work Area Outlet” provides the cross-connect between the horizontal cabling system and the end field device.

#### “Network Core Enclosure”:  A 19” rack enclosure constructed to support the termination of cables (fibre-optic, CAT6 UTP and power) and the installation of Network Core Switches, SCADA Servers and UPSs.

#### “Network Distribution Enclosure”:  A 19” rack enclosure constructed to support the termination of cables (fibre-optic, CAT6 UTP, power) and the installation of Ethernet Switch(s).  Network Distribution Enclosures are installed in the process areas and provide connectivity of the end field devices (i.e. PLC, OIT, etc.) via Work Area Outlets to the Network Core Switch.

#### “PC Enclosure”: A computer workstation enclosure constructed to support a PC workstation, Monitor, keyboard and UPS.

#### “Work Area” refers to the connection between the work area outlet and the station equipment in the work area.  It consists of cords, adapters, and other transmission electronics.

#### “Fibre-Optic Backbone Cabling” refers to the backbone cabling providing interconnection between the Network Distribution Enclosures (NDE) and the Network Core Enclosures.  It consists of the backbone cables, mechanical terminations and patch cords or jumpers used for backbone-to-backbone cross-connection.

#### “Horizontal Cabling System” refers to the horizontal cabling (copper Ethernet cables) extending from the Work Area Outlet (WAO) to the Network Distribution Enclosure. The system consists of horizontal cabling, work area outlets, cable terminations and cross-connections.

#### “Device Level Ring” refers to the subset of horizontal cabling (copper Ethernet cables) which is specifically intended to support the DLR network between Control Panels.  All standard requirements for Horizontal Cabling Systems apply to the DLR network except that the cable and jack ports will be Orange in colour.

## Purpose

### This document provides the minimum performance criteria for the components and sub-systems comprising a complete cabling and enclosure system that shall accommodate the Region’s requirements.

#### Product specifications, quantities, general design considerations, and installation guidelines are provided herein, and shown on the drawings. If the bid documents are in conflict, the written specification shall take precedence.  The successful vendor shall meet or exceed all requirements for the cabling system described in this document.

#### The communications system requires a structured cabling system and associated enclosures and components. The complete cabling system shall be supported by a System Warranty.  The system warranty shall be facilitated and be established between the Customer and the cabling system manufacturer.

#### Furnish all labor, supervision, tooling, miscellaneous mounting hardware, enclosures and consumables for each cabling system installed. Maintain current status with the warranting manufacturer, including all training requirements, for the duration of the project.  Staff each installation crew with the appropriate number of trained personnel, in accordance with their warranty.  After installation, submit all documentation to support the warranty in accordance with the manufacturer’s warranty requirements, and to apply for said warranty on behalf of the customer within the requirements stipulated by the manufacturer’s warranty. The warranty will cover the components and labour associated with the repair/replacement of any failed link, within the warranty period that is valid for a warranty claim.

#### Installation shall be by a Certified Member of the cabling system manufacturer. Check that all products/components of the cable system are eligible as covered by the cabling system manufacturer warranty. Ensure that all terms and conditions of the cabling system manufacturer are satisfied and complete all submissions to cabling system manufacturer within the time requirements defined in the warranty terms and conditions.

## General

### This section applies to construction of control system communication networks.

### The fibre optic backbone will be comprised of redundant, full-duplex, 1000BASE-FX segments.

### Horizontal cable segments are defined as the unshielded twisted pair (UTP), category 6 (CAT6) cables that permanently interconnect the patch panel in the Network Distribution Enclosure with a work-area outlet.

### Category 6 (CAT6) cables used in Device Level Ring Topology will be orange to distinguish them from standard Network Cables.  These cables can be run in the same conduit as any other Network Cable and both cables for a ring node are permitted to be located in the same conduit.  All other SCADA Ethernet cable is to be blue.

### All network components of a single type shall be from the same manufacturer and the same manufacturer’s catalogue number.

### All network sub-system components shall be from the same manufacturer.

## Scope of Work

### Furnish and install complete with all accessories a Structured Cabling System (SCS) with enclosures and subsystem components to include cable, termination hardware, supporting hardware, and miscellany.  The SCS shall serve as a vehicle for transport of data, video and voice telephony signals throughout the network from designated demarcation points to outlets located at various desks, workstation and other locations as indicated on the contract drawings and described herein.

### Wiring utilized for data and voice communications shall originate at Region provided hubs and concentrators either wall mounted, in vertical free standing and/or enclosed wall mounted vertical equipment located at the Network Core Enclosure and/or the Network Distribution Enclosures location(s). Wiring, terminations and patch bays between these designated demarcation points and outlet locations designated on the plans shall be considered part of the contract.  Work area Outlets (WAO) shall be furnished, wired and installed by the SCS system contractor.

### The system shall utilize a network of fibre optic, and unshielded twisted pair, and station cables.

### Fibre cables shall terminate on fibre patch panels and/or modular patch panels located in all demarcation and termination points shown on the drawings.

### All cables and terminations shall be identified at all locations.

### All cables shall terminate in an alphanumeric sequence at all termination locations.

### All copper cable terminations shall comply with, and be tested to ANSI/TIA/EIA 568-A standards for Category 6 installations.

### Horizontal cables shall terminate on one, two or three gang wall plates equipped as shown on the drawings.

### Testing and certification of the completed data and voice cable systems. It should be noted that the final termination on the master card of any DLR configuration cannot be completed until the card is configured correctly.

### Provide enclosures and equipment racks that will contain all rack-mountable components listed in this specification, the drawings, and specifications sheets. Telecom enclosure layout diagrams shall be provided to the Region’s Representative for pre-approval.

### Provide network wiring table spreadsheets in Excel format listing all structured cabling components and cabling source and destination connections for each fibre optic cable transmit and receive pair for backbone and horizontal cabling and each CAT6 horizontal cable and also include each fibre optic patch cord, each CAT6 patch cord, each work area outlet, each patch panel port and each network equipment switch port. These plant communications wiring tables shall be provided to the Region’s Representative for pre-approval.

### Use required cable labeling and management software.

### Work with Specification 13910 PLC Control Panel suppliers to co-ordinate installation and terminations of the cables to work area outlets. To be completed after the ICP is shipped to, installed and conduits to control panel are confirmed onsite.

### Work with general contractor to co-ordinate electrical power and conduit requirements. All electrical and conduit requirements for the structured cabling system described in this document are part of the scope of the structured cabling system. Co-ordinate with electrical specification for power and conduit installation details.

## Applicable Documents & Drawings

### The NDEs, Network Core and cabling are to be design and installed using the details outlined in the Contract Drawings.

### The cabling system described in this specification is derived in part from the recommendations made in industry standard documents.  The list of documents below is incorporated by reference:

#### This Technical Specification and Associated Drawings

#### TIA/EIA-568-B Commercial Building Telecommunications Cabling Standard – 2008. All standards referenced within the TIA/EIA-568-B, where applicable, constitute standard provisions of this specification. Furthermore, compliance with the Ontario Electrical Safety Code will supersede all other specifications.

#### TIA/EIA-569-B Commercial Building Standard for Telecommunications Pathways and Spaces – October, 2004

#### TIA/EIA-606-A Administration Standard for the Telecommunications Infrastructure of Commercial Buildings - May, 2002

#### TIA/EIA-607 Commercial Building Grounding and Bonding Requirements for Telecommunications - August, 1994

#### Building Industries Consulting Services, International (BICSI) Telecommunications Distribution Methods Manual (TDMM) – 11th edition

#### Ontario Electrical Safety Code, Section 56 – Optic Fibre Cables, Section 60 – Communication

#### EIA/TIA 455-61 Measurement of Fibre or Cable Attenuation Using an OTDR

#### EIA/TIA 455-53A Standard Test Procedures for Fibre optic Fibres, Cables and Transducers, Sensors, Connecting and Terminating Devices, and other Fibre optic Components

### If a conflict exists between applicable documents, then the order in the list above shall dictate the order of precedence in resolving conflicts.  This order of precedence shall be maintained unless a lesser order document has been adopted as code and is therefore enforceable as law by a local, provincial, or federal inspection agency.

### If this document and any of the documents listed above are in conflict, then the more stringent requirement shall apply.  All documents listed above are believed to be the most current releases of the documents; adhere to the most recent release when developing the proposal for installation.

## Submittals

### It is critical for on-going management of the data systems that the Region have up-to-date and accurate records of the actual work done.

#### Provide network wiring table spreadsheets in Excel format listing all structured cabling components and cabling source and destination connections for each fibre optic cable transmit and receive pair for backbone and horizontal cabling and each CAT6 horizontal cable and also include each fibre optic patch cord, each CAT6 patch cord, each work area outlet, each patch panel port and each network equipment switch port. These plant communications wiring tables shall be provided to the Region’s Representative for pre-approval.

### Data and voice work area outlets shall be marked on drawings with location of each work area outlet.

### Upon completion of the Project, the contractor shall provide “as-built” drawings of actual Work Area Outlet locations, cable run pathways, identification labels, and test results.

### The documentation including testing results shall be submitted in both a printed format and an electronic version.

### Shop Drawings

#### Determine the exact detailed routing paths for cabling within the plant. Submit these detailed routing drawings for review and approval to the Engineer.

#### Submit shop drawings to engineer for review and approval containing quantities and product data sheets before ordering.

#### Obtain list of Rack components from engineer, and submit Network Core Enclosure rack layout and plant area Network Distribution Enclosure layouts to the engineer for review and approval before ordering.

#### Submit Typical Outlet Wiring Drawing for review and approval to the Engineer.

#### Vendor shall submit, to the engineer, all factory test information prior to installation.

#### Provide manufacturer data sheets on all devices, modules, and subsystems of the proposed network communications systems.  If data sheets show more than one product, the proposed product shall be clearly indicated by arrows or other suitable means.  Data sheets shall be original manufacturer’s literature.  Reproductions are not acceptable.

#### Provide power connection diagram showing the interconnection from power sources through uninterruptible power supplies and power distribution panels, to computers/servers, peripherals and network equipment (routers and switches).

#### Provide grounding diagram showing grounding details for all enclosures and active network equipment.

#### Provide cable route schedule identifying all x-raying and coring required, the conduit path and cable run length.

### Test Documentation

#### Submit test documentation in accordance with sections Stage 1 Site Acceptance Test (SAT1) and Stage 2 Site Acceptance Test (SAT2) within this specification.

#### Submit the Network – Cable Test Results Manual and Operations and Maintenance Manual ten (10) working days prior to the site acceptance test.

#### Test results should be submitted in both an electronic and hard copy format.

### As-Built

#### Provide shop drawings to the Consultant at the conclusion of the project.  The marked up drawing set will accurately depict the as-built status of the system including termination locations, cable routing, and all administration labeling for the cable system.

#### A narrative will be provided that describes any areas of difficulty encountered during the installation that could potentially cause problems to the telecommunications system.

## Qualifications

Contractor must be a SYSTIMAX Solution Select Installation Partner as indicated on the CommScope web page at http://commscope.com/locator/wizard.aspx?p=sys.

In order to find listed partners use the following selections:

Select through the radio buttons the following:

Wired and Wireless Systems for the Enterprise Network (Building, Data Centre, Campus)

Using the drop down menus choose the following;

Wired Systems

Passive

SYSTIMAX

Display SYSTIMAX Premier/Select Installation Partners

Country: Canada

Province: Ontario

Companies that are not listed on the CommScope website will not be permitted to work on the Project. Letters of qualification from CommScope will not be accepted.

### Contractor must be a member of the BICSI Telecommunications Association.

### The contractor shall utilize the authorized manufacturer components and distribution channels in provisioning this Project.

### Contractor shall have a minimum of five (5) years of recent experience on structured cabling systems of similar type and size.

### Contractor and design firm shall be in compliance with all federal, provincial and local statutes regarding qualifications of firms.

### The contractor shall be experienced in all aspects of this work and shall be required to demonstrate direct experience on recent systems of similar type and size.

### The contractor shall own and maintain tools and equipment necessary for successful installation and testing of optical and Category 6 and fibre optic premise distribution systems.

### The contractor shall have personnel who are adequately trained in the usage of such tools and equipment.

### Contractor shall submit a resume of qualification with the Contractor’s proposal indicating the following:

#### A list of recently completed projects of similar type and size with contact names and telephone numbers for each.

#### A list of test equipment proposed for use in verifying the installed integrity of metallic and fibre optic cable systems on this project.

#### A technical resume of experience for the contractor’s Project Manager and on-site installation supervisor who will be assigned to this project.

#### A list of technical product training attended by the contractor’s personnel that will install the SCS system.

### Any sub-Contractor, who will assist the SCS contractor in performance of this work, shall have the same training and certification as the SCS contractor.

### Below is a list of some of the potential SYSTIMAX Solutions Select Installation Partners. Other contractors can be used provided they meet all the qualifications listed out in this section and they are listed on the CommScope webpage as a SYSTIMAX Solution Select Installation Partner.

ACP Communication Technologies

885 Main St East.

Milton, ON, L97 5A7

Primary Contact: Carl Starkes

Email: cstarkes@networkacp.com

Phone 1-800-501-7776

Connex Telecommunications Inc

44 Beaver Creek Road, Unit 16,

Richmond Hill, On. L4B 1G8Primary Contact: Edgar Balian

Email: ebalian@connexservice.ca

Phone: 905-944-6500

Guild Electric Ltd

470 Midwest Road

Scarborough, ON. M1P 4Y5

Primary Contact:  Rob Stevenson

Email:  rob.stevenson@guildelectric.com

Phone: (416) 288-8222

Idea Networks Inc

1515 Matheson Blvd. East, Unit B10

Mississauga, ON. L4W 2P5

Primary Contact:  Hayden Barker

Email: hbarker@ideanetworks.com

Phone: 905-970-3900

## Project Management Requirements

### The contractor shall provide a Project Manager who shall act as a single point of contact for all activities regarding this project. The Project Manager shall have the authority to make on-site decisions regarding the scope of the work and ad hoc, minor changes that may be required.

### The Region, in turn, shall appoint a Region’s Representative who will have the corresponding role on behalf of the Region.

## Planning Meetings and Schedule

### An initial planning meeting will be held with the successful bidder to:

### Clarify all requirements (systems, services, distribution methods, etc.),

### Identify responsibilities,

### Schedule the events that will transpire during the implementation of the project.

- PRODUCTS

  - ENCLOSURE WIRING

    - The following general requirements shall be followed:

      - All enclosure wiring shall run through a cable manager.

      - Cable managers shall not be filled to more than 50% of their volume upon initial installation.

      - All wires and cables, including spares, shall be identified at each end and at any connection.

      - Wire markers are required on each conductor in panel board gutters, and at load connections. The identification shall include branch circuit or feeder number for power and lighting circuits, and control wire numbers for control wiring.

      - All field wires and cables terminated within enclosures shall be identified at each termination with a marking that corresponds with the supporting documentation.

      - Power wiring insulation shall be rated at 600 volts at 90 C and be type RW 90 THHN. Conductors shall be stranded copper. No wire smaller than 14 AWG shall be used for power wiring, unless noted otherwise on the drawings.

  - Core and Server ENCLOSURES

    - Fiber Optic Cabling Patch Panel and Terminations

      - The fiber optic enclosure shall meet or exceed the following minimum requirements:

        - The enclosures shall protect the fiber optic connections for patching or splicing requirements within the premises cabling environment.

        - Enclosures shall accommodate up to 24 fibers per rack space.

        - The enclosure shall include bend radius management for fiber patch cords and backbone cable.

        - The enclosure shall support modular adaptor modules for multi-mode or single-mode fiber optic cables.

        - Fiber slack trays shall attach to the rear of the modules providing slack storage and proper bend radius of fibers.  The fiber slack trays and modules shall be front removable.

      - The following components are common for the Core and Server Enclosure regardless of the fibre type:

| Core and Server Enclosure Common Components |  |  |
| --- | --- | --- |
| Description | Module | Notes |
| Fiber Splice Panel/Shelf | 760231522 | HD-4U-SP Sliding Fiber Splice Panel/Shelf |
| Fiber Splice Panel/Shelf | 760231506 | ISP FIBRE PATCH PANEL HD-1U-SP |
| Fiber Splice Panel/Shelf | 760231514 | HD-2U-SP FIBRE PATCH PANEL, 2U |
| Fiber Cassette | 760245495 | G2-SP-12LC Splice Cassette w/ integrated splice tray, 12-strand, no pigtails |
| Blanking Module | 760109462 | 360G2 Mod Panel Blank Adapter, 4-pack |

      - The following components are used for Core and Server Enclosures with Multimode Fibre

- Multi-Mode Fiber Components

| Multi-Mode Fiber Module Components |  |  |
| --- | --- | --- |
| Description | Module | Notes |
| Fiber Pigtail Kit, multimode OM4 | FAXLCUC0A-XXF005 | Fiber Optic Pigtail Kit, 6-strand OM4 multimode, LC-to-unconnectorized, 1-6 (blue-white), 5ft |
| 4ft Patch Cable | FEXLCLC42-MXF004 | Fiber patch cord, duplex, LC-LC OM4 multimode, 4 ft. for enclosure end |
| 7ft Patch Cable | FEXLCLC42-MXF007 | Fiber patch cord, duplex, LC-LC OM4 multimode, 7 ft. for Core |
| 14ft Patch Cable | FEXLCLC42-MXF014 | Fiber patch cord, duplex, LC-LC OM4 multimode, 14 ft. for Core |

      - The following components are used for Core and Server Enclosures with Singlemode Fibre

| Single Mode Fiber Components – Core and Server Enclosure |  |  |
| --- | --- | --- |
| Description | Module | Notes |
| Fiber Pigtail Kit, singlemode | FAWLCUC0A-XXF005 | Fiber Optic Pigtail Kit, 6-strand singlemode, LC-to-unconnectorized, 1-6 (blue-white), 5ft |
| 4ft Patch Cable | FEWLCLC42-JXF004 | Fiber patch cord, duplex, LC-LC single-mode, 4 ft. for enclosure end |
| 7ft Patch Cable | FEWLCLC42-JXF007 | Fiber patch cord, duplex, LC-LC single-mode, 7 ft. for Core |
| 14ft Patch Cable | FEWLCLC42-JXF014 | Fiber patch cord, duplex, LC-LC single-mode, 14 ft. for Core |

    - Terminate all six (6) fibers of each backbone cable within the fiber optic enclosures.

    - Fiber colour and Tx/Rx orientation is to be identical for each termination panel.

    - All fibers are to be labeled as per the Network Core Enclosure – Port Assignments.

    - Dark fibers are to be covered to prevent damage.

    - CAT 6 Patch Panel & Terminations

      - Provide 24-port, patch panels as per the drawings with connectors and appurtenances for termination of unshielded twisted pair (UTP) cable.

      - All 24-port modular patch panels shall be CommScope material ID. 760152561 (360-IPR-1100-E-GS3-1U-24).

      - All Category 6 (CAT6) connectors shall be unshielded modular jacks and wired for a T586A wire-map.

      - The Category 6 modular jack panels shall meet or exceed Category 6 requirements in ISO/IEC 11801, CENLEC EN 50173 and ANSI/TIA/EIA-568A and shall be UL Listed

  - Network Distribution Enclosures

    - Provide Network Distribution Enclosures in all locations identified in the drawings and associated drawings. Construct Network Distribution Enclosures to support the termination of cables (multi-mode and single-mode fiber optic, CAT6 UTP, power) and the installation of Ethernet Switches (free issued).

    - Provide Network Distribution Enclosures per the Network Distribution Enclosure Interior Layout Drawing and associated schedules.

    - Network Distribution Enclosure enclosures shall meet or exceed the following minimum requirements:

      - Outside dimensions of 922 mm (36”) H x 600 mm (24”) W x 610 mm (24”) D.

      - 14 gauge steel, smooth continuously welded seams.

      - Oil resistant gasket.

      - Padlock capable ¼ turn latch

      - NEMA 4 rating.

    - Refer to drawings for make and model of Network Distribution Enclosures.

    - The front and rear doors shall be lockable when used with an optional key lock kit.  The connector housings shall have a labeling scheme that complies with ANSI/TIA/EIA-606.  The housings shall be available with factory-installed connector cable stubs in multiple cable and connector types.

    - Provide a 19U, 19” rack for the mounting of 19” rack mountable components. The front of the 19” rack is to be recessed 100 mm (4”) from the front of the enclosure.

    - Bond 19” rack and Enclosure to building ground. All racks in the enclosures shall be properly grounded.  All grounding and bonding shall meet the National Electrical Code (NEC) as well as local codes, which specify additional grounding and/or bonding requirements

    - The Network Distribution Enclosure is to be mounted on stainless steel separators or galvanized struts to ensure a minimum 20 mm separation from the wall. The Network Distribution Enclosure shall be leveled against the wall using the separators.

    - All enclosure doors shall open through 180 degrees without restriction.

    - Mid-section of the enclosure shall open through 90 degrees without restriction from wall-mount section.

    - The Network Distribution Enclosures are to be installed between a maximum height of 762 mm (30”) from the ground and a minimum height of 610 mm (24”) from the ground.

    - Provide the enclosure electrical distribution as per the Network Distribution Enclosure Power Distribution Drawing.

      - The UPS Supply is to power all network components. Contractor will provide the 120VAC Network Supply from the nearest Instrument Control Panel. . The Contractor shall provide galvanized rigid-steel conduit and wiring to provide the UPS Supply from the nearest Instrument Control Panel as indicated on the drawings.

      - Provide 120 VAC, 3-wire, duplex receptacles, circuit breakers, surge suppressor, wire duct and grounding bar per the Network Distribution Enclosure Layout Drawing and associated Component Schedule. Electrical distribution components are to be mounted on a rear accessory panel.

    - Provide a rack mount, fiber optic enclosure for termination of the multi-mode and single-mode fiber optic cable within the Network Distribution Enclosure.

    - The fiber optic enclosure shall meet or exceed the following minimum requirements:

      - The enclosures shall protect the fiber optic connections for patching or splicing requirements within the premises cabling environment.

      - Enclosures shall accommodate up to 12 fibers per rack space.

      - The enclosure shall include bend radius management for fiber patch cords and backbone cable.

      - The enclosure shall support modular adaptor modules for multi-mode fiber optic cables.

      - Fiber slack trays shall attach to the rear of the modules providing slack storage and proper bend radius of fibers.  The fiber slack trays and modules shall be front removable.

      - The following components are common for the Network Distribution  Enclosure regardless of the fibre type:

| Network Distribution Enclosure Common Components |  |  |
| --- | --- | --- |
| Description | Module | Notes |
| Modular Cassette Shelf | 760231506 | HD-1U-SP, Sliding Modular Cassette Shelf |
| Fiber Cassette | 760245495 | G2-SP-12LC Splice Cassette w/ integrated splice tray, 12-strand, no pigtails |
| Blanking Module | 760109462 | 360G2 Mod Panel Blank, 4-pack |

      - The following components are common for the Network Distribution  Enclosure with multi-mode fibe

| Network Distribution Enclosure - Multi-Mode Fiber Components – |  |  |
| --- | --- | --- |
| Description | Module | Notes |
| Fiber Pigtail Kit, multimode OM4 | FAXLCUC0A-XXF005 | Fiber Optic Pigtail Kit, 6-strand OM4 multimode, LC-to-unconnectorized, 1-6 (blue-white), 5ft |
| 3ft Patch Cable | FEXLCLC42-MXF003 | Fiber patch cord, duplex, LC-LC multi-mode, 3 ft. for enclosure end |

      - The following components are common for the Network Distribution  Enclosure with single-mode fiber

| Network Distribution Enclosure - Single-Mode Fiber Components |  |  |
| --- | --- | --- |
| Description | Module | Notes |
| Fiber Pigtail Kit, singlemode | FAWLCUC0A-XXF005 | Fiber Optic Pigtail Kit, 6-strand singlemode, LC-to-unconnectorized, 1-6 (blue-white), 5ft |
| 3ft Patch Cable | FEWLCLC42-JXF003 | Fiber patch cord, duplex, LC-LC smode, 3 ft for enclosure end |

    - Terminate all six (6) fibers of each backbone cable within the fiber optic enclosures.

    - Fiber colour and Tx/Rx orientation is to be identical for each termination panel.

    - All fibers are to be labeled as per the Network Core Enclosure – Port Assignments.

    - Dark fibers are to be covered to prevent damage.

    - CAT 6 Patch Panel & Terminations

      - Provide one (1) 24-port, patch panels with connectors and appurtenances for termination of unshielded twisted pair (UTP) cable.

      - All 24-port modular patch panels shall be CommScope material ID. 760152561(360-IPR-1100-E-GS3-1U-24).

      - All Category 6 (CAT6) connectors shall be unshielded modular jacks and wired for a T586A wire-map.

      - The Category 6 modular jack panels shall meet or exceed Category 6 requirements in ISO/IEC 11801, CENLEC EN 50173 and ANSI/TIA/EIA-568A and shall be UL Listed

  - Patch cables

    - Fiber optic Patch Cables

      - Fiber optic patch cords are to be factory assembled and tested by the manufacturer. Provide written certification from the manufacturer.

      - See drawing for quantity of each type of patch cable to be provided.

    - Copper CAT 6 Patch Cables

      - Provide MiN06 reduced diameter Category 6 (CAT6) yellow, unshielded twisted pair (UTP), patch cords for each 24 port modular patch panel for each Network Distribution Enclosure.  Part number CO166S2-09Fxxx (xxx = length in feet)

      - Install only those patch cables required to interconnect the Ethernet Access Switch and Patch Panels as noted in the Network Distribution Enclosure CAT6– Port Assignments.

      - CAT6 UTP patch cords are to be factory assembled and tested by the manufacturer.

      - See drawing for quantity of each type of patch cable to be provided. Patch cables to be provided by the contractor for all free issued equipment.

    - Copper CAT 6 Patch Cables for Device Level Rings (DLR)

      - Provide twenty-four (24) Category 6 (CAT6) orange, unshielded twisted pair (UTP), patch cords for each 24 port modular patch panel for each Network Distribution Enclosure. Part number CO166S2-06Fxxx (xxx = length in feet).

      - Install only those patch cables required to interconnect the Ethernet Access Switch and Patch Panels as noted in the Network Distribution Enclosure CAT6– Port Assignments.

      - CAT6 UTP patch cords are to be factory assembled and tested by the manufacturer.

  - HORIZONTAL Cabling System

    - Horizontal Cable

      - Provide twisted-pair cable, connectors and appurtenances that make up the Horizontal cables segments.

      - Horizontal cable segments shall meet the requirements of the TIA/EIA-568-A specification for Category 6 (CAT6), Unshielded Twisted Pair (UTP) cable.

      - Horizontal Cable Segments shall meet or exceed the following minimum requirements:

        - The cable shall be tested up to 200 MHz with a guaranteed performance that meets or exceeds the ANSI/TIA/EIA-568B/ISO/IEC 11801 horizontal cable requirements for PS-NEXT, attenuation, structural return loss, and attenuation-to-crosstalk ratio (ACR).

        - The cable shall be constructed from 0.574mm (23AWG), bare copper wire insulated. Two insulated conductors twisted together to form a pair and four pairs laid up to form the basic unit.

        - The cable shall be jacketed in flame-retardant PVC. Cable run in conduit shall meet or exceed FT4 rating. Cable not run in conduit shall meet or exceed FT6 rating.

      - Horizontal cable run in conduit shall be CommScope material ID. 760004689 (regular network) or 700212103 when used as part of a Device Level Ring network topology.

      - Horizontal cable not run in conduit shall be FT6 rated CommScope material ID. 700208093 (regular network) or 700210008 when used as part of a Device Level Ring network topology.

- Table 2 - Enhanced Category 6 Cable Performance

| Frequency, MHz | Attenuation, dB/100m Max. | NEXT, dB Min./Typical | PSNEXT, dB Min./Typical | ELFEXT, dB Min./Typical | PSELFEXT, dB Min./Typical | Return Loss, dB Min. | ACR, dB Typical, 90m | PS ACR, dB Typical, 90m |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| .772 | 1.8 | 72/81 | 69/77 | 66/73 | 63/70 | 19.4 | 77.4 | 73.4 |
| 1 | 2.0 | 70/79 | 67/75 | 64/71 | 61/68 | 20.0 | 75.2 | 71.2 |
| 4 | 4.1 | 61/70 | 58/66 | 52/59 | 49/56 | 23.1 | 64.3 | 60.3 |
| 8 | 5.8 | 57/66 | 54/62 | 46/53 | 43/50 | 24.5 | 58.8 | 54.8 |
| 10 | 6.5 | 55/64 | 52/60 | 44/51 | 41/48 | 25.0 | 56.2 | 52.2 |
| 16 | 8.2 | 52/61 | 49/57 | 40/47 | 37/44 | 25.0 | 51.6 | 47.6 |
| 20 | 9.3 | 51/60 | 48/56 | 38/45 | 35/42 | 25.0 | 49.6 | 45.6 |
| 25 | 10.4 | 49/58 | 46/54 | 36/43 | 33/40 | 24.3 | 46.6 | 42.6 |
| 31.25 | 11.7 | 48/57 | 45/53 | 34/41 | 31/38 | 23.6 | 44.5 | 40.5 |
| 62.5 | 17.0 | 43/52 | 40/48 | 28/35 | 25/32 | 21.5 | 34.7 | 30.7 |
| 100 | 22.0 | 40/49 | 37/45 | 24/31 | 21/28 | 20.1 | 27.2 | 23.2 |
| 155 | 28.1 | 37/46 | 34/42 | 20/27 | 17/24 | 18.8 | 18.7 | 14.7 |
| 200 | 32.4 | 36/45 | 33/41 | 18/25 | 15/22 | 18.0 | 13.8 | 9.8 |
| 300 | 41.0 | 33/42 | 30/38 | 14/21 | 11/18 | 16.8 | 3.1 | – |
| 350 | 44.9 | 32/41 | 29/37 | 13/20 | 10/17 | 16.3 | – | – |

      - The contractor shall provide any screws, anchors, clamps, tie wraps, hooks, and any other miscellaneous supplies necessary for the proper installation and support of the cable systems.

      - All communications cabling used throughout this project shall comply with the requirements as outlined in the National Electric Code (NEC) Articles 725, 760, 770, and 800 and the appropriate local codes.

      - All copper cabling shall bear CMP (Plenum Rated), CM/CMR (Riser Rated) and/or appropriate markings for the environment in which they are installed.

      - Required hardware includes, but is not limited to, termination blocks, fastening devices, work area outlets, voice outlets, connectors and all required accessories to comply with this specification.

    - Work Area Outlet Components

      - All outlets shall terminate on:

        - Data Outlet: CommScope Yellow work area outlets

        - Device Level Ring Outlet: CommScope Orange work area outlets

        - Voice Outlet: CommScope white work area outlets

        - The outlets shall be installed in CommScope white flush mount faceplates for office environments and CommScope metal faceplates for non-office settings.

        - All components shall be CommScope manufactured.

      - Work Area Outlets shall be CommScope material ID 700206691 (MGS400-123 - yellow) or 700206683 (MGS400-112 - orange) for a Device Level Ring Work Area Outlet.

      - Unless otherwise noted on the floor plans or within this document, all voice and work area outlets for 23 AWG copper cables shall be:

        - 8-position/ 8-conductor modular outlets

        - Insulation displacement

        - Support Universal applications in a multi-vendor environment, accepting modular RJ-45 plugs.

        - Provided with blank module inserts for all unused module locations.

        - Mounted in one, two or four gang NEMA utility outlet boxes.

        - Equipped with EIA/TIA-T568A and EIA/TIA-T568B universal wiring labels.

    - Surface Mount Boxes

      - All surface mount boxes shall:

        - Support a wide range of applications and configurations using snap-in components.

        - Have cable entrances available through the base and/or sides

        - Be mountable on any surface or single gang electrical boxes.

        - Be ivory in colour.

      - Surface mount box shall be CommScope 6-port, material ID 107431538 (M106SMB-262).

  - Fiber Optic Backbone cabling system

    - The backbone data cabling shall be CommScope SCS Cabling system.  All components shall be manufactured and approved by CommScope. No exceptions will be considered.

    - Each backbone cable runs radiating from the Network Core Enclosure to Plant area Network Distribution Enclosures.

    - Work with Division 13 Instrumentation and Control, Instrument Control Panel (ICP) suppliers to co-ordinate installation and terminations of the cable runs after installation of the ICP.  Division 13 is responsible for the supply and installation of the Work Area Outlets within the Instrument Control Panel. Division 17 is responsible for the installation, termination and certification of the structured cabling.

    - Fiber Optic Backbone Cabling System – Termination

      - The fiber optic cable shall be terminated at the Network Distribution Enclosures in rack mount enclosures providing protection to the terminated fibers. The LC connectors shall be a 50μm, multi-mode connectors, capable of terminating either 250 μm coated or 900 μm buffered fibers.  The connectors shall be field-installable, requiring no epoxy, or polishing. The connectors shall meet the intermateability requirements of TIA/EIA-604-12.

      - The fiber optic cable shall be terminated at the Network Distribution Enclosures in rack mount enclosures providing protection to the terminated fibers. When installing single-mode fiber, LC connectors are to be fusion spliced to the backbone fiber cable and spliced are to be properly managed within fiber enclosure using appropriate splice kits. LC single mode pigtail kits are to be dressed in the cartridges and installed in appropriate fiber panels.

  - Fiber Optic Backbone Cable

      - Provide fiber optic cable, connectors and appurtenances that make up the backbone cable segments.

      - The fiber optic backbone cable segments shall meet the requirements of the TIA/EIA-568-A specification for 50 micron multi-mode fiber and single-mode fiber.

      - All connectors for the termination of the fiber optic backbone cable shall be multi-mode LC connectors.

  - Single Mode Fiber Optic Cable

      - Single-mode fiber optic backbone cable shall meet or exceed the following minimum requirements:

        - Quantity 6 – single-mode fiber strands.

        - Indoor/Outdoor Rating.

        - Core-locked, Tight-buffered.

        - 8/125 micron Core/Cladding for single-mode fiber.

        - 950 MHz-km Bandwidth at 1310 nm wavelength for single-mode fiber.

        - 500 MHz-km Bandwidth at 1550 nm wavelength for single-mode fiber.

        - Riser-Rated (FT4) inner and outer PVC jackets.

      - The single-mode fiber optic cable shall be CommScope TeraSpeed, zero water peak single-mode fiber Plenum indoor/outdoor cable, P-006-OD6-8W-FSUBK, material ID. 760036384.

  - Multi-Mode Fiber Optic Cable

      - Multi-mode fiber optic backbone cable shall meet or exceed the following minimum requirements:

        - Quantity 6 – 50 micron multi-mode fiber strands.

        - Indoor/Outdoor Rating.

        - Core-locked, Tight-buffered.

        - 50/125 micron Core/Cladding for multi-mode fiber.

        - 950 MHz-km Bandwidth at 850 nm wavelength for multi-mode fiber.

        - 500 MHz-km Bandwidth at 1300 nm wavelength for multi-mode fiber.

        - Riser-Rated (FT4) inner and outer PVC jackets.

      - The multi-mode fiber optic cable shall be CommScope LazrSpeed 550 Plenum indoor/outdoor cable, P-006-OD-5K-FSUBK, material ID. 760036426.

  - General Enclosure Requirements

      - Unless otherwise specified in the Contract Documents indoor enclosures containing network components are to be NEMA 4.

      - All screws, bolts, fasteners etc. are to be corrosion resistant stainless steel.

      - All wall-mounted panels are to be separated from the wall by stainless steel spacers or galvanized steel struts.

      - Doors are to have continuous hinges with removable pin and oil resistance cellular neoprene gasket secured by gasket retainers.

      - Cable bundles are to be neatly laced, run in ducting or approved cable managers and secured to 19” rack or mounting back-panel.

      - All enclosure doors shall open through 180 degrees without restriction.

      - Enclosure layout and equipment spacing shall be constructed to allow for device removal, calibration and maintenance without disassembly of adjacent devices.

      - All enclosures shall have sufficient structural reinforcements to ensure a limited plane surface vibration and to provide rigidity during shipment, installation and operation without distortion or damage to the enclosure, mounting panel or mounted instruments.

      - All enclosure seams shall be continuously welded and ground smooth to be undetectable after painting.

      - Devices shall be installed on the enclosure back-panel or 19” rack.

      - There shall be no devices installed on the side plates of the enclosure.

    - Enclosure Wiring

      - All enclosure wiring shall run through a cable manager.

      - Cable managers shall not be filled to more than 50% of their volume upon initial installation.

      - All wires and cables, including spares, shall be identified at each end and at any connection. Use durable non-fading sleeve type wire markers to identify network cables as follows:

      - Labels for cabling shall be laser printed, self-laminating, adhesive, polyester (indoor/outdoor).

      - Hand-written labels will not be accepted.

      - Lettering shall be black on a white background. Characters shall be a minimum of 4 mm high.

      - Wire markers are required on each conductor in panel board gutters, and at load connections. The identification shall include branch circuit or feeder number for power and lighting circuits, and control wire numbers for control wiring.

      - All field wires and cables terminated within enclosures shall be identified at each termination with a marking that corresponds with the drawings and supporting documentation.

      - Power wiring insulation shall be rated at 600 volts at 90 degrees Celsius and shall be type RW 90 THHN. Conductors shall be stranded copper. No wire smaller than 12 AWG shall be used for power wiring, unless noted otherwise on the Contract Drawings.

  - PC Enclosures

    - The PC Enclosure shall have the following minimum requirements:

      - Keyboard compartment

      - Two Shelves

      - Upper front window door

      - Lower front solid door

      - Rear solid door

      - Dimensions of 1785mm H X 909mm W x 542 mm D (70.3”x31.8”x21.3”).

      - Lifting eyes

      - Modified by the manufacturer to meet NEMA 4 rating.

    - The PC Enclosure shall be Hoffman, part number PGLD1886CWS with modifications by the manufacturer to meet NEMA 4.

  - NORDX BIX wiring Block

      - The wiring block shall support Category 3, Category 5, Category 5E and Category 6 applications and facilitate cross connection and interconnection using either cross connect wire (voice only) or the appropriate category patch cords.

      - The wiring blocks shall be fire retardant, molded plastic consisting of horizontal index strips for terminating 25 pairs of conductors each.  The index strips shall be marked with five colors on the high teeth, separating the tip and ring of each pair, to establish pair location.

      - A series of fanning strips shall be located on each side of the block for dressing the cable pairs terminated on the adjacent index strips.

      - The wiring block shall accommodate 22- through 26-AWG conductors and shall be able to mount directly on wall surfaces without backboards or on a 19” rack.

      - Clear label holders with the appropriate colour inserts shall be provided with the wiring blocks. The insert labels shall contain vertical lines spaced on the basis of circuit size (5-pair) and shall not interfere with running, tracing or removing jumper wire/patch cords.

      - The wiring blocks shall be available in 25 & 50 pair sizes.

      - The wiring block shall be able to accommodate over 500 repeated insertions without incurring permanent deformation and it shall pass the reliability test of no more than one contact failure in 10000 connections.

# EXECUTION

## Cable Installation Specifications

### General Description

#### The structured cabling system shall consist of the Work Area, Horizontal, Backbone, Telecommunications Room or network core enclosure, and Network Distribution Enclosures.

#### All installation work shall comply with the latest version of the applicable Codes, Standards, and Regulations of authorities having jurisdiction. In particular, EIA/TIA 568-A standards and CommScope Technologies’ Design and Installation guidelines shall be followed.

#### The Contractor shall ensure that the maximum pulling tensions of the specified distribution cables are not exceeded and cable bends maintain the proper radius during the placement of the facilities.  Failure to follow the appropriate guidelines will require the Contractor to provide in a timely fashion the additional material and labor necessary to properly rectify the situation.  This shall also apply to any and all damages sustained to the cables by the Contractor during the implementation.

#### The contractor shall provide any special equipment or tools necessary to properly perform the cable installation.

#### Install network enclosures in locations identified in the Contract Drawings. Field verify and obtain written approval from the Consultant of final locations of the enclosures prior to commencing this Work. Costs required to relocate enclosures in unapproved locations will be the responsibility of the Contractor.

#### Provide a complete and operational system, all components and appurtenances necessary to ensure that the network enclosures are functional and meet the intent of this Specification.

#### Locate Work-Area Outlets such that the length of the horizontal cable runs from the Network Distribution Enclosure interconnect to the Work-Area Outlet shall be less than 85 meters. For Work-Area Outlets where this proves impossible the Consultant may authorize in writing an exception if the link still meets the performance requirements of this Specification.

#### The Consultant reserves the right to relocate Network Distribution Enclosures and Work-Area Outlets within 5 m of the locations identified in the Contract Drawings at no additional cost to the Region.

#### It is the Contractor's responsibility to size power supply cables to meet the requirements of the Ontario Electrical Safety Code based on field verified length of cable run and power supply load.

#### It is the Contractor’s responsibility for all x-raying and coring where conduit passes through floors, walls and ceilings.

#### All cable ties are to be Velcro. No nylon cable ties will be allowed.

### Horizontal Cable Runs

#### Cable Pathway

##### The contractor shall provide and install “J”-hooks where conduit is not supplied where exposed above ceilings in plenum spaces.

##### In suspended ceiling and raised floor areas where duct, cable trays or conduit are not available, the Contractor shall bundle, in bundles of 50 or less, station wiring with Velcro cable ties snug, but not deforming the cable geometry.

##### Cable bundles shall be supported via “J” hooks attached to the existing building structure and framework at a maximum of five (5) foot intervals.

##### The contractor shall adhere to the manufacturers’ requirements for bending radius and pulling tension of all data and voice cables.

##### Cables shall not be attached to lift out ceiling grid supports or laid directly on the ceiling grid.

##### Cables shall not be attached to or supported by fire sprinkler heads or delivery systems or any environmental sensor located in the ceiling air space.

##### Cable shall be installed in 25.4 mm (1”) galvanized rigid-steel conduit unless the environment is corrosive.

##### Conduit running through corrosive environments shall be rigid PVC.

##### Install and leave a continuous length of pull string in all conduit runs

#### Horizontal Cabling

##### Contractor shall supply horizontal cables to connect each work area outlet to the backbone subsystem.

##### The cables shall be run using a star topology format from the Network Distribution Enclosure or the Network Core Enclosure to every individual work area outlet.

##### Contractor shall observe the bending radius and pulling strength requirements of the Cat 6 UTP cable during handling and installation.

##### Each run of cable between the termination block and the work area outlets shall be continuous without any joints or splices.

##### If the interior of walls is not obstructed, the Contractor shall conceal horizontal distribution wiring internally within the walls.  If such obstructions exist, the Contractor shall secure approval in writing from the Region’s Representative prior to the use of an alternate method.

##### Conduit runs installed by the contractor should not exceed 100 feet or contain more than two 90 degree bends without utilizing appropriately sized pull boxes.

##### Care shall be taken to ensure that during the installation nicks, abrasions, burning, and scuffing of cables are prevented. Data cables found to be damaged shall be replaced at the contractor’s expense regardless of whether the data cable passes Enhanced Category 6 testing.

##### Cable pathways shall be planned to avoid EMF and RFI interference emanating from sources such as, florescent lighting fixtures, air handling motors, and electrical controls including starters, lighting contractors, and power distribution panels.  All cable runs shall be at least 12 inches away from all florescent lights and EMF sources.  Any violations of this requirement shall be corrected at the Contractor’s expense.

##### A three (3) foot minimum to four (4) foot maximum service loop shall be left inside a pull box mounted as close to the enclosures for all Work Area Outlets that are to be mounted to the inside of enclosures including control panels. Ensure the bend radius of the cable is not exceeded.

##### The Region’s Representative must approve all exceptions.

##### For wall, ceiling or floor installations, conduit to be anchored every one (1) metre.

#### Work Area Termination

##### Work area outlets shall be colour-coded yellow for data, orange for Device level Rings and beige for voice and labeled according to the Region’s conventions specified in this document.

##### Ends of cables terminating at the work area shall be tagged and labeled according to the Region’s conventions specified in this document.

##### For fixed-walled offices the building contractor will supply in-wall conduit.

### Backbone

#### Contractor shall supply and install the transmission media and terminating hardware to provide interconnection between the Network Core Enclosure and each Network Distribution Enclosure in a star topology.

#### All fibres will be run in conduit and terminate in the Network Core Enclosures equipped with sufficient panels, couplers and jumper storage shelves to terminate and secure all fibres.

#### Adequate conduit space will be available in all Network Core Enclosures such that no drilling is necessary.

#### Contractor shall run the horizontal cables in a star topology, terminated in the Network Core Enclosure at one end and in the Network Distribution Enclosures at the other end.

#### Contractor shall observe the bending radius and pulling strength requirements of all backbone cables during handling and installation.

### Network Distribution Enclosure Termination

#### Termination

##### All data cables shall be terminated in the enclosure on CommScope patch panels mounted in 19” racks.

##### Data cable ends at the Network Distribution Enclosures shall be labeled according to the Region’s conventions specified in this section

##### Patch cables shall be bundled in a neat and organized manner.

#### Grounding Conductor

##### The Contractor shall be responsible for providing an approved ground at all newly installed distribution frames, and/or insuring proper bonding to any existing facilities.

##### The Contractor shall also be responsible for ensuring ground continuity by properly bonding all appropriate cabling, closures, cabinets, service boxes, and framework.

##### All grounds shall consist of #6 AWG copper wire and shall be supplied from an approved building ground and bonded to the main electrical ground.

##### Grounding must be in accordance with the ESA, NEC, NFPA and all local codes and practices.

### Workmanship

#### Components of the Structured Cabling System shall be installed in a neat, workmanlike manner.

#### Wiring color codes shall be strictly observed and terminations shall be uniform throughout the system.

#### Identification markings and systems shall be uniform.

#### ANSI/TIA/EIA 568-A wiring codes shall standardize all Structured Cabling System wiring.

### Miscellaneous Equipment

#### The Contractor shall provide any necessary screws, anchors, clamps, tie wraps, distribution rings, wire moulding, miscellaneous grounding and support hardware, etc., necessary to facilitate the installation of the System.

### Special Equipment and Tools

#### It shall be the responsibility of the Contractor to furnish any special installation equipment or tools necessary to properly complete the System.

## Tagging Convention Standard

### General

#### The requirements of this Section will take precedence over other Sections, with respect to network component identification.

#### The codification of network components, cables and cable routing shall follow the identification standards detailed in this Specification Section.

### Network Enclosure Identification

#### This section applies to the labeling of all network enclosures including the Network Core Enclosure, Network Distribution Enclosures and PC Enclosure.

#### Provide a nameplate for each enclosure on the top-left corner of the door.

#### Use engraved gravoply laminate nameplates having white letters on black background. Minimum nameplate height shall be 50 mm. Minimum character height shall be 12 mm.

#### Mount nameplates with adhesive backing.

#### Centre lettering on each line.

#### Nameplates to be as per drawings.

#### Network Core Enclosure shall be labeled NETWORK CORE ENCLOSURE.

#### Network Distribution Enclosures labels shall be “NETWORK DISTRIBUTION ENCLOSURE XXYNDE01. Where XX is the code for the plant/facility, Y is the code for the process area and 01 is the sequential number of the NDEs in that process area..

#### PC Enclosure names utilize a seven character alpha numeric device number which is based on the SCADA name of the work station inside the enclosure. PC Enclosure names shall be YYZWSXX where YY represents the plant, Z represents the process area where the enclosure is located, WS stands for work station and XX is a numeric code which starts at 01 and increments by 1 for each new PC enclosure in the specific process area. See drawings for indication of the SCADA work station name. Nameplates shall have the descriptive name PC ENCLOSURE.

### Work Area Outlet Identification

#### Work Area Outlets, are, associated with a Network Distribution Enclosure and a patch panel termination point so they will utilize the Network Distribution Enclosure  name followed by “-WAO” + (X) where X is a unique number related to the termination point on the patch panel. For example, the first Work Area Outlet associated with Network Distribution Enclosure NDE03 would be tagged as NDE03-WAO1. The horizontal cable would then be terminated on the first termination point on the first patch panel in NDE03.

#### Labels for each Work Area Outlet shall be laser printed, self-laminating, adhesive, polyester, or polyolefin. Hand-written labels will not be accepted.

#### Lettering shall be black on a white background. Characters shall be a minimum of 6 mm high.

#### Provide white snap-in icons for each port. Material ID 107296642

### UTP and Fibre Patch Panels

#### Labels for patch panels shall be laser printed, self-laminating, adhesive, polyester, or polyolefin. Hand-written labels will not be accepted.

#### Lettering shall be black on a white background. Characters are a minimum of 6 mm high.

#### Labels shall be applied to patch panels in such a manner as to be readily visible and not obscured by structured cabling or patch cords.

#### The tagging convention for Network Distribution Enclosure patch panels will employ a four (4) character alphanumeric tag. The first two characters will indicate the type of patch panel. The second two characters will be a unique index within each enclosure starting from the top. The characters “CP” will denote Copper Ethernet Patch Panels. The characters “FP” will denote Fibre Patch Panels. For example the second copper Ethernet patch panel from the top in Network Distribution Enclosure NDE03 would be labeled CP02.

### UTP Patch Panel Termination Point

#### Each patch panel termination point will be labeled.  The label will identify the corresponding Work Area Outlet to which it is connected. For example the first termination point will be labeled NDE03-WAO1 and will be connected to the work area outlet with the same name. The next termination point will be labeled NDE03-WAO2 and will be connected to the work area outlet with the same name.

#### Labels for each logical group shall be laser printed, self-laminating, adhesive, polyester, or polyolefin. Hand-written labels will not be accepted.

#### Lettering shall be black on a white background. Characters are a minimum of 4 mm high.

### Fibre Optic Patch Panel Termination Point

#### Terminate all strands of each fibre optic cable.

#### The ordering and colour of individual fibres will be the same for each fibre cable and compliant with TIA/EIA-568-A.

#### Labels shall be laser printed, self-laminating, adhesive, polyester, or polyolefin. Hand-written labels will not be accepted.

#### Lettering shall be black on a white background. Characters are a minimum of 4 mm high.

#### A label shall be applied to the top of each fibre adapter panel module associated with a single fibre cable indicating the destination of the cable.  The cable destination shall be the Network Distribution Enclosure tag name.

### Network Cable Identification

#### Use durable non-fading sleeve type wire markers to identify network cables.

#### Labels for cabling shall be laser printed, self-laminating, adhesive, polyester (indoor/outdoor). Hand-written labels will not be accepted.

#### Lettering shall be black on a white background. Characters shall be a minimum of 4 mm in height.

### Fibre Optic Backbone Cables

#### As a minimum, fibre optic backbone cables are to be labeled at both ends of the cable.

#### In addition, the fibre backbone cables are to be labeled at each transition. A transition is defined as: a change in ducting (e.g. cable tray to conduit), a change in direction of more than 45 degrees, or an entrance and exit of ducting through a wall or floor.

#### If a single fibre cable is run in conduit then the transition labels shall be applied to the conduit.

#### If multiple fibre cables are run in the same conduit then the transition labels shall be applied to the individual fibre cables.

#### The tagging convention for identification of fiber optic backbone cables shall indicate the source and destination of the cable separated by a colon. For example a fiber optic backbone cable whose source is Network Core Enclosure XNDE01, Fiber Patch Panel #1 and terminates in Network Distribution Enclosure XNDE01, Fiber Patch Panel #1 would have the following tag:

##### XNDE01-FP01 : X_NDE01-FP01

#### X represents the process area that the NDE is in.

### Horizontal Cables

#### As a minimum, horizontal CAT6 cable is to be labeled at both ends of the cable.

#### The tagging convention for identification of fiber optic backbone cables shall indicate the source and destination of the cable separated by a colon. For example a fiber optic backbone cable whose source is Network Core Enclosure XNDE01, Fiber Patch Panel #1 and terminates in Network Distribution Enclosure XNDE01, Fiber Patch Panel #1 would have the following tag:

### XNDE01-FP01 : X_NDE01-FP01

#### X represents the process area that the NDE is in.

### Patch Cords

#### No labels are required on copper or fibre patch cords.

### Cable Routing

#### All ducting (cable tray or conduit) carrying fibre optic backbone cable shall be tagged as “LAN BACKBONE”. Labels shall be applied on the conduit every 6 meters, on either side of a wall pass through or on either side of a bend of 45 degrees or greater.

#### All ducting carrying Horizontal cables shall be tagged as “LAN”. Labels shall be applied on the conduit every 6 meters, on either side of a wall pass through or on either side of a bend of 45 degrees or greater.

#### Labels should be black lettering on white background. Letters should be 22mm in height. Label are to be orientated so they can easily be read from the ground.

## Testing and Inspection

### General

#### All terminated data cables shall be tested.

#### Tests shall include conformance to EIA/TIA 568-A Category 6 specifications

#### The contractor shall be responsible for bringing any cable not meeting requirements into compliance at no cost to the Region.

#### At the completion of each phase the contractor and the Region’s Representative shall jointly inspect the work for completeness, consistency, and conformance to required standards. The following points in particular shall be examined:

##### That all labeling of cables and work area outlets meet specifications.

##### That there is consistency in the colour coding of work area outlets.

##### That all cables are properly routed and supported.

##### That all cables are tested and meet specifications.

##### That all terminations meet specifications.

##### That the overall appearance of work area and Network Distribution Enclosure is clean, neat, and orderly.

#### Unspecified equipment and material: Any item of equipment or material not specifically addressed on the drawings or in this document and required to provide a complete and functional SCS installation shall be provided in a level of quality consistent with other specified items.

### Cable System Testing – Copper

#### Category 6 horizontal cables shall be tested according to test set manufacturer’s instructions utilizing the latest firmware and software.

#### Complete, end to end, test results must be submitted to the Region.

#### Voice and data horizontal wiring pairs shall be tested from the work area outlet to the Network Core Enclosure.

#### Testing of all copper wiring shall be performed prior to system cutover. All cables and termination hardware shall be 100% tested for defects in installation and to verify cable performance under installed conditions.  All conductors of each installed cable shall be verified usable prior to system acceptance.  Any defect in the cable system installation including but not limited to cable, connectors, feed-through couplers, patch panels, splices, and connector blocks shall be repaired or replaced in order to ensure 100% useable conductors in all cables installed. The Category 6 cable runs shall be tested for conformance to the specifications of EIA/TIA 568-A Category 6.

#### All cables shall be tested in accordance with this document and best industry practices.

#### 100 percent of the horizontal wiring pairs shall be tested for opens, shorts, polarity reversals, transposition and presence of AC voltage. Each cable shall be tested for continuity on all pairs and/or conductors.  Twisted-pair cables shall be tested for continuity, pair reversals, shorts, and opens using a “green light” type test set plus tests that indicate installed cable performance.  These cables shall be tested using a Class II cable analyzer.

#### Continuity: Each pair of each installed cable shall be tested using a “green light” test set that shows opens, shorts, polarity and pair-reversals.  Shielded/screened cables shall be tested with a device that verifies shield continuity in addition to the above stated tests.  The test shall be recorded as pass/fail as indicated by the test set in accordance with the manufacturers recommended procedures, and referenced to the appropriate cable identification number and circuit or pair number.  Any faults in the wiring shall be corrected and the cable re-tested prior to final acceptance.

#### Length: Each installed cable shall be tested for installed length using a TDR type device.  The cables shall be tested from patch panel to patch panel, block to block, patch panel to outlet or block to outlet as appropriate.  The cable length shall conform to the maximum distances set forth in the TIA/EIA-568-A Standard.  Cable lengths shall be recorded, referencing the cable identification number and circuit or pair number.  For multi-pair cables, the longest pair length shall be recorded as the length for the cable.

#### Performance Verification: Enhanced Category 6 unshielded twisted pair (UTP) data cable shall be performance verified using an automated test set.  This test shall be conducted from the patch panel or wiring block to the outlet (installed link).  The test shall include checks for continuity and length as defined above and the following:

##### Bi-directional Near End Cross-Talk (NEXT)

##### Attenuation to Cross-Talk Ratio (ACR)

#### The cables under test shall meet or exceed the requirements for an Enhanced Category 6 link as defined by the following table:

#### Table 3 - Enhanced Category 6 Cable Performance

| Frequency, MHz | Attenuation, dB/100m Max. | NEXT, dB Min./ Typical | PSNEXT, dB Min./ Typical | ELFEXT, dB Min./ Typical | PSELFEXT, dB Min./ Typical | Return Loss, dB Min. | ACR, dB Typical, 90m | PS ACR, dB Typical, 90m |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| .772 | 1.8 | 72/81 | 69/77 | 66/73 | 63/70 | 19.4 | 77.4 | 73.4 |
| 1 | 2.0 | 70/79 | 67/75 | 64/71 | 61/68 | 20.0 | 75.2 | 71.2 |
| 4 | 4.1 | 61/70 | 58/66 | 52/59 | 49/56 | 23.1 | 64.3 | 60.3 |
| 8 | 5.8 | 57/66 | 54/62 | 46/53 | 43/50 | 24.5 | 58.8 | 54.8 |
| 10 | 6.5 | 55/64 | 52/60 | 44/51 | 41/48 | 25.0 | 56.2 | 52.2 |
| 16 | 8.2 | 52/61 | 49/57 | 40/47 | 37/44 | 25.0 | 51.6 | 47.6 |
| 20 | 9.3 | 51/60 | 48/56 | 38/45 | 35/42 | 25.0 | 49.6 | 45.6 |
| 25 | 10.4 | 49/58 | 46/54 | 36/43 | 33/40 | 24.3 | 46.6 | 42.6 |
| 31.25 | 11.7 | 48/57 | 45/53 | 34/41 | 31/38 | 23.6 | 44.5 | 40.5 |
| 62.5 | 17.0 | 43/52 | 40/48 | 28/35 | 25/32 | 21.5 | 34.7 | 30.7 |
| 100 | 22.0 | 40/49 | 37/45 | 24/31 | 21/28 | 20.1 | 27.2 | 23.2 |
| 155 | 28.1 | 37/46 | 34/42 | 20/27 | 17/24 | 18.8 | 18.7 | 14.7 |
| 200 | 32.4 | 36/45 | 33/41 | 18/25 | 15/22 | 18.0 | 13.8 | 9.8 |
| 300 | 41.0 | 33/42 | 30/38 | 14/21 | 11/18 | 16.8 | 3.1 | – |
| 350 | 44.9 | 32/41 | 29/37 | 13/20 | 10/17 | 16.3 | – | – |

#### Test results shall be automatically evaluated by the equipment, using the most up-to-date criteria from the TIA/EIA Standard, and the result shown as pass/fail.  Test results shall be printed directly from the test unit or from a download file using an application from the test equipment manufacturer.  The printed test results shall include all tests performed, the expected test result and the actual test result achieved. Use test software to organize test results and provide results that are compatible with the label software.

### Cable System Testing – Fibre Optic

#### All fibre testing shall be performed on all fibres in the completed end-to-end system. Testing of all fibre optic cable shall be performed prior to system cutover. All cables and termination hardware shall be 100% tested for defects in installation and to verify cable performance under installed conditions.  All conductors of each installed cable shall be verified usable prior to system acceptance.  Any defect in the cable system installation including but not limited to cable, connectors, feed-through couplers, patch panels, splices, and connector blocks shall be repaired or replaced in order to ensure 100% useable conductors in all cables installed.

#### Testing shall consist of a bi-directional end to end OTDR trace performed per EIA/TIA 455-61 and a bi-directional end to end power meter test performed per EIA/TIA 455-53A.

#### The system loss measurements shall be provided at 850 and 1300 nanometers for multimode fibres

#### The system loss measurements shall be provided at 1310 and 1550 for single mode fibres.

#### Pre-installation cable testing:

##### The Contractor shall test all light guide cable prior to the installation of the cable.

##### The Contractor shall assume all liability for the replacement of the cable should it be found defective at a later date.

#### Allow for min 2 meetings for coordination with electrical for cabling conduit and power circuits/outlets.

#### Refer to network architecture drawing for locations of work area outlets, Network Distribution Enclosures and Network Core Enclosure.

#### All fibre terminations shall be visually inspected with a minimum 100 X microscope to ensure that no surface imperfections exist after final polishing.  In addition, each fibre strand shall be tested for attenuation with an optical power meter and light source.

#### Multimode Fibre Testing: Horizontal distribution multimode optical fibre attenuation shall be measured in one direction at either 850 nanometers (nm) or 1300 nm using an LED light source and power meter.  Backbone multimode fibre shall be tested at both 850 nm and 1300 nm in one direction.  Test set-up and performance shall be conducted in accordance with ANSI/EIA/TIA-526-14 Standard, Method B.  One 2-meter patch cord shall be used for the test reference and two 2-meter patch cords shall be used for the actual test.  This test method uses a one-jumper reference, two-jumper test to estimate the actual link loss of the installed cables plus the loss of two connectors.

#### The testing shall be compliant with the performance measurements in the following table:

#### Table 4 – Performance Measurements

| Subsystem | Max Segment Length (meters) | Attenuation (dB) @ 850 | Attenuation (dB) @1300 |
| --- | --- | --- | --- |
| Horizontal | 100 | 2.5 | 2.2 |
| Centralized (splice) | 300 | 2.9 | 2.3 |
| Centralized (interconnect) | 300 | 3.4 | 2.7 |
| Building Backbone | 500 | 3.9 | 2.6 |

#### Single-mode Fiber: Horizontal distribution single-mode optical fiber attenuation shall be measured in one direction at either 1310 nm) or 1550 nm. Backbone single-mode fiber shall be tested at both 1310 nm and 1550 nm in one direction. Test set-up and performance shall be conducted in accordance with ANSI/EIA/TIA-526-7: Optical Power Loss Measurement, Single-mode standards.  Detectors shall have a dynamic range of at least +3 dB to -55 dB.

#### Single-mode backbone fibre-optic cabling shall meet the following loss and length criteria:

##### Attenuation at 1310 nm shall be less than or equal to: fiber length (km) x 1.0dB/km + number connector pairs x 0.75dB + number of splices x 0.3dB.

##### Attenuation at 1550 nm shall be less than or equal to: fiber length (km) x 1.0dB/km + number connector pairs x 0.75dB + number of splices x 0.3dB.

##### Length shall be less than or equal to 3000 metres.

#### Where concatenated links are installed to complete a circuit between devices, test each link from end to end to ensure the performance of the system.  After the link performance test has been successfully completed, all patch cables shall be installed to complete and then the entire channel shall be tested.  The test method shall be the same used for the test described above.  The evaluation criteria shall be established with the Region prior to the start of the test.  The values for calculating loss shall be those defined in the ANSI/TIA/EIA Standard.

#### Test results must be submitted in two (2) formats. First, must be original file(s) downloaded from the tester. Second, the file must be cohesively placed in Excel format with the following field:

##### ER / TR RM# /RM # of drop / Port # / all relevant test information in as many fields as necessary.

## Stage 1 Site Acceptance Test (SAT1) - Network Distribution Enclosure

### The system components that will be Site Acceptance Tested are the Network Distribution Enclosures. The SAT1 will evaluate workmanship and verify construction and components against the Layout drawings and associated Component Schedules submitted to and reviewed by the Consultant.

### Provide Record and Shop Drawings to the Consultant at least fifteen (15) Working Days prior to the test, for review.

### Prepare a checklist or test sheet using MICROSOFT Excel. Submit to the Consultant, fifteen (15) Working Days prior to the commencement of the test, for review. The Contractor shall conduct the test when directed by the Consultant. At a minimum, the Consultant and the Region shall witness the test.  As a minimum, the SAT1 checklist or test sheet must include products / materials used in the construction of the Network Distribution Enclosure.

### The SAT1 will be completed when items in the checklist have been witnessed and initialled by the Consultant as being in conformance with the design as specified.

### To mitigate the possibility for major re-work, a single (1) Network Distribution Enclosure will be Site Acceptance Tested. Following acceptance of the enclosure the Contractor will be directed to proceed with construction of the remaining Network Distribution Enclosures.

### The remaining Network Distribution Enclosures will not undergo a Stage 1 Site Acceptance Test. However, the Contractor will certify that: each enclosure has been constructed in the same manner as the equivalent witnessed and accepted enclosure, each enclosure has undergone a QA/QC test by the Contractor, and the manufacturer and catalogue number of components utilized are identical to those of the equivalent witnessed and accepted enclosure. Network Distribution Enclosures that do not comply with above will be made compliant at no expense to the Region.

## Stage 2 Site Acceptance Test (SAT2)

### Stage 2 Site Acceptance Tests will evaluate the workmanship and verify installation against the Installation and Layout drawings.

### Provide Record and Shop Drawings to the Consultant fifteen (15) Working Days prior to the test for review.

### Prepare a checklist or test sheet using MICROSOFT Excel. Submit to the Consultant, fifteen (15) Working Days prior to the commencement of the test, for review. The Contractor shall conduct the test when directed by the Consultant. At a minimum, the Consultant and the Region shall witness the test.

### As a minimum, the SAT2 checklist or test sheet must include verification of the following:

#### All products / materials used in the construction of the Network Core Enclosure

#### UPS power distribution and grounding

#### Utility power distribution and grounding

#### Fibre-optic cabling installation and termination

#### CAT6 (UTP/STP) cabling installation and termination

#### Work-Area Outlet installation and termination

### The SAT will be completed when items in the checklist have been witnessed and initialled by the Consultant as being in conformance with the design as specified.

### Network Distribution Enclosure SAT

#### The Contractor will provide one complete Network Distribution Enclosure, associated Work-Area Outlet and Horizontal Cable for the Network Distribution Enclosure SAT. Following acceptance, the Contractor will be directed to proceed with the installation of the remaining Network Distribution Enclosures, Work-Area Outlets and Horizontal Cabling. The Contractor is to note that the fibre optic backbone cable installation will be included in the Network Core Enclosure SAT.

#### At a minimum, the complete Network Distribution Enclosure for the SAT will include the installation of the Ethernet Switch, UTP patch panels, fibre patch panel, power supplies, horizontal cable terminations, cable management and patch cords.

#### The remaining Network Distribution Enclosures will not undergo a witnessed Site Acceptance Test. However, the Contractor will certify that each Network Distribution Enclosure has been provided in the same manner as the witnessed and accepted Network Distribution Enclosure. The Region reserve the right to do a random inspection of the remaining Network Distribution Enclosures and those that do not comply with the above will be made compliant at no expense to the Region.

### Network Core Enclosure

#### As a minimum, the Network Core Enclosure SAT will include evaluation of the following: installation of the Core Switch(s), Core Router(s), patch panels, power supplies, horizontal cable terminations, cable management and patch cords.

### PC Enclosures

#### As a minimum, the PC Enclosure will include evaluation of the following: installation of the PC Workstation, UPS, Monitor, power supplies, horizontal cable terminations, cable management and patch cords.

## Test Documentation

### Test documentation shall be provided in an electronic format from the network tester as well as hard copies in a three ring binder(s) separate from all other contract documentation within three weeks after substantial completion of the project.  The binder(s) shall be clearly marked on the outside front cover and spine with the words “Test Results”, the project name, and the date of completion (month and year).  The binder shall be divided by major heading tabs, Horizontal Cabling System and Fibre Optic Backbone Cabling. Each major heading shall be further sectioned by test type.  Within the horizontal and backbone sections, provide scanner test results (Category 5e and 6). Test data within each section shall be presented in the sequence listed in the administration records.  The test equipment by name, manufacturer, model number and last calibration date will also be provided at the end of the document.  Unless a more frequent calibration cycle is specified by the manufacturer, an annual calibration cycle is anticipated on all test equipment used for this installation.  The test document shall detail the test method used and the specific settings of the equipment during the test.

### When repairs and re-tests are performed, the problem found and corrective action taken shall be noted, and both the failed and passed test data shall be collocated in the binder.

## Firestop Systems

### A firestop system is comprised of: the item or items penetrating the fire rated structure, the opening in the structure and the materials and assembly of the materials used to seal the penetrated structure.  Firestop systems comprise an effective block for fire, heat, vapour and pressurized water stream.

### All penetrations through fire rated building structures (walls and floors) shall be sealed with an appropriate firestop system.  This requirement applies to through penetrations (complete penetration) and membrane penetrations (through one side of a hollow fire rated structure).  Any penetrating items i.e., riser slots and sleeves, cables, conduit, cable tray, and raceways, etc. shall be properly firestopped.

### Firestop systems shall be UL Classified to ASTM E814 (UL 1479) and shall be approved by a qualified Professional Engineer (PE), licensed (actual or reciprocal) in the province where the work is to be performed.  A drawing showing the proposed firestopped system, stamped/embossed by the cognizant PE shall be provided to the Region’s Technical Representative prior to installing the firestop system(s).

### All firestop systems shall be installed in accordance with the manufacturer’s recommendations and shall be completely installed and available for inspection by the local inspection authorities prior to cable system acceptance.

## Grounding and Bonding

### The facility shall be equipped with a Telecommunications Bonding Backbone (TBB).  This backbone shall be used to ground all telecommunications cable shields, equipment, racks, cabinets, raceways, and other associated hardware that has the potential to act as a current carrying conductor.  The TBB shall be installed independent of the buildings electrical and building ground and shall be designed in accordance with the recommendations contained in the TIA/EIA-607 Telecommunications Bonding and Grounding Standard.

### Each building shall be equipped with a telecommunications main grounding bus bar (TMGB).  Each Network Distribution Enclosure shall be provided with a telecommunications ground bus bar (TGB).  The TMGB shall be connected to the building electrical entrance grounding facility.  The intent of this system is to provide a grounding system that is equal in potential to the building electrical ground system.  Therefore, ground loop current potential is minimized between telecommunications equipment and the electrical system to which it is attached.

### All racks, metallic backboards, cable sheaths, metallic strength members, splice cases, cable trays, etc. entering or residing in the TC or ER shall be grounded to the respective TGB or TMGB using a minimum #6 AWG stranded copper bonding conductor and compression connectors.

### All wires used for telecommunications grounding purposes shall be identified with a green insulation.  Non-insulated wires shall be identified at each termination point with a wrap of green tape.  All cables and busbars shall be identified and labeled in accordance with the System Documentation Section of this specification.

## Conduit and Ventilated Cable Tray

### Route all copper and fibre cable in 25.4 mm (1”) galvanized rigid-steel conduit, as per Division 16 and in compliance with this specification.

### Completed all work in conjunction with Division 16.

### Where approved by engineer, ventilated cable tray may be used as alternate.

## Penetrations of Walls, Floors and Ceilings

### Prior consent

#### The Contractor shall make no penetration of floors, walls or ceiling without the prior consent of the Consultant and General Contractor.

### Sealing penetrations

#### Where penetrations through acoustical walls or other walls for cableways have been provided for the Contractor or made by the Contractor, such penetrations shall be sealed by the Contractor in compliance with applicable code requirements and as directed by the Consultant or General Contractor.

#### Where penetrations through fire-rated walls for cableways have been provided for the Contractor or made by the Contractor, the Contractor shall seal such penetrations as required by code and as directed by the Consultant or General Contractor.

#### Contractor shall, prior to the commencement of on-site activities, submit to Region for review by its Architect, details of any special systems to be used.

## Warranty and Services

### General

#### Provide a warranty covering the installed cable system against defects in workmanship, components, and performance, and follow-on support after project completion.

#### Materials and workmanship hereinafter specified and furnished shall be fully guaranteed by the contractor for twenty years from transfer of title against any defects.

#### The contractor at no additional cost to the Region shall correct defects, which may occur as the result of faulty materials or workmanship within twenty years after installation and acceptance by the Region. The contractor shall promptly, at no cost to the Region, correct or re-perform (including modifications or additions as necessary) any non-conforming or defective work within the twenty-year warranty period

### Warranty Documentation

#### Complete documentation regarding the manufacturer’s warranty including documentation of the support procedure for warranty issues shall be submitted when the installation is complete.

### Cable System Manufacturer Warranty

#### Contractor shall provide a Twenty (20) year CommScope Structured Connectivity Solution Extended Product Warranty and Application Assurance.

#### An extended component warranty shall be provided which warrants functionality of all components used in the system for 20 years from the date of acceptance.

#### The Performance Warranty shall warrant the installed structured cabling system. The performance warranty must include the labor and materials to replace or repair defective components for the life of the warranty.

### Installation Warranty

#### The Contractor warrants that the works shall, with ordinary use, remain in such conditions as will meet with the approval of the Region’s Representative for a period of twenty four (24) months from the date of the issuance of completion certificates. The Contractor agrees to make good, in a manner satisfactory to the Region’s Representative any imperfections due to material or workmanship.  The decision of the Region’s Representative as to the nature, extent and cause of such imperfections and the necessity for remedying the same shall be final.

#### Should the Contractor fail to comply with the directions of the Region’s Representative, the latter may, after giving the Contractor twenty-four (24) hours notice, perform the necessary work. Should the Region’s Representative judge the failure to be an emergency, they may waive the twenty-four (24) hours notice and perform the necessary work. In both cases, the cost of such work is to be paid, on demand, by the Contractor or failing that, by the Region from any monies owing to the Contractor or by drawing on any securities associated with the contract.

#### If the Region’s Representative notifies the Contractor in writing of imperfections prior to the termination of the warranty period, the Contractor shall make good the imperfections as specified above, notwithstanding that the work of making good may commence after or extend beyond the end of the warranty period.

#### The Contractor warrants also that the materials comply with the Specifications and that the works and materials are free from defects in workmanship and material except defects that exist because the Contractor strictly followed the Specifications or due to service demands beyond the demands established by the Specifications and drawings.

### Additional Warranty

#### Contractor shall state any additional Contractor supplied warranty.

## Damages

### The contractor shall be held responsible for all damages to the building or building systems caused by its employees or subcontractors

### It shall be the responsibility of the contractor to notify the Region’s Representative when damages have occurred and to make the necessary arrangements for the prompt repair of these damages.

END OF SECTION