Regional Municipality of Halton

SCADA Standards Manual

Appendix 5B: SLC Reference Guide

VERSION 2022

Table of Contents

5B.1	Overall Guidelines	1

5B.2	SLC Hardware Selection	1

5B.3	Specific SLC 500 Programming Guidelines	2

IEC-61131 Standards	2

Standard Program Layout	2

SLC Alarming	2

5B.4	SLC Subroutine Descriptions, Purpose, and Layout	3

Ladder Common Elements	3

LAD2	Main Program File	3

LAD3	Field Input Processing	4

LAD4	Field Output Processing	4

LAD5	Digital Input Mapping	4

LAD6	Analog Input Mapping	4

LAD7	Digital Output Mapping	5

LAD8	Analog Output Mapping	5

LAD9	Analog Input Processing	5

LAD10	Digital Input Processing	5

LAD11	Communication	6

LAD12	General Housekeeping	6

LAD15	Automatic Control Program	6

LAD19	Device Drivers	6

LAD21	Duty Alternation	7

LAD22	Duty Assignment Mapping to Virtual Points	7

LAD23	Duty Assignment Mapping to Equipment Points	7

LAD24	Automatic Control of Duty Equipment	7

LAD 41 Program for Dialer Channels	8

5B.5	Standard SLC Software Modules	8

Device Drivers	8

Pump and Valve Device Drivers	8

Standard Layout of SLC Pump Device Drivers	9

Standard Layout of Valve Device Drivers	10

SLC Analog Device Driver	10

Standard Layout of SLC Analog Module	11

5B.6	SLC Message Blocks	12

This Controller	13

Control Bits	14

Messaging for an SLC to a Logix Based Controller	14

5B.7	Configuring data to be read from a SLC to a ControlLogix PLC	18

5B.8	SLC Standard Date File Configuration	22

5B.9	SLC Device Driver Status Bits	25

5B.10	SLC Analog Device Driver Assignments	27

List of Tables

Table 5B.1	SLC Hardware Selection	2

Table 5B.2	Pump Device Driver Standard Logic	10

Table 5B.3	Valve Device Driver Standard Logic	10

Table 5B.4	Analog Device Driver Standard Logic	11

Table 5B.5	Message Block Parameters	13

Table 5B.6	Control Bits	14

Table 5B.7	Data File description	25

Table 5B.8	Device Driver Status Bits	26

Table 5B.9	Analog Device Driver Assignments	29

List of Figures

Figure 5B.1	Conceptual Flow of Program Logic – Subroutine Levels	4

Figure 5B.2	MSG Instruction General Configuration	13

Figure 5B.3	PLC/SLC Message Mapping	14

Figure 5B.4	PLC/SLC Logix Tag Mapping	15

Figure 5B.5	MSG Read Instruction and Controller-scoped Array Map	16

Figure 5B.6	General Configuration MultiHop Selection	16

Figure 5B.7	MultiHop Configuration Parameters	17

Figure 5B.8	MultiHop Selection	17

Figure 5B.9	Logix Backplane Slot Entry	18

Figure 5B.10	Controller Scoped Tags for a MSG read instruction	19

Figure 5B.11	Message Read Instruction Configuration Tab	20

Figure 5B.12	Message Read Instruction SLC Path Entry	21

Figure 5B.13	Message Read Instruction SLC Type Read Tag Tab	21

## Overall Guidelines

#### This appendix must be reviewed in conjunction with the other SCADA standards, specifically section 5.

#### This Appendix provides a reference to existing SLC installations within Halton Region.  Under no circumstances will Halton Region accept the SLC PLC platform for new installs.

## SLC Hardware Selection

#### Consultants must use the following table when specifying SLC PLC hardware.

| Processor Selection |  |  |
| --- | --- | --- |
| Model | Model | Application |
| SLC Processor | 1746-L553, 1746-L552 | Use of 1746-L551 is not accepted by Halton Region. |
| Power Supply and Chassis Selection |  |  |
| Description | Module | Notes |
| SLC Power Supply | 1746-P4 |  |
| SLC Chassis | 1746-A7, 1746-A10, 1746-A13 | Avoid use of 1746-A4. |
| Communication Module Selection |  |  |
| Description | Module | Notes |
| SLC Remote I/O Scanners | 1747-SN | Use of 1747-SN must be approved by Halton Region. |
| Rack Extension Cable |  |  |
| Description | Module | Notes |
| SLC Rack Extension Cable | 1746-C7, 1746-C9, 1746-C16 | The preferred design is to mount each rack horizontally. |
| Digital Input Module Selection |  |  |
| Description | Module | Notes |
| 1746-IA16 | 16 120 VAC Digital Inputs | Halton Region’s preference is 120 VAC digital inputs. |
| 1746-IV16 | 16 24 VDC Digital Input | 1746-IB16 is an approved alternative. |
| Digital Output Module Selection |  |  |
| Description | Module | Notes |
| 1746-OA16 | 16 120 VAC Digital Outputs | Halton Region’s preference is 120 VAC Digital Outputs |
| 1746-OV16 | 16 24 VDC Digital Output | 1746-OB16 is an approved alternative. |
| Analog Input Module Selection |  |  |
| Description | Module | Notes |
| 1746-NI8 | 8 isolated 4-20 mA analog inputs | 1746-NI4 is an approved alternative. |
| Analog Output Module Selection |  |  |
| Description | Module | Notes |
| 1746-NO8I | 8 isolated 4-20 mA analog outputs | 1746-NO4I is an approved alternative. |
| Slot Filler Modules |  |  |
| Description | Module | Notes |
| Slot Filler | 1746-N2 | All spare slots must contain a slot filler module. |

- SLC Hardware Selection

#### The Consultant must take into consideration all provisions to ensure that adequate memory is available for current and future programming needs. All foreseeable future requirements must be considered as current requirements when applying Halton Region’s PLC processor selection criteria.

## Specific SLC 500 Programming Guidelines

#### SLC Process Control Software can be developed using a number of different formats. Each of these formats provides control and monitoring of the process to meet the intent of the process narrative. To facilitate maintenance and troubleshooting of the software Halton Region has developed a standard program layout using ladder logic, one (1) of the four (4) languages recognized by the International Electrotechnical Commission (IEC) for the programming of field controllers.

### IEC-61131 Standards

#### Only Ladder Diagram (LD) programming will be accepted in SLC processors.

### Standard Program Layout

#### Halton Region has developed a standard program layout for the implementation of PLC logic.  The purpose of the standard layout is to facilitate troubleshooting and has been created with the concept of clarity of code taking precedence over compactness of code.  To facilitate the ongoing efforts to ensure consistency between projects and those Programmers delivering PLC programming solutions, Halton Region has adopted a standard layout.

### SLC Alarming

#### Analog Modules

##### Analog modules will create the following virtual alarms.

###### Transmitter Out of Range;

###### Signal Off Scan; and,

###### Analog HIHI, HI, LO and LOLO Alarms.

##### Acknowledging any of these virtual alarms at the HMI will cause the alarm banner to indicate an acknowledged alarm condition. Until the analog signal is within normal operating range, the alarm status will remain ON.

##### A virtual alarm can be individually enabled/disabled from the HMI advanced pop-up at the analog control window. This allows the user to disable virtual alarms that are not required for a specific analog device (ex. Flow LOLO).

#### Device Drivers

##### Device drivers create the following virtual alarms.

###### Deviation alarm for pumps (speed) and valves (position);

###### Device Fail to Start/Stop or Open/Close; and,

###### Device Uncommanded Start/Stop or Open/Close.

##### When an alarm condition is present, the alarm will appear at the HMI. The alarm condition remains active until acknowledged from device control pop-up screen. The acknowledgement resets the alarm at the PLC.  The deviation alarm is the only alarm that does not need to be acknowledged at the HMI for it to reset in the PLC logic.

## SLC Subroutine Descriptions, Purpose, and Layout

#### The following section provides a brief description of the purpose of the standard subroutines within the base load.

### Ladder Common Elements

#### All ladders (or subroutines), except for MAIN, can be enabled or disabled by manipulating the corresponding bit, B15:X/YY, where xx represents the program file number being called. For example, manipulating the value of B15:0/3 to 0 (OFF) will disable subroutine 3 (INPUTS).

### LAD2	Main Program File

#### Description:	MAIN

#### Purpose:	This subroutine is the ‘spine’ or ‘heart’ of the program. It is from this subroutine that all other subroutines are directly, or indirectly, ‘called’. This subroutine is the only Level 1 subroutine in the program.

#### Layout:	This subroutine consists mostly of ‘calls’ to other subroutines such as:

##### General Housekeeping;

##### Inputs;

##### Communications;

##### Automatic Control Programs;

##### Device Drivers;

##### Operator Interface;

##### Auto Dialer; and,

##### Outputs.

#### The first rung of this subroutine consists of a timer module that is used to prevent the ‘calls’ to all subroutines after power up or a download. This is a feature that is primarily used for safety and to reduce confusion during the first 5 seconds of power up.

#### The last three (3) rungs contains the PLC security logic that reports back to the Wonderware Historian when a processor is edited on-line by a programmer.

#### This software must not be removed or modified from its present state

#### The subroutine levels are defined in the figure below.

- Conceptual Flow of Program Logic – Subroutine Levels

### LAD3	Field Input Processing

#### Description:	INPUTS

#### Purpose:	This subroutine is the main input program that is responsible for the processing of all physical inputs for field signals. It is from this subroutine that all subroutines responsible for digital and analog input processing directly, or indirectly, are ‘called’. This subroutine is considered a Level 2 subroutine.

#### Layout:	This subroutine consists only of ‘calls’ to other subroutines as follows:

##### DI_Raw;

##### AI_Raw;

##### AI_Processing;

##### DI_Processing;

### LAD4	Field Output Processing

#### Description:	OUTPUTS

#### Purpose:	This subroutine is the main output program and is responsible for the processing of all physical outputs for field equipment such as pumps, valves, horns and lights. It is from this subroutine that all subroutines responsible for digital and analog output processing directly, or indirectly, are ‘called’. This subroutine is considered a Level 2 subroutine.

#### Layout:	This subroutine consists only of ‘calls’ to other subroutines as follows:

##### Digital Outputs (DO); and,

##### Analog Outputs (AO).

#### When remote I/O is connected to the processor, the subroutine containing the logic to write to the outputs should be called after the AO subroutine.

### LAD5	Digital Input Mapping

#### Description:	DI_RAW

#### Purpose:	This subroutine is responsible for the mapping of the ‘raw’ digital inputs to data table file B11. No other subroutines are ‘called’ from this subroutine.  This subroutine is considered a Level 3 subroutine.

#### Layout:	This logic uses COPY blocks to copy the values of entire digital input cards to the corresponding B11 data table file. For example if a SLC has two (2) digital inputs cards located in slots 2 and 3 a rung will exist in this subroutine that copies the values I:2.0 to B11:2 (B11:2/0 – B11:2/15). Similarly, a second rung, or branch off the first rung, will exist that moves the values of the second digital input card I:3.0 to B11:3 (B11:3/0-B11:3/15).

### LAD6	Analog Input Mapping

#### Description:	AI_RAW

#### Purpose:	This subroutine is the logic responsible for the mapping of the ‘raw’ analog inputs to data table file N112. No other subroutines are ‘called’ from this subroutine. This subroutine is considered a Level 3 subroutine.

#### Layout:	This logic utilizes MOVE and /or COPY blocks to map the values of entire analog input cards to the corresponding N112 data table file. For example, if a SLC has one (1) analog input card located in slot 6 a rung will exist in this subroutine that copies the values of four (4) elements from I:6.0 to N112:1 (N112:1-4).

#### The configuration of an NI8 card is performed in rung 0.  If more than one card is connected, Programmers can branch the copy and use the same N110:0 address.  This rung can be deleted if no NI8 cards are installed in the chassis.

### LAD7	Digital Output Mapping

#### Description:	DO

#### Purpose:	This subroutine contains the logic responsible for passing requests from device drivers and other subroutines that control devices with discrete (digital) outputs. No other subroutines are ‘called’ from this subroutine. This subroutine is considered a Level 3 subroutine.

#### Layout:	This program links requests, such as ‘PUMP1 START’ or VALVE2 OPEN’, to the digital output that is physically wired to a device in the field. Simulation bits exist in this subroutine that allow for testing, irrespective of programming evaluations, of each digital output. Rungs for spare digital outputs are included in this subroutine.

### LAD8	Analog Output Mapping

#### Description:	AO

#### Purpose:	This subroutine contains the logic responsible for passing requests from device drivers and other subroutines that control devices with analog outputs. No other subroutines are ‘called’ from this subroutine. This subroutine is considered a Level 3 subroutine.

#### Layout:	This logic links control parameters, such as ‘PUMP2 SPEED SETPOINT’ or VALVE2 POSITION SETPOINT’, to the analog output that is physically wired to a device in the field. This subroutine is also responsible for the scaling of engineering units, such as 0-100%, to the ‘raw’ scale that is used by the field controller. As identified earlier in the standard the ‘raw’ scale for an SLC is (6250-31250). Rungs for spare analog outputs are included in this subroutine.

#### The configuration of an NO8I card should be performed in Rung 0.  If more than one card is connected, Programmers can branch the copy and use the same N110 address.

### LAD9	Analog Input Processing

#### Description:	AI_MAIN

#### Purpose:	This subroutine contains the main analog input logic and is responsible for the processing of all analog inputs. It is from this subroutine that all analog input processing logic is ‘called’. This subroutine is considered a Level 3 subroutine.

#### Layout:	This subroutine consists only of ‘calls’ to analog input drivers such as:

##### Analog Input 1;

##### Analog Input 2;

### LAD10	Digital Input Processing

#### Description:	DI_EVAL

#### Purpose:	This subroutine contains the digital input evaluation logic and is responsible for the processing of all digital inputs. No other subroutines are called from this program. This subroutine is considered a Level 3 subroutine.

#### Layout:	All digital inputs have a dedicated rung with two branches. The multiple branch approach allows for both Normally Opened and Closed modes of operation. This multiple ‘mode’ operation is made possible by manipulating the corresponding bit, B12:X/YY. For example, an SLC with two (2) separate digital input cards (1746-IV16), manipulating the value of B12:2/2 to 1 (ON) will enable the NORMALLY CLOSED mode of operation for the 3rd input (I:3/2) on the 2nd digital input card.

### LAD11	Communication

#### Description:	COMM

#### Purpose:	This subroutine contains the logic responsible for the exchange of process information between field controllers. No other subroutines are called from this logic. This subroutine is considered a Level 2 subroutine.

#### Layout:	It is in this subroutine that message blocks read process information from other field controllers. The logic is structured using a combination of timers and counters to ensure that communication is carried out in sequential order, thus preventing the execution of simultaneous message blocks.  The message block error bit is used to signify a failed communication link.

### LAD12	General Housekeeping

#### Description:	GEN_HK

#### Purpose:	This subroutine contains the ‘general housekeeping’ logic components that are common to multiple areas of the field controller. No other subroutines are called from this program. This subroutine is considered a Level 2 subroutine.

#### Layout:	Global parameters such as internal clock resets (i.e. Day Reset bits that are used for flow totalizers) and flow total sample triggers are established.

### LAD15	Automatic Control Program

#### Description:	ACP

#### Purpose:	This subroutine is the main automatic control program (ACP). It is from this subroutine that all other subroutines dedicated to the automatic control of field equipment are ‘called’. This subroutine is considered a Level 2 subroutine.

#### Layout:	This subroutine consists only of ‘calls’ to other automatic control related programs such as:

##### Duty Alternations (DUTY_ALT);

##### Duty Translations (DUTY_IN);

##### Device Automatic Control (DEV_ACP); and,

##### Duty Assignments (DUTY_OUT).

### LAD19	Device Drivers

#### Description:	DEV_DRV

#### Purpose:	This subroutine contains the main device driver logic. It is from this subroutine that all device drivers are ‘called’. This subroutine is considered a Level 2 subroutine.

#### Layout:	This subroutine consists only of ‘calls’ to device drivers such as:

##### Pump 1 (Ladder 101);

##### Pump 2 (Ladder 102);

##### Valve 1 (Ladder 121); and,

##### Valve 2 (Ladder 122).

### LAD21	Duty Alternation

#### Description:	DUTY_ALT

#### Purpose:	This subroutine is dedicated to the automatic alternation and sequencing of devices that are part of duty tables or arrangements. No other subroutines are called from this program. This subroutine is considered a Level 3 subroutine.

#### Layout:	This subroutine provides automatic alternations of duty pumps based on scheduled sequencing or in the event of equipment failures.

### LAD22	Duty Assignment Mapping to Virtual Points

#### Description:	DUTY_IN

#### Purpose:	This subroutine is dedicated to the mapping of actual pump (or valve) control mode, status, fail status to virtual duty pump control mode, status and fail status bits. The DUTY_ACP uses only virtual duty pump bits for start/stop or open/close evaluations. This subroutine is basically the ‘set up’ subroutine for the ‘true’ ACP. No other subroutines are called from this program. This subroutine is considered a Level 3 subroutine.

#### Layout:	This subroutine relies heavily on comparison utilities such as the ‘EQUAL’ module to assign duty status values. For example, if Low Lift Pump 2 is designated as Duty Pump 1 this subroutine will use a rung to energize the Duty Pump 1 status bit, provided that Low Lift Pump 2 status is on (1).

### LAD23	Duty Assignment Mapping to Equipment Points

#### Description:	DUTY_OUT

#### Purpose:	This subroutine is dedicated to the mapping of actual duty pump (or valve) requests such as start/stop (or open/close) to the actual device start/stop (or open/close) device driver. This subroutine is used to absorb requests from the DUTY_ACP and direct the requests to the proper devices. No other subroutines are called from this logic. This subroutine is considered a Level 3 subroutine.

#### Layout:	This subroutine relies heavily on comparison utilities such as the ‘EQUAL’ module to assign the results of DUTY_ACP to a ‘true’ device. For example, if the duty program requires that Duty Pump 1 be started this subroutine will use a rung to energize the Low Lift Pump 2 start request.

### LAD24	Automatic Control of Duty Equipment

#### Description:	DUTY_ACP

#### Purpose:	This subroutine is dedicated to the automatic starting and stopping, opening and closing, speed setpoints, and valve position of devices by performing evaluations using field instruments, timers or other methods described by process narratives. Normally no other subroutines are called from this logic. This subroutine is considered a Level 3 subroutine.

#### Layout:	This subroutine relies heavily on comparison utilities such as the ‘EQU’, ‘NEQ’, ‘GRT’, as well as ‘PID’ modules to automatically control field equipment. In situations where groups of devices are dedicated to sub-process areas the logic in this subroutine is aimed specifically at DUTY pumps (or valves) and as a result relies on the DUTY_IN, DUTY_OUT and DUTY_ALT subroutines for pre-processing. In addition to the comparison modules identified above this subroutine makes extensive use of timer modules for debouncing.

### LAD 41 Program for Dialer Channels

#### Description:	ALARM

#### Purpose:  The program for Dialer Channels is used to collect all alarms for the PLC which are required to trigger an Autodialer alarm.

#### Layout:	The base load contains six rungs of logic.  Rung 0 is used as a place holder rung for the comment.  The first rung is an example of sites using a single general alarm for the whole plant.  Rungs 2 -5 are examples of the North Water alarming by groups.

#### Programmers are required to contact Halton Region for clarification on how to setup this subroutine.

#### Programmers are required to modify the plant Autodialer PLC to interface with the project they are developing.  Programmers are required to contact Halton Region for direction on how to modify the plant Autodialer PLC.

## Standard SLC Software Modules

### Device Drivers

#### Halton Region has standardized software modules.  These standard modules have been defined as “Device Drivers.”  Halton Region has three (3) device drivers – pump, valve, and analog device.  The standard modules are used in all software development which involves a pump or valve which must be controlled through the PLC/HMI, and/or an analog device which is monitored through the SCADA system.

##### A Pump Device Driver is used for All Motor devices, such as pumps, mixers and conveyors.

##### A Valve Device Driver is used for All valve type devices, such as valves and gates.

##### An Analog Device Driver is used for all Analog Inputs.  This includes spares.

### Pump and Valve Device Drivers

#### The standard pump device drivers are located within the standard PLC program layout beginning at LAD101. The concept of this driver is to create a standard module that reduces programming and commissioning time.   The standard driver can be used for each pump within the program and contains the following basic features.

##### Minimum time between starts and stops;

##### Ability to change between PLT-MAN and PLT-AUTO;

##### Start and Stop Evaluations with critical safety interlocks;

##### Used for pumps with maintained run contact or separate start/stop contacts, and includes a speed deviation alarm for use with VFD’s or analog pumps;

##### Includes virtual pump faults, including Fail to Start/Stop and Uncommanded Start/Stop, and one general failure status with HMI alarm acknowledge;

##### Track number of starts for Total, Daily, and,

##### Includes Runtime, Hours and 1/10 Hours and Runtime Reset function.

#### The standard valve driver works in much of the same way and has similar features:

##### Minimum time between open and close conditions;

##### Ability to switch between PLT-MAN and PLT-AUTO;

##### Open and Close Evaluations with critical safety interlocks;

#### Used for valves with maintained open or separate open/close contacts and includes a position deviation alarm for modulating valves.

#### Includes virtual valve faults, including Fail to Open/Close and Uncommanded Open/Close and one general failure status with HMI alarm acknowledge.

### Standard Layout of SLC Pump Device Drivers

#### The device driver (program file) consists of standard logic for a single device that is connected to the PLC.  Each rung is identified in the following table –indicating the purpose of the rung.  The standard driver is included as part of the “Base” load.

| Rung | Description |
| --- | --- |
| 00 | Minimum On and Off Timers |
| 01 | Hardwired Alarms |
| 02 | Mode Determination |
| 03 | Stop Evaluation |
| 04 | Stop Timer |
| 05 | Start Evaluation |
| 06 | Start Timer |
| 07 | Requests for Control |
| 08 | Maintained Run Device |
| 09 | Fail to Start |
| 10 | Fail to Stop |
| 11 | Uncommanded Start |
| 12 | Uncommanded Stop |
| 13 | General Pump Failure Evaluation |
| 14 | Fail Test – Initial Evaluation |
| 15 | Fail to Start - Initial Evaluation |
| 16 | Fail to Stop - Initial Evaluation |
| 17 | Uncommanded Start – Initial Evaluation |
| 18 | Uncommanded Stop – Initial Evaluation |
| 19 | Fail Timer Evaluation |
| 20 | Pump Starts - Counter |
| 21 | Pump Starts – Counter Resets |
| 22 | Last Scan Status Assignments |
| 23 | Device Runtime Logic |
| 24 | Runtime Reset – Counter 2 |
| 25 | Runtime Timer Resets |
| 26 | Runtime Reset – Counter 1 |
| 27 | Device Runtime and Pump Start Logic |
| 28 | Runtime Reset Request |
| 29 | Speed Setpoint Assignment |
| 30 | Speed Setpoint Range Confirmation |
| 31 | Deviation Alarm – Max./Min. Evaluations |
| 32 | Deviation Alarm – Temporary Evaluation |
| 33 | Deviation Alarm |

- Pump Device Driver Standard Logic

### Standard Layout of Valve Device Drivers

#### The device driver (program file) consists of standard logic for a single device that is connected to the PLC. Each rung is identified in the following table –indicating the purpose of the rung.  The standard driver is included as part of the “Base” load.

| Rung | Description |
| --- | --- |
| 00 | Minimum Opened and Closed Timers |
| 01 | Mode Determination |
| 02 | Close Evaluations |
| 03 | Close Request |
| 04 | Open Evaluations |
| 05 | Open Requests |
| 06 | Maintained Contact Valve |
| 07 | Open & Close Request Resets |
| 08 | Fail To Open |
| 09 | Fail to Close |
| 10 | Uncommanded Open |
| 11 | Uncommanded Close |
| 12 | Fail Evaluation |
| 13 | Fail Test Evaluation |
| 14 | Fail to Open- Initial Evaluation |
| 15 | Fail to Close- Initial Evaluation |
| 16 | Uncommanded Open- Initial Evaluation |
| 17 | Uncommanded Close- Initial Evaluation |
| 18 | Last Scan Status Assignments |
| 19 | Fail Timer |
| 20 | Acknowledge Request Reset |
| 21 | Valve Position Assignment |
| 22 | Valve Position Range Confirmation |
| 23 | Deviation Alarm – Max./Min. Evaluation |
| 24 | Deviation Alarm – Temporary Evaluation |
| 25 | Deviation Alarm |

- Valve Device Driver Standard Logic

### SLC Analog Device Driver

#### The standard analog modules are in the standard PLC program layout beginning at ladder 61. The concept of the driver is to create a standard module that reduces programming and commissioning time. An Analog Input module is created for each AI point available based on the PLC cards. The software module has some basic features.

##### Signal Validation to determine if transmitter has a signal out of range.  A signal is considered out of range when it is no longer within the 4 – 20mA range +/- 2.5%;

##### Device readings can be disabled for the HMI, when transmitter is out of range;

##### Conversion of raw input value into scaled engineering units;

##### Allows simulation of analog values;

##### Provides clamping for low signal range to avoid erroneous flows.  The signal is set to 0.0 when below a pre-defined low level;

##### Evaluates input signal for virtual HIHI, HI, LO, LOLO alarms;

##### Records instantaneous Minimum and Maximum values for reporting purposes; and,

##### Calculates Total Daily when applicable.

### Standard Layout of SLC Analog Module

#### The device driver (program file) consists of standard logic for a single device that is connected to the PLC. Each rung is identified in the following table – indicating the purpose of the rung.  The standard driver is included in the base load.

| Rung | Description |
| --- | --- |
| 00 | Signal Validation |
| 01 | Scan Status |
| 02 | Force Signal to Range |
| 03 | Scale Signal |
| 04 | Simulation |
| 05 | Signal Clamping |
| 06 | Signal Alarming (HIHI, HI, LO and LOLO) |
| 07 | Alarm Declaration |
| 08 | Minimum & Maximum Reset |
| 09 – 10 | Instantaneous Maximum and Minimum Values |
| 11 | Flow is sampled every scan and totalized for daily, monthly and yearly values. |
| 12 | The daily value is moved into yesterday’s total and then the totalizer is reset. |
| 13 | The monthly value is moved into last month’s total and then the totalizer is reset. |
| 14 | The yearly value is moved into last year’s total and then the totalizer is reset. |

- Analog Device Driver Standard Logic

## SLC Message Blocks

#### A Message Block is a software command used by the SLC to exchange data file information between similar processors. A message block can be used to read any one processor. Any number of message blocks can be setup to communicate to different processors.

#### Halton Region does not approve the use of Write message blocks.

#### Halton Region does not approve the use of using Channel 0 to message to other devices using the Common Interface File (N9:0).  Should the Programmer require the use of this method, they must inform Halton Region using the Standards Deviation Memo, prior to the commencement of programming.

#### The message instruction has command parameters that must be configured. These parameters are identified below.

##### Type: The type cannot be changed and always indicates Peer-to-Peer;

##### Read/Write: – indicates that the local processor (where the instruction is located) is receiving data.  Halton Region does not approve the use of Write Message Blocks.

##### Target Device: identifies the type of device from where the message instruction will read the data:

###### 500CPU when target device is SLC;

###### PLC-5 if the target device is a PLC-5 or a ControlLogix PLC.

##### Local/Remote: identifies if the message instruction is sent on the local protocol, Ethernet or to a remote device through a bridge.  ControlLogix PLC’s are set for Remote, as the SLC must bridge across the ControlLogix Chassis.

##### Control Block: is the address of the message instruction and can be any integer file. Halton Region has standardized on the N160 address range.

##### Control Block Length: is automatically set 51 to words for Channel 1. Once the address has been entered the message instruction setup screen appears (as shown below). Only information in the boxes with the white background can be entered or changed.  The following figure demonstrates the setup for SLC to SLC communications.

- MSG Instruction General Configuration

#### The following tables identify the purpose of the parameters to be entered in the message block.

### This Controller

| Parameter | Description |
| --- | --- |
| Data Table Address | Refers to the data file address where the information received will be stored, or with a write instruction, this is the address in the local processor which is to send data. Valid file types are S,B,T,C,R,N,I,O, M0, M1, F, ST and A. |
| Size in Elements | Refers to numbers of words. |
| Channel | Identifies physical channel used for message communication. Set to either 1 or 0. Channel 1 is the Ethernet port (SLC 5/05). Channel 0 refers to protocol for the RS-232 port. |
| Channel 0 | Modem communications or local operator interfaces use DF1 Master or Half Duplex Master. |
| Message Timeout | Defines how long the message will wait for a valid reply before going into error. This timer is internal to the message instruction. A timeout of 0 indicates no timer and that the message will wait indefinitely for a response. |
| Data Table Address | The data file location in target PLC where the message instruction will get the required information. |
| Ethernet IP Address | Is required when Channel 1 is selected in SLC 5/05. Enter the target processor IP address. |
| Local Node Address | Used when Channel 0 is selected. This can be entered as either a decimal or octal number. |

- Message Block Parameters

### Control Bits

##### Control bits are monitored by the control program and can be used within the software to control the message instruction or to trigger an alarm when communication fails.

| Parameter | Description |
| --- | --- |
| Ignore if Timed Out | This bit is used to remove an active message instruction from processor control; |
| To be Retried | This bit is set when no response is received after a message request. This status is for information only. |
| Awaiting Execution | Bit is set once message block has been enabled and is awaiting execution. Bit cannot be changed and is for information only. |
| Continuous Run | This bit can be set. Will allow the message block to read or write on a continual basis. |
| Error Bit | Bit is set if communication has failed. This bit can be used in the control logic to send an alarm, reset the message block etc. Information about the error is displayed on the bottom of the setup screen. |
| Message Done | After a successful transmission this bit is set to 1. |
| Message Transmitting | Bit is set once acknowledgment from target device has been received. |
| Message Enabled | Bit is set to 1 once rung conditions are true and the message block has been enabled. This bit remains set until transmission has completed and rung conditions are false. |
| Waiting for Queued Space | Once there is no room in active queue, bit is set to 1. |

- Control Bits

### Messaging for an SLC to a Logix Based Controller

#### If an SLC is required to read data from a Logix PLC, the PLC/SLC mapping must be setup in the Logix PLC.  This is accomplished from the “Logic” menu in RSLogix 5000/Studio 5000, and by selecting PLC/SLC mapping, shown below.

- PLC/SLC Message Mapping

#### Next the PLC/SLC type file needs to be mapped to the appropriate Logix tag, shown in the figure below.

- PLC/SLC Logix Tag Mapping

#### In the above example the Logix tag “A01_INT_MSG1” is mapped to PLC/SLC data register 180.  The Logix tag “MSG_ASV1_INT_1” is mapped to PLC/SLC data register 192.  The definition of B, N or F is not required, however it must be consistent between the two programs.  As an example A01_INT_MSG1 is an Integer array.  The SLC must be programmed to poll N180.

#### After the MSG read instruction is complete, all individual data points from the controller-scoped arrays must be mapped from their array into their corresponding device UDT members. The following figure shows a MSG read instruction and two mapping rungs within the Main routine in the  COMMS_MSG program / task.

- MSG Read Instruction and Controller-scoped Array Map

#### When configuring the message instruction, the MultiHop box must be selected as yes (shown below).

- General Configuration MultiHop Selection

#### Selecting MultiHop will bring up the MultiHop sub tab, shown beside the General tab.  MultiHop parameters instruct the SLC that the message instruction must “hop” past the Ethernet card to retrieve the correct information.  The MultiHop configuration window is shown below.

- MultiHop Configuration Parameters

#### The Logix Ethernet card’s I.P. address must be entered in the “To Address” field.  Once entered the “Insert” key must be pressed to insert the “Hop” to the CPU.  When the “Insert” key is pressed, the following field is added:

- MultiHop Selection

#### The selection menu has four options

##### 1756-DHRIO or 1756-DH485

##### ControlNet Interface

##### Logix Backplane

##### Remote (HD/DH+/DH-485)

##### Halton Region only approves the use of Logix Backplane.  If the Programmer is required to select any other configuration, they must inform Halton Region using the Standards Deviation Memo.

#### Once Logix Backplane is selected, the Slot where the Logix CPU resides must be entered, shown below.

- Logix Backplane Slot Entry

#### In the above example the Logix PLC has an Ethernet card with an I.P. address of 192.168.183.101 and the Logix CPU is installed in Slot 0.

## Configuring data to be read from a SLC to a ControlLogix PLC

#### The RSLogix 5000/Studio 5000 MSG read instruction is not able to move data from non-Logix PLC processors directly into a controller tag. Data originating from the non-Logix processor must be read in as an array, and then mapped into the appropriate array locally. The MSG instruction must save its data in a temporary controller scope array first. The programmer must create one of three types of arrays for each MSG read instruction from a non-Logix PLC processor. Each array holds one data type (Boolean, Real, and Integer). The array name consists of four fragments separated by an underscore character.

##### The first fragment is the string “MSG”.

##### The second fragment is the standard PLC name (for example: BLC1 for the Burloak WTP chemical area PLC 1).

##### The third fragment is the data type of the array

##### “BOOL” indicates a single array of bits that store words of 16 bits from the source PLC.  This data comes from a “B” type register. Note that the MSG instruction is not able to place its result from an Integer type array into a Boolean array.

##### “INT” indicates an array of INTs that store integers from the source PLC.  This data comes from an “N” type register.

##### “REAL” indicates an array of 32-bit IEEE floating point registers. This data comes from an “F” type register.  This array will hold all floating point numbers read from the source PLC.

##### The fourth fragment is a number that is indexed in sequence starting at 1.  For example if the destination PLC needs to read 40 bits from a “B-File” in a SLC 505 PLC named BSC1, then the controller scoped array that will hold the 40 bits from the source PLC will be named “MSG_BSC1_BOOL_1”. The array will be of type DINT[2]. The first 40 bits will store the data read in from the source PLC, the remaining 24 are not used.

##### In applications where both BOOL and INT type data is required, Programmers should map all of the source data into an Integer array and use only one READ instruction, rather than creating separate MSG_READ instructions.

##### REAL data should not be “packed” into an INT register.

#### The following figure shows a sample list of controller scoped tags created for a MSG read instruction.

- Controller Scoped Tags for a MSG read instruction

#### All MSG read instructions from non-Logix controllers are sequenced the same way that Logix family PLC processor read instructions are sequenced.

#### The following figures illustrate the configuration settings for a non-Logix (AB SLC 505) MSG read instruction:

- Message Read Instruction Configuration Tab

##### Message Type: Select “SLC Typed Read”

##### Source Element: Enter the tag name in the source PLC

##### Number of Elements: Enter the number of elements in the source PLC tag.

##### Destination Element: Enter the tag name in the destination PLC. Make sure that the destination tag name is an array sized large enough to contain all elements from the source PLC.

##### The part to an SLC is similar, except that the Backplane and CPU address are not required.

- Message Read Instruction SLC Path Entry

##### In the above example the PLC will communicate using the BXX1 Ethernet Card “BXX1_ENET_1_1.”  The card will communicate using Port 2 which is the Ethernet port “2.”  It will communicate to the SLC at I.P. address “192.168.176.101.”

##### Cache Connections: Leave this box unchecked. When checked the PLC processor will keep the CIP connection open to the source PLC even when the read instruction is finished and is waiting for its next sequenced call.

- Message Read Instruction SLC Type Read Tag Tab

##### Name: The MSG Control tag associated with the MSG read instruction.

## SLC Standard Date File Configuration

#### The following table consists of a brief description of each data file used in a Standard Halton Region SLC program.

#### Programmers can reference this table when considering where a bit address should be located.

| Data File | Description | Usage |
| --- | --- | --- |
| O0 | Outputs | The output file is automatically created by RSLogix, and is the interface between the logic and the digital/analog output cards. |
| I1 | Inputs | The input file is automatically created by RSLogix, and is the interface between the logic and the digital/analog input cards. |
| S2 | Status | The status file contains internal registers used to display operating system parameters, including error codes. |
| B3 | Binary | The binary file is automatically created by RSLogix. The B3 file is used as general housekeeping bits in LAD12. |
| T4 | Timers | The timer file is used in LAD2 (Main) and for communications in LAD11. |
| C5 | Counters | The C5 file is used as a communication counters in LAD11 (Communications). |
| R6 | Control | Control. |
| N7 | Integer | The integer file is used for analog scaling in compute blocks in LAD8 and LAD12 for virtual clock setup. |
| F8 | Floating Point | Floating Point file- Base Program uses file to show current values of all analog devices. Example the first analog device at lad 61 would use F8:1. |
| N9 BT9 PLC5 | CIF (Common Interface File) | Reserved only for communications between Bristol Babcock controllers and SLC 5/05. File used for Block Transfer instructions in PLC 5 controllers. |
| F10 | PYEAR_TOT | Stores total previous year’s flow used in analog modules. |
| B11 | DI RAW | The B11 file is used in LAD 10 and is the address used for storing the I.1 file (new digital inputs). B11 is the mapped register for the raw digital inputs. |
| B12 | DI NC ENBL | The B12 file is used in LAD10. Can be used for simulation of digital inputs. |
| B13 | DI OUT SIM | The B13 binary file is used in LAD7, (digital outputs). |
| B14 | DI STS | The B14 binary file is used in ladder 10. They are used to represent alarm status or other information not represented in device drivers. |
| B15 | SUBR ENBL | Binary file used in all the subroutine ladders to enable/disable subroutine calls. |
| N22 | SCALE | Contains numbers used in Analog Modules for scaling purposes. |
| F30 | CUR MA | Used to store current analog device span as milliamp value in analog device drivers. |
| F31 | TOTL TMP | Stores temporary totalizer value for analog module. |
| F32 | TOTL TMP2 | Used as temporary register for flow totalizing in the analog module. Added with F31 registers. |
| F33 | DAY TOTAL | Stores the daily flow totals calculated in the analog modules. |
| F34 | YDAY TOTL | Stores total flow yesterday used in analog modules. |
| F35 | MON TOTL | Stores monthly total flow used in analog modules. |
| F36 | PMON TOTL | Stores total previous month’s flow used in analog modules. |
| F37 | PERCENT | Used to display analog input span from analog module as a percentage value. |
| F39 | FLOW CALC | Flow calculation values. Used in analog module to perform conversion to m3. |
| F40 N40 | DEV SP | Used in automatic control programs when a device setpoint is needed. Then mapped to LAD8 analog output compute block, ex. Pump speed output setpoint. |
| F41 | AI CUR TMP | Analog pump or valve feedback temporary value |
| N101 | DI STS | Used for digital status information such as pump running, valve opened. |
| N102 | DI ALM | Virtual digital alarms for device drivers such as Fail to Start. |
| N103 | DI MODE | Used to display mode status, PLT-AUTO, PLT-MAN, of current device. |
| N104 | DI MISC | Digital miscellaneous bits used for virtual alarm enabling, virtual alarm evaluations. |
| N105 | RTIME HRS | Device total runtime in hours. |
| N106 | RTIME 1/10 | Device runtime in 1/10 of hours. |
| N107 | TOTL ST | Total number of starts of pump. |
| N108 | DAY START | Total number of daily starts of pump. |
| N109 | MONTH ST | Total number of monthly starts of pump. |
| N111 | AI STS | Analog virtual alarm status, such as HIHI,HI etc. |
| N112 | AI RAW | Analog input raw value- unscaled. |
| N114 | AI TMP | Analog input raw value temporary register-unscaled. |
| F115 | DAILY MIN | Used to record daily minimum values. |
| F116 | DAY MAX | Records daily maximum values in analog drivers. |
| F117 | DAY MIN | Records yesterday daily minimum value. Used for trending purposes in HMI. |
| F118 | YDAY MAX | Used to keep track of yesterday daily maximum value. Used for trending in HMI. |
| T121 | START TMR | Device start timer- LAD101. |
| T122 | STOP TMR | Device stop timer- LAD101. |
| T123 | FAIL TMR | Virtual alarms device fail timer. |
| T124 | MNON TMR | Device minimum on timer. |
| T125 | MINOF TMR | Device minimum off timer. |
| T126 | RTIME TMR | Records runtime of pumps in 3600 second. |
| T131 | HIHI TMR | De-bounce timer for Analog HIHI alarms. |
| T132 | HI TMR | De-bounce timer for Analog HI alarms. |
| T133 | LO TMR | Analog alarm LO de-bounce timer. |
| T134 | LOLO TMR | LOLO analog alarm de-bounce timer. |
| T136 | CALB TMR | Calibration timer values. |
| C141 | RTIME HRS | Device runtime hour counter LAD101. |
| C142 | RTIME 1/10 | Device runtime 1/10 hour counter LAD101. |
| C143 | TOTL ST | Total starts of pump counter. |
| C144 | DAILY ST | Total daily starts of pump counter. |
| C145 | MONTH ST | Total monthly starts pump counter. |
| N151 | MAX TIME | Register to records time when maximum analog value reached. Year, month, day, hour, minute and second. |
| N152 | MIN TIME | Used to record time when minimum analog value occurred. |
| N160 | COMM BLK | Data file to hold message block addresses. |
| N170 | PID BLK | Used for PID block address. |
| N171 | PID PV | Contains PID block process variable. |
| N172 | PID CV | Contains the control variable for PID block. |
| N180-N190 | IN BOX | Used for Inbox (local data table address) registers from message instructions. |
| N191-N200 | OUT BOX | Registers are used for outbox data, when polled by other controllers or used in write message instruction. |
| N201 | PLTMAN OUT | Device driver PLT-MAN requests such as start/ stop. |
| N203 | AUTO OUT | Device driver PLT-AUTO requests such as auto start/stop. |
| F204 | PLTMAN SP | Plant Man device analog setpoint. |
| F206 | AUTO SP | Plant Auto device analog setpoint. |
| F207 | CAL DB | Calibration alarm deadband setpoint. |
| N211 | AI ENBL | Analog module virtual alarms, scan status and error enable. |
| F212 | HIHI LIMIT | Setpoint for virtual analog HIHI alarm limit. |
| F213 | HI LIMIT | Virtual analog HI alarm limit. |
| F214 | LO LIMIT | Virtual analog LO alarm limit. |
| F215 | LOLO LIMIT | LOLO alarm virtual setpoint. |
| F216 | EGU MIN | Maximum Scaling Engineering Units used in SCP instruction. |
| F217 | EGU MAX | Minimum value of scaled EGU for SCP instruction. |
| F218 | CLAMP SP | Setpoint in analog device for clamping level. |
| F219 | SIM VALUE | Setpoint value for when simulation enabled for Analog inputs. |
| F241 | CAL DB LL | Calibration alarm low limit. |
| F242 | CAL DB UL | Calibration alarm upper limit. |
| F251 | TOTL TMP3 | Monthly Temporary Totalizer |
| F252 | TOTL TMP4 | Monthly Temporary Totalizer. Used for significant digits in totalizer calculation. |
| F253 | TOTL TMP5 | Yearly Temporary Totalizer |
| F254 | TOTL TMP6 | Yearly Temporary Totalizer. Used for significant digits in totalizer calculation. |
| F255 | AI_YR_TOT | Stores Yearly total flow used in analog modules. |

- Data File description

## SLC Device Driver Status Bits

#### In the following table, the ‘x’ field corresponds to the last two numbers of the device driver.  For example, in the LAD 101 pump driver ‘x’ would be ‘1’.

| Address | Pump Description | Valve Description |
| --- | --- | --- |
| N101:x/0 | Local/Remote Status Of Pump | Local/Remote |
| N101:x/1 | Running Status Of Pump |  |
| N101:x/2 |  | Opened Status |
| N101:x/3 |  | Closed Status |
| N101:x/4 | Pump Not Read |  |
| N101:x/5 | Pump Overload Status |  |
| N102:x/0 | Pump General Failure Status | Valve General Failure |
| N102:x/1 | Fail to Start Alarm | Fail to Open |
| N102:x/2 | Fail to Start | Fail to Close |
| N102:x/3 | Uncommanded Start | Uncommanded Open |
| N102:x/4 | Uncommanded Stop | Uncommanded Close |
| N102:x/8 | Calibration Alarm | Calibration Alarm |
| N103:x/1 | Plant Manual Status | Plant Manual Status |
| N103:x/2 | Auto Mode Status | Auto Mode Status |
| N104:x/0 | Start Request | Open Request |
| N104:x/1 | Stop Request | Close Request |
| N104:x/2 | Maintained Run Contact | Maintained Open Contact |
| N104:x/3 | Hardwired Alarm | Hardwired Alarm |
| N104:x/4 | Fail to Start Temporary Status | Fail to Open Temporary Status |
| N104:x/5 | Fail to Stop Temporary Status | Fail to Close Temporary |
| N104:x/6 | Uncommanded Start Temp | Uncommanded Open Temp |
| N104:x/7 | Uncommanded Stop Temp | Uncommanded Close Temp |
| N104:x/8 | Pump Local/Remote Status Last | Valve Local/Remote last |
| N104:x/9 | Pump Running Status Last | Valve Open Status Last |
| N104:x/10 |  | Valve Closed Status Last |
| N104:x/11 | Fail Event Test | Fail Event Test |
| N104:x/12 | Pump General Fail Temp | Valve General Fail Temp |
| N104:x/15 | Calibration Alarm Temp | Calibration Alarm Temp |
| N105:x | Pump Runtime Hours |  |
| N106:x | Pump 1/10 Runtime Hours |  |
| C141:x | Runtime Counter Hours |  |
| C142:x | Runtime 1/10 Hours Counter |  |
| T126:x | Runtime Timer |  |
| T136:x | Calibration Alarm Timer | Calibration Alarm Timer |
| N201:x/0 | PLT-MAN Start request | PLT-MAN Open request |
| N201:x/1 | PLT-MAN Stop request | PLT-MAN Close request |
| N201:x/2 | Pump Alarm Acknowledge | Valve Alarm Acknowledge |
| N201:x/3 | Pump Runtime Reset |  |
| N201:x/5 | PLT-MAN/AUTO Mode Request | PLT-MAN/AUTO Mode Request |
| N201:x/8 | Maintained Run Enable | Maintained Open Enable |
| N201:x/9 | Calibration Alarm Enable | Calibration Alarm Enable |
| N201:x/10 | Virtual Alarm Enable | Event Alarms Enable |
| N203:x/0 | PLT-AUTO Start Request | PLT-AUTO Open Request |
| N203:x/1 | PLT-AUTO Stop Request | PLT-AUTO Close Request |
| F40:x | Pump Speed Setpoint | Valve Position Setpoint |
| F41:x | Current Speed Value Temporary | Current Position Temporary |
| F204:x | PLT-MAN Speed Setpoint | PLT-MAN Valve Setpoint |
| F206:x | PLT-AUTO Speed Setpoint | PLT-AUTO Speed Setpoint |
| F207:x | Calibration Tolerance Deadband | Calibration Tolerance Deadband |
| F241:x | Calibration Alarm Lower Limit | Calibration Alarm Lower Limit |
| F242:x | Calibration Alarm Upper Limit | Calibration Alarm Upper Limit |

- Device Driver Status Bits

## SLC Analog Device Driver Assignments

#### In the following table, the ‘x’ field corresponds to the last two numbers of the device driver.  For example, in the LAD 61 analog driver ‘x’ would be ‘1’.

| Address | Description |
| --- | --- |
| N22:0 | Global value used for all analog input signals to test for valid signal between 4-20 mA. (N22:0) is the validation point at 4 mA and is equal to 3277. |
| N22:1 | Global value used for all analog input signals to test for valid signal between 4-20 mA. (N22:1) is the validation point at 20 mA and is equal to 16383. |
| N22:2 | Global value used for all analog input signals to test for valid signal between 4-20 mA.  2.5% (N22:2) is the validation point at 3.9 mA and is equal to 3000. |
| N22:3 | Global value used for all analog input signals to test for valid signal between 4-20 mA.  2.5% (N22:3) is the validation point at 20.5 mA and is equal to 16700. |
| N22:4 | Global value used for all analog 4-20mA SCP instructions for scaled minimum field and represents a signal minimum at 4 mA. (N22:4). |
| N22:5 | Global value used for all analog 4-20mA SCP instructions for scaled maximum field and represents a signal maximum at 20 mA. (N22:5). |
| N22:6 | Global value used for all analog 0-100% SCP instructions for scaled minimum field and represents a signal minimum of 0% (N22:6). |
| N22:7 | Global value used for all analog 0-100% SCP instructions for scaled maximum field and represents a signal maximum of 100% (N22:7). |
| N111:x/0 | Global status bit used for all analog input signals to indicate when raw signal is outside allowable range. |
| N111:x/1 | HIHI alarm status bit is used to indicate when the analog input is above the operator entered HIHI setpoint (F212:x). |
| N111:x/2 | HI alarm status bit is used to indicate when the analog input is above the operator entered HI setpoint (F213:x). |
| N111:x/3 | LO alarm status bit is used to indicate when the analog input is above the operator entered LO setpoint (F214:x). |
| N111:x/4 | LOLO alarm status bit is used to indicate when the analog input is above the operator entered LOLO setpoint (F215:x). |
| N111:x/5 | Indicates that the HMI is treating scaled values as valid. |
| N151:x0 | Used for time recording of max/min values. Holds year value when maximum value took place. |
| N151:x1 | Records the month at which analog value was at maximum. |
| N151:x2 | Records the day at which maximum value happened. |
| N151:x3 | Keeps track of the hour when analog hit maximum. |
| N151:x4 | Records minute value of maximum analog input. |
| N151:x5 | Used to record the second when maximum analog value happened. |
| N152:x0 | Yearly minimum value. |
| N152:x1 | Records month at which minimum occurred. |
| N152:x2 | Records day at which minimum value occurred. |
| N152:x3 | Holds hour when minimum analog value happened. |
| N152:x4 | Records minute value of minimum. |
| N152:x5 | Holds second of minimum value. |
| N211:x/9 | Analog input X flow totalizer enable. |
| N211:x/10 | Analog Max/Min recording enabled. |
| F8:x | Current value of analog input (EGU). |
| F30:x | Current value of analog input in mA. |
| F31:x | Temporary totalized value of analog input in L/sec, used for daily total. Value is totalized up to 10 counts and then reset. Only valid for flow signals. |
| F32:x | Used to hold daily running number of 10 unit counts. Only valid for flow signals. Reset at midnight. |
| F33:x | Running daily total. |
| F34:x | Analog input total yesterday. |
| F35:x | Running Monthly total. |
| F37:x | Current value of analog input in %. |
| F115:x | Minimum value of Analog X, once max/mins are enabled. |
| F116:x | Maximum value of Analog X. |
| F117:x | Yesterday minimum value of Analog X. |
| F118:x | Yesterday maximum value of Analog X. |
| F212:x | Operator entered HIHI alarm setpoint. |
| F213:x | Operator entered HI alarm setpoint. |
| F214:x | Operator entered LO alarm setpoint. |
| F215:x | Operator entered LOLO alarm setpoint. |
| F216:x | Operator entered minimum EGU value. |
| F217:x | Operator entered maximum EGU value. |
| F218:x | Setpoint for clamping value, usually set at 1% of F8:X maximum value. |
| F219:x | Simulation value setpoint when simulation is enabled. |
| N112:x | Raw analog input x- x represents analog input number. |
| N114:x | Analog input X temporary variable. Used to hold raw value after all error checking has been performed. |
| N211:x/0 | Analog input X scan enabled. |
| N211:x/1 | Analog input Simulation enable. |
| N211:x/2 | Analog error enable. Used to disable transmitter out of range signal alarm. |
| N211:x/3 | Global enable bit for all analog alarms. |
| N211:x/4 | Enable bit for HIHI alarm. |
| N211:x/5 | Enable bit for HI alarm. |
| N211:x/6 | Enable bit for LO alarm. |
| N211:x/7 | Enable bit for LOLO alarm. |
| N211:x/11 | Enable bit for clamping EGU value. |
| F251:x | Temporary totalized value of analog input in L/sec, used for monthly total. Value is totalized up to 10 counts and then reset. Only valid for flow signals. |
| F252:x | Used to hold monthly running number of 10 unit counts. Only valid for flow signals. Reset at monthly. |
| F253:x | Temporary totalized value of analog input in L/sec, used for yearly total. Value is totalized up to 10 counts and then reset. Only valid for flow signals. |
| F254:x | Used to hold yearly running number of 10 unit counts. Only valid for flow signals. Reset yearly. |
| F255:x | Running Yearly total. |

- Analog Device Driver Assignments