Regional Municipality of Halton

SCADA Standards Manual

Section 5 PLC Hardware & Programming

SCADA STANDARDS 2022

Table of Contents

SECTION 5 PLCPLC Hardware & Programming	1

5.1	Overall Guidelines	1

5.2	Specific Hardware Design Standards	1

Allen Bradley Communications Networks	1

5.3	Logix Platform Selection	2

5.4	ControlLogix Hardware Selection	3

5.5	PanelView HMI	4

5.6	Autodialer	4

5.7	Legacy SCADA Hardware	4

5.8	ControlLogix Hardware Configuration	4

General	5

Major Faults	6

Minor Faults	6

Date / Time	6

Advanced	8

Security	8

SFC Execution	9

Project	9

Capacity	9

Nonvolatile Memory	9

Internet Protocol and Port Configuration	9

ControlLogix Ethernet Card Configuration	10

ControlLogix I/O Cards	18

Digital Input Card Configuration	18

Digital Output Cards	21

Analog Input Cards	24

Analog Output Cards	28

Rockwell 5000 Series Power Monitors	31

General Programming Requirements	34

Software Documentation	34

General Programming Concepts	35

Program Naming Convention	36

Security	36

Backup / Record Keeping	37

Alarming	37

5.9	Specific Programming Requirements	38

5.10	Standard Logix Project Configuration Parameters	39

Logix 5000 Standard Project Tagging Structure	39

Scope	39

Tagname	39

Data Type	40

Predefined Data Types	40

Strings	40

Module Defined Data Types	40

User Defined Data Type	40

Description	41

5.11	Device Types	41

Field Device Type	41

System Device Type	41

Process Device Type	41

Device UDTs	41

System Device UDT	42

Process Device UDT	42

Other UDTs	43

Device Drivers	43

SCADA UDTs	44

5.12	Standard Project Folder Structure	44

Tasks	44

Programs	45

Routines	45

5.13	Main Program	45

GEN_HK	45

Heartbeat	45

Security	46

S1_S2_S33_Processor_Status	46

S5_Minor_Faults	46

5.14	Inputs Program	46

Digital Input Map	46

Analog Input Map	47

Digital Input Evaluation	47

5.15	Device Program	48

5.16	ACP Program	49

Duty Alternations	49

Duty Out	49

Duty In	50

Duty ACP	50

Device ACP	50

Security	50

Alarm Dialer Interface	50

Process UDT	50

5.17	Outputs Program	51

DO_EVAL	51

AO	52

5.18	Function Block Diagram	52

PIDE Program	53

Moving Average	54

5.19	COMMS_MSG Program	54

Inter-PAC/PLC Communications	54

Destination Registers	55

Logix Family Processors	55

Non-Logix Family Processors	57

5.20	HISTORIAN Program	57

5.21	Application Specific Programming Examples	59

Critical Alarm Reminder Sample Source Code	59

Autodialer Verification System Sample Source Code	59

5.22	Working Alone System – Waste Water	60

Auto Dialer Programming	60

List of Tables

Table 5.1	ControlLogix Hardware Selection	4

Table 5.2	Input Signal to User Counts for a 1756-IF8IH module (ControlLogix)	47

Table 5.3	List of user data types for common devices	48

Table 5.4	List of UDTs used to support device programming	48

Table 5.5	Output Signal to User Counts for a 1756-OF8IH module (ControlLogix)	52

Table 5.6	PIDE Ladder Diagram Rung Functions	54

List of Figures

Figure 5.1	ControlLogix Controller Properties Selection	5

Figure 5.2	ControlLogix Controller Properties – General Tab	5

Figure 5.3	ControlLogix Controller Properties - Date / Time Tab	7

Figure 5.4	ControlLogix Controller Properties - Advanced Tab	8

Figure 5.5	ControlLogix Controller Properties - SFC Execution Tab	9

Figure 5.6	Adding a New 1756-EN2T/A Module	10

Figure 5.7	Selecting the Ethernet Card	10

Figure 5.8	1756-EN2T/A General Configuration	11

Figure 5.9	1756-EN2T Connection Tab	12

Figure 5.10	1756-EN2T RSNetWorx Tab	12

Figure 5.11	EN2T Port Configuration Tab (offline)	13

Figure 5.12	RSLinx Ethernet Configuration	14

Figure 5.13	1756-EN2T Port Configuration Tab (on-line)	15

Figure 5.14	1756-EN2TR Slot 2 General Configuration	16

Figure 5.15	1756-EN2TR Slot 3 General Configuration	17

Figure 5.16	Device Level Ring I/O Configuration	17

Figure 5.17	Adding a New Module 1756-IA16I Module	18

Figure 5.18	Selecting the 1756-IA16I Card	18

Figure 5.19	Selecting the Major Revision Number for the 1756-IA16I Card	19

Figure 5.20	1756-IA16I New Module Configuration	19

Figure 5.21	1756-IA16I Module Connection Tab	20

Figure 5.22	1756-IA16I Configuration Tab	20

Figure 5.23	Adding a New 1756-OA16I Module	21

Figure 5.24	Selecting the 1756-OA16I Card	21

Figure 5.25	Selecting the Major Revision Number for the 1756-OA16I Card	22

Figure 5.26	1756-OA16I New Module Configuration	22

Figure 5.27	1756-OA16I Connection Tab	23

Figure 5.28	1756-OA16I Module Configuration Tab	23

Figure 5.29	Adding a New 1756-IF6I Module	24

Figure 5.30	Selecting the 1756-IF8IH Card	24

Figure 5.31	1756-IF8IH Module Configuration	25

Figure 5.32	1756-IF8IH Connection Tab	26

Figure 5.33	1756-IF8IH Configuration Tab	27

Figure 5.34	1756-IF8IH Alarms Tab	28

Figure 5.35	Adding a New 1756-OF8IH Module	28

Figure 5.36	Selecting the 1756-OF8IH Card	29

Figure 5.37	1756-OF8IH Module Configuration	29

Figure 5.38	1756-OF8IH Connection Tab	30

Figure 5.39	1756-OF8IH Configuration Tab	31

Figure 5.40	Power Monitor New Module Configuration	32

Figure 5.41	Selecting the Power Monitor	33

Figure 5.42	Power Monitor Module Configuration	33

Figure 5.43	Device Main Task	43

Figure 5.44	Performing a Device Tag substitution within an instance of a Device Driver.	44

Figure 5.45	Rung from the "DI_Map" Subroutine	46

Figure 5.46	Rung from the "AI_Map" Subroutine	47

Figure 5.47	Discrete_Input_V1 Add-On Instruction	48

Figure 5.48	Device Subroutine JSR Instruction	49

Figure 5.49	Rung from the "DO_Eval" Subroutine	52

Figure 5.50	COMMS_MSG Task Configuration Properties	55

Figure 5.51	CIP Message Read Instruction Configuration Tab	56

Figure 5.52	CIP Message Read Instruction Communication Tab	57

Figure 5.53	Historian Task Configuration	59

Figure 5.54	Enable the Working Alone System and Start the 2 hour Timer	60

Figure 5.55	Working Alone Warning Window Timer	61

Figure 5.56	Working Alone Operator Acknowledgement Timer	61

# PLCPLC Hardware & Programming

## Overall Guidelines

#### This section must be reviewed in conjunction with the other SCADA standards.

#### Unless otherwise approved or stated by Halton Region, the Consultant shall assume that the controller hardware platform is Allen-Bradley ControlLogix PACs. It is important for the Consultant to recognize that non-Logix controllers are currently in use at various Halton facilities, primarily SLC 500 series processors.

#### The CompactLogix PLC platform is no longer accepted for new installs in Halton Region.

#### Halton Region has developed standards for Wastewater Pumping stations (See Section 9). Should the Consultant or the Programmer identify a discrepancy between those standards and these standards they should inform Halton Region.  Halton Region will review the discrepancy and provide direction on how to proceed and update the standards to eliminate the discrepancy.

#### Halton Region’s preference is to install thin clients in field applications and avoid the installation of Allen-Bradley PanelViews or other types of Operator Interface Terminals. The installation of any Allen-Bradley PanelViews or other types of Operator Interface Terminals must be approved by the Region through a Standards Deviation Memo.

## Specific Hardware Design Standards

#### The use of Master PACs should be avoided.  Every PLC should be capable of operating independent of other PLC systems.

#### Halton Region does not implement redundant controller configurations.

#### Where discrete I/O requires the use of a non-standard card due to voltage requirements and where eight or less points are required, installation of interposing relays is preferred rather than the installation of a non-standard card.  Refer to the selection tables for standard cards.

#### In applications where new I/O modules are being added to an existing PLC and the modules will be within the same PLC panel, the preference is that Consultants specify the same type of I/O modules that are currently installed within the PLC panel.

#### In applications where a new remote I/O panel is being added to an existing PLC panel, all modules specified must be chosen from the appropriate selection tables.

#### Halton Region requires 4 – 20 mA for all analog inputs and outputs.

### Allen Bradley Communications Networks

#### Halton Region Technology Services will free issue all major pieces of networking equipment, such as switches, modems, media converters, and routers.

#### All industrial network communications cards must be located in the main PLC rack within the Instrument Control Panel. The main PLC is responsible for communicating with all devices in the process area.

#### The Common Industrial Protocol (CIP) is an open application protocol that specifies how information is transferred between all Allen Bradley products.  ODVA EtherNet/IP is the preferred CIP protocol.

#### Halton Region permits the use of EtherNet/IP protocol for information applications only. These applications include the following:

##### Communication to Remote I/O Racks

##### Downloading and monitoring PLC programs

##### Making small changes online with the PAC

##### Supervisory monitoring and control via the plant SCADA system

##### Supervisory monitoring and control via OITs.

##### Supervisory connection to third-party packaged systems.

##### Peer-to-Peer data exchanged between PACs.

#### Halton Region has standardized on Remote I/O over Ethernet.  If a single Remote I/O rack is present, there must be one dedicated 1756-EN2T card in the main ControlLogix rack for the remote I/O rack. The Remote I/O rack must connect directly to the main rack. Connecting remote I/O to an Ethernet switch will not be accepted.

#### If two or more Remote I/O racks exist in a single process area, the configuration requires a Device Level Ring (DLR) network architecture. The Ethernet cable for this network will be orange for distinction. One (1) dedicated 1756-EN2TR card will be used in the main ControlLogix rack, which will be designated the Supervisor Node and must be configured prior to completing ring network connections. The remaining remote I/O racks will have their own 1756-EN2TR card connected in a loop to the previous rack. The final remote I/O rack will connect directly to the main rack using the second port on the 1756-EN2TR card. The Design Contractor must only use a single DLR in each process area and must consider the length of each copper network run to ensure it remains within traditional Ethernet design tolerances.

#### The Consultant and the Programmer must be aware of the limited number of connections (CIP and TCP) supported by the Ethernet Cards or the ControlLogix PAC. Additional cards must be specified when the expected number of connections to the card or controller at design time will exceed 80% of the total number of connections supported by that card or controller.

#### The EtherNet/IP protocol shall not be used for real-time control applications.  Examples include VFD drive control.

#### The serial/USB port must be left available for use by support personnel in the field for local monitoring / control purposes.  However, PLC Processors assigned to a Verbatim Autodialer use the serial port to exchange information with the Autodialer.  This is the only exception accepted by Halton Region.

#### The Consultant shall not specify Prosoft communications cards as part of a new design. Prosoft modules can only be specified to interface to field devices already in place that cannot use EtherNet/IP communications networks. Halton Region uses Prosoft Technologies INRAX Third-party communications cards to interface to these existing systems.

## Logix Platform Selection

#### ControlLogix processors are available in many sizes.  It is the responsibility of the Consultant to select and properly size the processor as per Halton Region’s selection criteria.

#### If a vendor wishes to use a CompactLogix PLC in their design, they must submit a standards deviation memo justifying their decision.  If approved, the vendor is expected to supply enough spare parts to allow for a full replacement of the PLC rack.  If the design will require more than one CompactLogix rack the vendor should strongly consider the use of the ControlLogix platform instead.

## ControlLogix Hardware Selection

#### Consultants must use the following table when specifying ControlLogix hardware.

#### Each ControlLogix I/O module requires a removable terminal block (RTB).  RTBs and are not included with the I/O modules and must be specified with the module.

#### Consultants are required to specify the use of the latest hardware version.

| Processor Selection |  |  |
| --- | --- | --- |
| Model | Memory | Application |
| 1756-L82E | 5MB | All remote stations. All WTP / WWTP process with one rack (17 slot maximum) including spare slots. |
| 1756-L83E or 1756-L84E | 10MB 20MB | All WTP / WWTP process areas with two or more racks (local or remote). |
| Power Supply and Chassis Selection |  |  |
| Description | Module | Notes |
| Power Supply | 1756-PA75 |  |
| Chassis | 1756-A7, 1756-A10, 1756-A13, 1756-A17 | Avoid the use of 1756-A4. |
| Communication Module Selection |  |  |
| Description | Module | Notes |
| ControlLogix Ethernet Module | 1756-EN2T | Only for systems with a remote rack. |
| ControlLogix Ethernet Module | 1756-EN2TR | For Remote IO DLR configurations |
| Digital Input Module Selection |  |  |
| Description | Module | Notes |
| 1756-IA16I | 16 individually isolated 120 VAC digital inputs | All Digital Inputs |
| 1756-TBCH | Removable Terminal Block | One required per module |
| Digital Output Module Selection |  |  |
| Description | Module | Notes |
| 1756-OA16I | 16 individually isolated 120 VAC digital outputs | All Digital Outputs |
| 1756-TBCH | Removable Terminal Block | One required per module |
| Analog Input Module Selection |  |  |
| Description | Module | Notes |
| 1756-IF8IH | 8 Channel HART Analog Input | All analog inputs. No alternatives will be accepted. |
| 1756-TBNH | Removable Terminal Block | One required per module |
| ControlLogix Analog Input Module Selection |  |  |
| Description | Module | Notes |
| 1756-OF8IH | 8 Channel HART Analog Output | All analog outputs. No alternatives will be accepted. |
| 1756-TBNH | Removable Terminal Block | One required per module |
| Slot Filler Modules |  |  |
| Description | Module | Notes |
| Slot Filler | 1756-N2 | All spare slots must contain a slot filler module. |

- ControlLogix Hardware Selection

#### The Consultant must consider the memory requirements of the PLC program when specifying a ControlLogix processor. For instance, a small process area with a large number of critical analog tags might require the L83E CPU. If the result from the processor selection criteria does not provide enough memory, the Consultant must inform Halton Region, and request to select a larger memory PAC. The Consultant must take into consideration all provisions to ensure that adequate memory is available for current and future programming needs. Any foreseeable future requirements must be considered a current requirement when applying Halton Region’s PLC processor selection criteria.

## PanelView HMI

#### Halton Region's preference is not to install local Operator Interface Terminals.  When Consultant's deem the installation of the terminal is required, they should contact Halton Region through the use of the Standards Deviation Memo.

## Autodialer

#### Halton Region uses the Raco Verbatim Gateway (model number 325VPLC- 4C-96AB) for remote annunciation of alarms in each plant.

#### Autodialers are not used in remote stations.

#### No alternative Autodialer Models will be accepted.

#### Consultants should contact Halton Region to determine the installation location of the Autodialer.

#### The Instrument Control Panel with the Autodialer will have a ControlLogix processor in the main rack, which will be dedicated for the functionality of the Autodialer.

## Legacy SCADA Hardware

#### Reference specifications for CompactLogix systems are documented in Appendix 5A.  These are provided for informational purposes only to assist programmers who may have to modify these systems as part of a project or ongoing maintenance work.  Vendors who receive approval for using the CompactLogix platform in their design must adhere to the specifications in this Appendix.

#### Reference Specifications for SLC 500 systems are documented in Appendix 5B.  These are provided for informational purposes only to assist programmers who may have to modify these systems as part of a project or ongoing maintenance work.

## ControlLogix Hardware Configuration

#### The processor configuration can be modified in the RSLogix 5000/Studio 5000 by right clicking on the very top folder of the controller organizer labeled “Controller BXX1” and selecting “Properties”. The programmer must fill out the controller, I/O and Communications card configurations to suit the specific application.

#### All ControlLogix Processors must have the following configuration:

- ControlLogix Controller Properties Selection

### General

- ControlLogix Controller Properties – General Tab

#### Vendor: Allen-Bradley (Cannot be modified)

#### Type: Click the “Change Controller…” button to select the Logix Family PLC processor for this application.

#### Revision: The version of RSLogix 5000 programming software used to program this application.  Programming revision is to be confirmed with Halton Region before starting any work.

#### Name: This is the name of the PLC processor.  See “” for details on creating the name.

#### Description: Must contain 3 lines of text. The first line indicates the PLC location, and process area (if applicable). The second line must give a version number and date for the PLC program. The third line indicates the IP address of the PAC.

#### Chassis Type: The catalogue number, and size (in slots) of the chassis that the processor resides in

#### Slot: The slot number that the processor resides in. This is usually slot 0.

### Major Faults

#### This tab is used to list and clear major faults within the processor. There is no configuration required for this tab.

### Minor Faults

#### This tab is used to list and clear minor faults within the processor. There is no configuration required for this tab.

### Date / Time

#### This tab is used to set the controller time. After a download occurs, the programmer must ensure that the Controller’s time is accurate. This is accomplished by clicking the <Set Date, Time and Zone from Workstation’ button to set the controller’s time to that of the workstation, or by clicking the “Change Date and Time” button and manually changing the date and time.  The Time Zone must be set to (GMT – 05:00) Eastern Time and the Date and Time must be the current time in Oakville, Ontario, Canada.

- ControlLogix Controller Properties - Date / Time Tab

#### Make this controller the Coordinated System Time master: Leave this box un-checked.

#### Make sure that the ‘Adjust for Daylight Saving (+01:00) checkbox is checked. This will automatically adjust the controller for Daylight Savings Time.

### Advanced

- ControlLogix Controller Properties - Advanced Tab

#### Controller Fault Handler: Leave this selection as is (Fault_Routine). This tells the PLC processor to execute the built in event task upon detection of a processor fault.

#### Match Project to Controller: This feature is used to mate a Logix PLC program to one unique PLC processor. Check this box, and make sure that the processor serial number matches the serial number of the destination PLC processor in the field.

#### Allow Consumed Tags to Use RPI Provided by Producer – leave unchecked.

#### Report Overflow Faults – leave unchecked.

### Security

#### Security: Leave this section as is. Halton Region SCADA staff will set-up the security features after the PLC program has been accepted.

### SFC Execution

- ControlLogix Controller Properties - SFC Execution Tab

#### The default configuration is the standard configuration for ControlLogix processors within Halton Region. The default settings are shown above.

### Project

#### Displays the PLC processor name and program file location. There is no configuration of this tab required.

### Capacity

#### Used to display and estimate PLC program memory usage. No configuration is required.

#### The User Memory contains the current working project in the PLC and all data needed to execute the project. In the event of a power failure, the contents of User Memory are held in place by a high discharge capacitor.

### Nonvolatile Memory

#### Halton Region does not use Nonvolatile memory for program or firmware storage.

### Internet Protocol and Port Configuration

#### These panels display the IP configuration and status for the controller when online.   The IP Address must be configured via RSLinx through USB or a secondary Ethernet Path, if available.  All IPs are to be manually configured and settings will be provided by Halton Region.  Refer to the details in the EN2T/EN2TR configuration section on configuring an IP address via RSLinx.

### ControlLogix Ethernet Card Configuration

#### The Consultant must select the latest model hardware / firmware available at the time of purchase.

#### To add the EN2T or EN2TR card to the current configuration, right click on the “I/O Configuration folder in the RSLogix 5000 project tree and select “New Module…”

- Adding a New 1756-EN2T/A Module

#### Expand the communications tree node, and select the 1756-EN2T or 1756-EN2TR card and click on the OK button.

- Selecting the Ethernet Card

#### When the “New Module” window appears, fill in the following parameters:

- 1756-EN2T/A General Configuration

##### Name: The card name will consist of three fragments. The first fragment is the PLC processor name. The second fragment is the text “EN2T”. The third fragment is an index number indicating the slot number of the card. All three fragments are separated by the underscore “_” character.

##### Description: The description contains the PLC processor name, followed by the words “PLC Ethernet Card”, and finally the rack and slot index of the card.

##### Slot: The slot number that the Ethernet card is plugged into (0 represents the first slot on the left).

##### Revision: This must match the revision number on the card installed in the rack.

##### IP Address: Enter the IP address for the installed card. Halton Region will issue an IP address to the Programmer when the card is installed.

##### Host Name: Leave this radio button un-selected.

##### Electronic Keying: Select “Compatible Keying” from the dropdown box.

#### Once all the above fields have been filled in, click on the “Connection” tab. This will open the Connections window:

- 1756-EN2T Connection Tab

##### Inhibit Module: Leave this box un-checked

##### Major Fault on Controller if Connection Fails While in Run Mode: Leave this box un-checked

- 1756-EN2T RSNetWorx Tab

#### Halton Region does not use the RSNetWorx configuration. If the Programmer sees a benefit, contact Halton Region via the Design Deviations Memo.

#### The “Module Info” tab is used for online monitoring of the EN2T card and does not require setup during installation.

- EN2T Port Configuration Tab (offline)

#### While offline with the processor, the port configuration parameters are not available.

#### The card’s IP address, gateway, and subnet mask are set using RSLinx.

##### Network Configuration Type is Static.

##### IP Address, Network Mask and Gateway are provided by the Region.

##### Primary Name Server, Secondary Name Server, Domain Name, and Host Name Are Blank.

##### Check “Auto-negotiate port speed and duplex”.

##### Hit Apply to make changes.

- RSLinx Ethernet Configuration

#### Once the address is set, the programmer must go online with the processor either using the built in USB port or Ethernet and set the Port Configuration settings on the card.  Once on-line, right click on the new EN2T card in the “I/O Configuration” folder in the project tree, and then select properties. The module properties dialog will re-appear with all of the fields in the Port Configuration tab available.  These settings must match those configured on the card using RSLinx.

- 1756-EN2T Port Configuration Tab (on-line)

#### The Device Level Ring Configuration will apply the unique IP addressed for the 1756-EN2T and EN2TR cards in process areas with more than one remote I/O rack or panel. New parameters will apply to the 1756-EN2TR card in the same rack when a second remote I/O rack or second remote panel exists in a process area. The Remote Racks on the Device Level Ring will be on an isolated IO subnet and will not be directly visible from the main SCADA network.

- 1756-EN2TR Slot 2 General Configuration

#### When three or more remote I/O racks or remote panels are present in the same process area the Ethernet cards will only be visible from the main controller and not from the entire network. The last number of the IP address will increase by one when a new remote I/O rack or remote panel is added.

- 1756-EN2TR Slot 3 General Configuration

#### The Device Level Ring configuration within the program for 2 or more remote I/O racks or remote panels will be as follows:

- Device Level Ring I/O Configuration

### ControlLogix I/O Cards

### Digital Input Card Configuration

#### A 1756-IA16I card can be added to the local rack by right clicking on the “I/O Configuration” folder in the RSLogix 5000 project tree, and selecting “New Module….”

- Adding a New Module 1756-IA16I Module

#### Expand the “Digital” tree node in the “Select Module” window. Select the 1756-IA16I card and click the “OK” button.

- Selecting the 1756-IA16I Card

#### When prompted for the major revision number, enter the latest revision number corresponding to the card installed. All 1756-IA16I cards purchased for Halton Region must be the latest major revision number. Click the “OK” button when complete.

- Selecting the Major Revision Number for the 1756-IA16I Card

#### When the “New Module” configuration window appears, enter the following information

- 1756-IA16I New Module Configuration

##### Name: The card name consists of four fragments separated by the underscore “_” character. The first fragment is the PLC name (BXX1 in this case). The second fragment is Rockwell’s card type identifier (IA16I in this case). The third and fourth fragments are the rack and slot numbers for the card.

##### Description: The description must contain the PLC Name (BXX1), the number of points on the card (16 in this case), the operating electrical voltage/current of the card (120 VAC in this case), the data format of the card (Digital/Analog Input/Output), and finally the rack and slot numbers.

##### Slot: Enter the slot number for the input card.

##### Comm Format: Select the “Input Data” option.

##### Revision: Enter the minor revision number for this card. Note that the major revision cannot be modified, as the major revision is set in the previous window.

##### Electronic Keying: Select the “Compatible Keying” option.

##### Open Module Properties: Leave this box checked.

#### Click on the “OK” button when finished. This will automatically open the “Module Properties configuration window. Enter the following information in all configuration tabs:

- 1756-IA16I Module Connection Tab

##### Requested Packet Interval, set this box at 10.0 ms.

##### Inhibit Module: Leave this box un-checked

##### Major Fault on Controller If Connection Fails While in Run Mode: Leave this box un-checked

- 1756-IA16I Configuration Tab

#### Leave all default options as is for this tab. All changes of state must be enabled, and the input filter times must be left at 1ms for “Off -> On” and 9 ms for “On -> Off”.

#### The General tab shows all information entered during the “New Module Configuration” window. All settings should be left as is.

#### The “Module Info” and “Backplane” tabs show real-time status information for the card while online with the PAC. No configuration is required for these tabs.

### Digital Output Cards

#### Digital Output Card Configuration

##### A1756-OA16I card can be added to the local rack by right clicking on the “I/O Configuration” folder in the RSLogix 5000 project tree, and selecting “New Module….”

- Adding a New 1756-OA16I Module

##### Expand the “Digital” tree node in the “Select Module” window. Select the 1756-OA16I card and click the “OK” button.

- Selecting the 1756-OA16I Card

#### When prompted for the major revision number, enter the latest revision number corresponding to the card installed. All 1756-OA16I cards purchased for Halton Region must be the latest major revision number. Click the “OK” button when complete.

- Selecting the Major Revision Number for the 1756-OA16I Card

#### When the “New Module” configuration window appears, enter the following information

- 1756-OA16I New Module Configuration

##### Name: The card name consists of four fragments separated by the underscore “_” character. The first fragment is the PLC name (BXX1 in this case). The second fragment is Rockwell’s card type identifier (OA16I in this case). The third and fourth fragments are the rack and slot numbers for the card.

##### Description: The description must contain the PLC Name (BXX1), the number of points on the card (16 in this case), the operating electrical voltage/current of the card (120 VAC in this case), the data format of the card (Digital/Analog Input/Output), and finally the rack and slot numbers.

##### Slot: Enter the slot number for the card.

##### Comm Format: Select the “Output Data” option.

##### Revision: Enter the minor revision number for this card. Note that the major revision cannot be modified, as the major revision is set in the previous window.

##### Electronic Keying: Select the “Compatible Keying” option.

##### Open Module Properties: Leave this box checked.

#### Click on the “OK” button when finished. This will automatically open the “Module Properties configuration window. Enter the following information in all configuration tabs:

- 1756-OA16I Connection Tab

##### Requested Packet Interval set this box at 10.0 ms.

##### Inhibit Module: Leave this box un-checked

##### Major Fault on Controller If Connection Fails While in Run Mode: Leave this box un-checked

- 1756-OA16I Module Configuration Tab

#### Leave all default options as is for this tab. In Program or Fault state, all outputs must default to the off state.

#### The General tab shows all information entered during the “New Module Configuration” window. All settings should be left as is.

#### The “Module Info” and “Backplane” tabs show real-time status information for the card while online with the PAC. No configuration is required for these tabs.

### Analog Input Cards

#### A 1756-IF8IH card can be added to the local rack by right clicking on the “I/O Configuration” folder in the RSLogix 5000 project tree, and selecting “New Module…”

- Adding a New 1756-IF6I Module

#### Expand the “Analog” tree node in the “Select Module” window. Select the 1756-IF8IH card and click the “OK” button.

- Selecting the 1756-IF8IH Card

#### When the “New Module” configuration window appears, enter the following information

- 1756-IF8IH Module Configuration

##### Name: The card name consists of four fragments separated by the underscore “_” character. The first fragment is the PLC name (BXX1 in this case). The second fragment is Rockwell’s card type identifier (IF8IH in this case). The third and fourth fragments are the rack and slot numbers for the card.

##### Description: The description must contain the PLC Name (BXX1), the number of points on the card (8 in this case), the operating electrical voltage/current of the card (4-20 mA in this case), the data format of the card (Digital/Analog Input/Output), and finally the rack and slot numbers.

##### Slot: Select the slot number for the card.

##### Click on the “Change” button under Module Definition and Select “Analog and HART by Channel” from the Input Data Dropdown.  Change the series and firmware revision for the card if necessary.

#### Enter the following information in all configuration tabs:

- 1756-IF8IH Connection Tab

##### Requested Packet Interval:  Leave this box at 100 ms (default).

##### Inhibit Module: Leave this box un-checked

##### Major Fault on Controller If Connection Fails While in Run Mode: Leave this box un-checked

- 1756-IF8IH Configuration Tab

#### All settings on the Configuration Tab should be left at their default values.  If the Field Device is HART capable then check the “Enable Hart” checkbox to allow for HART data to be received in the PAC.

#### On the Alarms Tab, “Disable All Alarms” should be checked for all channels.

- 1756-IF8IH Alarms Tab

#### The Calibration tab allows the Engineer/Licensed Technician to fine tune each individual analog point to account for offsets generated by heat. Halton Region does not use calibration offsets on analog input cards, hence all parameters on this tab must remain at default values.

#### The General tab shows all information entered during the “New Module Configuration” window. All settings should be left as is.

#### The “Module Info” and “HART Device Info” tabs show real-time PLC card and HART Field Device information while online with the PAC. No configuration is required for these tabs.

### Analog Output Cards

#### A 1756-OF8IH card can be added to the local rack by right clicking on the “I/O Configuration” folder in the RSLogix 5000 project tree, and selecting “New Module…”

- Adding a New 1756-OF8IH Module

#### Expand the “Analog” tree node in the “Select Module” window. Select the 1756-OF8IHcard and click the “OK” button.

- Selecting the 1756-OF8IH Card

#### When the “New Module” configuration window appears, enter the following information

- 1756-OF8IH Module Configuration

##### Name: The card name consists of four fragments separated by the underscore “_” character. The first fragment is the PLC name (BXX1 in this case). The second fragment is Rockwell’s card type identifier (OF8IH in this case). The third and fourth fragments are the rack and slot numbers for the card.

##### Description: The description must contain the PLC Name (BXX1), the number of points on the card (8 in this case), the operating electrical voltage/current of the card (4-20 mA in this case), the data format of the card (Digital/Analog Input/Output), and finally the rack and slot numbers.

##### Slot: Select the slot number for the card.

##### Click on the “Change” button under Module Definition and Select “Analog and HART by Channel” from the Input Data Dropdown.  Change the series and firmware revision for the card if necessary.

#### Enter the following information in all configuration tabs:

- 1756-OF8IH Connection Tab

##### Requested Packet Interval: Leave at the default of 25ms.

##### Inhibit Module: Leave this box un-checked

##### Major Fault on Controller If Connection Fails While in Run Mode: Leave this box un-checked

- 1756-OF8IH Configuration Tab

#### On the Configuration Tab, set all channels to “Hold for Init”.  Check the “Enable Hart” check box if the Field Device is HART capable.  Leave all other values at their default setting.

#### Leave all values on the “Output State” tab at their defaults.

#### Check “Disable All Alarms” for each channel on the Limits Tab.

#### The Calibration tab allows the Engineer/Licensed Technician to fine tune each individual analog point to account for offsets generated by heat. Halton Region does not use calibration offsets on analog output cards, hence all parameters on this tab must remain at default values.

#### The General tab shows all information entered during the “New Module Configuration” window. All settings should be left as is.

#### The “Module Info” and “HART Device Info” tabs show real-time PLC card and HART Field Device information while online with the PAC. No configuration is required for these tabs.

### Rockwell 5000 Series Power Monitors

#### A Rockwell 5000 series power monitor is treated in the same manner as a remote IO rack.   The monitor can be added to the IO tree by selecting the “Ethernet” branch of the Ethernet module that will be connecting to the Power Monitor and selecting “New Module…”

- Power Monitor New Module Configuration

#### Type “1426-M5E” into the filter field.  Select the catalog number that matches the Power Monitor installed in the field and click “Create”.

#### When the new module configuration appears, enter the following information:

#### Name: Enter the name of the Power Monitor.

#### Description:  The first line of the description should be “Power Monitor”.  The second line should indicate the Motor Control Centre (MCC) or Device with which the Power Monitor is installed.  The third line should indicate the physical area or building where the Power Monitor is located.

#### IP Address: Enter the IP Address for the Power Monitor.

#### Module Definition: Click “Change” and select the Major and Minor revision of the Power Monitor firmware.  Electronic Keying should be “Compatible Module”.  “Connection” should be set to “Input Only” and Configured by “External Means”.

#### The settings on the remaining tabs should be left at their defaults.

- Selecting the Power Monitor

- Power Monitor Module Configuration

## General Programming Requirements

#### Halton Region has created standards for both the PLC and HMI development that are integrated to provide a single standardized approach to SCADA system implementation within Halton Region.

#### In order to ensure consistency between the PLC and HMI development, which may be completed by different Programmers, it is imperative that these standards be followed.  Failure to follow these standards may cause a mismatch between PLC and HMI leading to project delays.  Halton Region insists that these standards are followed by those carrying out work within Halton Region.

#### These standards are designed to be read in conjunction with Halton Region’s base load programs.  Consultants, Programmers, and OEM equipment vendors are required to contact Halton Region in writing and request a copy of the latest base load program, prior to reading these standards.

#### The standard program layout is developed using the concept of a “Base” PLC load. The base load is all the commonly required PLC logic for the operation of the unique process area or remote site, with any process area or site specific automatic logic removed.  For each subroutine or Add-on instruction a standard layout has been established to facilitate troubleshooting and modifications/additions to the logic.  Any deviation from this structure must be approved by Halton Region.

#### The Programmer must use the version of the RSLogix software that matches the firmware revision of the controller to develop a project in Halton Region. The base load project implements all standard software modules that conform to the latest version of this document. The Programmer must use the base load project as a starting point, and then customize the project for the process area that they are responsible for. The Programmer can introduce custom functions within the “ACP” subroutines. All other subroutines must contain function calls to standard add-on instructions.

#### The Programmer must remove all unused code and routines. This doesn’t extend to Data Types or Add-On Instructions in Controller Organizer as they will be needed if additional programing is done in the future.

### Software Documentation

#### Documentation of the software is extremely important to Halton Region. Effectively documented code facilitates troubleshooting and ensures the long-term support of the software. The RSLogix/Studio 5000 software allows programmers to enter a comment for each subroutine, rung and tag or address. The following lists the documentation requirements within the PLC code:

##### All SCADA Accessible tags must be assigned an appropriate tagname which is based upon Halton Regions tagname convention. Each tag must also contain a detailed description of the function of the tag.

##### Each tag shall be unique and RSLogix/Studio 5000 will not allow programmers to create duplicate tags within the same scope (controller/program). The tag can consist of any letters (A-Z), numbers (0-9) and underscores but must begin with a letter. The tag length can be up to 40 characters.

##### The tag description is used to define the operation or purpose. The name of every Device Tag Description must be the long-form extension of the standard tag name. The comment need not include the facility name / process area for tags that are in the same process area controlled by the PAC. For instance, a Device Tag named BLC_CFP1_DM within the BLC1 PLC will have the comment “Chemical Feed Pump 1 Drive Motor”

##### If the Device corresponds to another process area (i.e. tags/bits that are read using a message read instruction), then the description will contain the facility and process area text (where required). For instance, the Device Tag BSC_RSP1-DM in the BSX1 PLC will have the comment “Inlet Works Raw Sewage Pump 1 Drive Motor” (the Burlington Skyway Plant prefix is still implied).

##### Every member of a UDT must have a comment that clearly describes the function of the member. The comment for a SCADA interface UDT member must match the description from the Halton Region tagging standard. For instance, the DI_CL member of the pump UDT must have the comment “Control Mode”.

##### All other controller tags must have a comment that clearly describes the function of the tag. All System Device Tags (prefixed with the characters “SYS_”) must have a comment that starts with “SYSTEM – “.

##### All elements in an array used for peer-to-peer messaging must be commented to indicate what the value is and what target PLC that data originates in.

##### A subroutine title is used to define the purpose of the subroutine. The title rung must have a description of the purpose of the routine.  Every routine must have a title rung containing a NOP instruction.

##### Every rung must have a comment that completely describes the function of the rung. One rung comment can be used to describe several consecutive rungs, as long as the purpose of each consecutive rung is clear from the instruction on the first rung.  Rung comments are not unique and can be used in multiple rungs.  Rung comments are to be informative and provide sufficient information to facilitate troubleshooting on site.

##### All calculations must clearly document what formula is being used and the full form of the equation.  All constants are to be identified as either engineering constants (e.g. Pi), or if the constant is the result of a separate calculation (e.g. fixed dimensions of a vessel) the calculation of that constant value must be documented.

##### If a complex calculation is to be performed across multiple rungs than intermediate holding registers must be used to facilitate troubleshooting.

##### Halton Region has standardized the tags used in the PLC logic.  Standards ensure consistency between devices (pumps), valves, and analog transmitters.

### General Programming Concepts

#### Halton Region has developed a number of general programming concepts to facilitate the standard creation of programs.  The following general principles should always be practiced:

##### Use subroutines to group similar logic and avoid repetitive tasks.

##### I/O registers are only to be used once in the controller software.  The field inputs (I) and outputs (O) are mapped to/from internal registers.

##### De-bounce timers are applied to all field generated alarms.

##### Avoid using constants.  Constants should be placed in a tag and configured as a constant in the PLC tag database.

##### The use of Jumps and Labels will not be accepted

##### The use of latching coils will not be accepted.

##### The use of Message Write Instructions for Peer-to-Peer messaging will not be accepted.

##### All Tags are to be Controller Scoped.

##### Do not sacrifice the clarity or simplicity of the logic in order to minimize scan time or develop smaller programs.

##### Program indexing and indirect array addressing should not be used.

##### When using PIDE/PID instructions, the derivative factor is to be disabled.

##### Include necessary software interlocks to disable equipment operation when a hardwired field alarm occurs.

##### All spare Discrete and Analog Input points must be fully mapped to spare addresses or analog input device drivers.  Mapping should be identical to non-spare inputs.

##### Unlatching of the math overflow bit will not be accepted.  Programmers are expected to account for potential overflows from a math instruction (typically, but not always, a divide by zero error) with appropriate programming safeguards.

##### Programmers are expected to perform cleanup of any dead code resulting from the programming.  This includes any code that may be auto-generated by third party programs.  All unused subroutines, programs, tasks and tags are to be deleted from the program.  Unused UDTs and Device Driver AOIs may be left in the program to support future expansion.

### Program Naming Convention

#### The project filename at facilities with process areas use a naming convention consisting of four characters.  The first three (3) characters use fragment 1 and 2 of Halton Region’s Tagname Convention.  The fourth character is the number of the field controller at each particular site.  An example would be BWA1.  This is the first PLC in the Low Lift area at the Burlington Water Plant.

#### The project filename for existing Water Distribution facilities use a naming convention with three or four characters.  These projects have been created by Halton Region and Programmers do not need to modify them.  Programmers should contact Halton Region in writing if more information is required.

#### Halton Region will provide Programmers with the three-character project name for new Water Distribution facilities.

#### The project filename for wastewater collection facilities use a naming convention with three characters.  The three (3) characters use the fragment 1 and 2 of Halton Region’s Tagname Convention.  An example is A01, which is the Agnes Street pumping station in Acton.

#### The processor name must be set to the same name as the project.

### Security

#### Consultants, Programmers, and OEM equipment vendors shall not place software locks on any PLC program. The Consultant, Programmer, or OEM equipment vendor will write and commission the PLC program, however Halton Region is the sole owner of the program during development, commissioning, and after the final program is submitted. At any time during development, Halton Region may request a documented source copy of the program for internal review.

#### The base load programs contain Security software. This is used by Halton Region’s SCADA department to monitor:

##### Mode changes in the controller i.e. remote program to remote run or after a program download; and,

##### Anytime an online edit occurs in the controller.

#### Should any of above conditions occur an alarm will be generated.   In addition, all changes made to PLC programs are tracked by FactoryTalk AssetCentre.

### Backup / Record Keeping

#### The Programmer must obtain the latest version of the “Gatekeeper Protocol” document from Halton Region. The Programmer must follow the procedure outlined in the Gatekeeper Protocol and any related Standard Operating Procedure (SOP) documents when obtaining the latest version of a PLC program, or when submitting a new / revised PLC program.

#### Revision notes are required whenever an on-line edit or upload is made. This allows Halton Region to:

##### Monitor and Track Changes.

##### Have an update to date record on the last Programmer who modified the PLC program.

##### Provide documentation to the next Programmer informing them of all changes.

#### Revision notes are mandatory whenever code is checked back in the AssetCentre.  The programmer must provide a high-level description of the work performed.

#### In addition to providing revision notes, the programmer shall update modified rungs with their initials, the name of their firm or company, the date, and what was changed on the rung.

#### Programmers are expected to return the latest copy of the program to Halton Region at the end of the day, even if they are to continue working on the program on a following day.  Revision notes are to be provided daily when the code is returned.

#### A Revision note must be provided anytime a PLC program is downloaded.  The note must indicate that a download occurred.  PLC downloads affect flow totalizers and daily minimum and maximum averages.  This allows Halton Region to have a record of the event occurring.

### Alarming

#### Alarming is used to notify designated personnel of an alarm condition in the system. There are two (2) alarm types that are generated by the PLC logic.  These alarms are defined as “field generated alarms” which are hardwired conditions in the field, and “virtual” alarms.  Virtual alarms are generated by logic in the PLC which considers operator-initiated requests and process feedback to determine if an alarm condition is present.

##### Field generated alarms are hardwired to input points at the PAC. Examples of hardwired alarms are motor overload, high building temperature, and fire alarm. When an alarm condition occurs, the alarm is displayed at the HMI. To acknowledge the alarm, if associated with a device, the device control pop-up screen is selected at the HMI and the ‘ACK’ button is then selected from the device control pop-up.  Alternatively, the alarm can be acknowledged from the alarm summary screen.  Acknowledging the alarm will not cause the alarm condition to reset in the field, but will result in a change of the alarm notice at the HMI.  The alarm notification will remain until the alarm has reset in the field.  Once the field condition has reset, the equipment can restart.

##### Field generated alarms are monitored by the PLC and ensure certain device control interlocks are present. For example, in the pump device driver an overload alarm would cause an interlock condition and prevent a start request from executing.

#### Virtual alarms are software generated alarms created by the device drivers and analog modules.

##### An example of a device driver virtual alarm would be a Fail to Start alarm. When the alarm is acknowledged on the HMI, the alarm is only acknowledged in the SCADA system.  The alarm condition must be cleared from the device control pop-up screen at the HMI, by using the Device “Ack” button.  When the alarm is acknowledged using the device control pop-up “Ack” Button, the HMI writes an alarm acknowledge bit to the PAC, which clears the Fail to Start alarm along with any other Virtual alarms active in the device driver.

##### An example of an analog virtual alarm would be a Level HIHI alarm. When the alarm is acknowledged at the HMI, the alarm will only be acknowledged on the SCADA system.  The Level HIHI condition must be cleared in the field before the alarm will clear on SCADA.  Using the “Ack” from the analog device control pop-up acknowledges the alarm on the SCADA system.  Some virtual alarms are configurable so that they “seal” in when the alarm is triggered.  This is done to prevent a process from restarting if the alarm condition goes out of alarm before being acknowledged by the operator.  In this case the “ack” command is processed by the PLC to unseal the alarm; there is no longer an “out of alarm, unacknowledged” condition for these alarms as they cannot be removed from the alarm banner until the alarm condition has cleared and the operator has hit the acknowledge button.

## Specific Programming Requirements

#### This section must be read in conjunction with “,” which contains the common programming requirements for all Region controllers.

#### The International Electrotechnical Commission (IEC) owns and develops a set of standards for programmable controllers and automation software called the IEC-61131 standards. The Logix family of processors uses Allen-Bradley’s RSLogix 5000/Studio 5000 programming software, which complies with the IEC-61131-3 standard. The IEC-61131-3 standard provides the framework for many different types of industrial programming languages. The Programmer must be experienced and adept with the following types of languages.

#### Ladder Diagram (LD).  The Ladder Diagram programming language uses rungs, contacts, and various programming elements (timers, counters, move instructions, compute blocks, etc.) in its syntax. Halton Region uses the ladder diagram language exclusively for all input/output mapping and device drivers. Ladder Diagrams are also used within the ACP program.

#### Function Block Diagram (FBD).  The Function Block Diagram programming language uses function blocks arranged on a grid, executed according to a sequence number. Connecting network lines between the I/O pins passes variables to and from each function block. Halton Region uses FBD language in two specific applications:

##### Enhanced PID Control (PIDE): One FBD Sub-Routine contains a single instance of the PIDE function block for one device driver. All LD code within the ACP calls the corresponding Function Block Diagram Routine that contains a single PIDE instruction. When the PIDE instruction is complete, the results are passed back to the original LD Routine.

##### Moving Average (MAVE) UDT: The Moving Average (MAVE) UDT is used to calculate a time average value for an input signal- a rolling average. For example, this instruction can easily be used to provide a five-minute average flow rate, chlorine residual etc.

#### Structured Text (ST).  The Structured Text programming language resembles native programming languages such as Visual Basic or C++. The ST programming language uses a list of textual commands to perform mathematical operations, make logical decisions, repeat or loop through instructions multiple times. A Structured Text Routine can only be used to perform complex mathematical calculations that cannot fit on a single rung of LD code in a Compute (CPT) instruction. Halton Region must approve the creation of each new ST Routine. Each ST Routine must be programmed in a modular fashion so that multiple LD Routines can call the same ST Routine. The ST Routine must be written in a clear and concise manner and must be easy to debug online. The programmer cannot sacrifice clarity for efficiency. Every mathematical formula must be well documented. Large complex formulae must be broken down into several smaller operations using a temporary tag to hold the result for the next operation. The ST language shall not be used for any process control, device drivers, or system housekeeping tasks.

#### Sequential Function Chart (SFC).  Halton Region does not permit the use of the SFC language in any Logix Family PLC processor.

#### Should any extra program(s) be added to the base load, other than Main, Inputs, Device, ACP and Outputs, the programmer must notify Halton Region so that the Security sub routine can be modified.

#### Halton Region does not permit the use of Produced / Consumed tags.

#### Halton Region does not permit the use of tag name aliasing.

## Standard Logix Project Configuration Parameters

### Logix 5000 Standard Project Tagging Structure

#### In RSLogix5000, tags are created with the following main properties:

##### Scope

##### Tagname

##### Data Type

##### Description

### Scope

#### The scope of the tag defines which routines can access the data. A tag can be assigned one of two types of scope, namely, “Controller” or “Program”. If a tag’s scope is “Controller”, then it can be accessed by all of the programs and routines within the project.  If it is assigned as “Program”, then it can only be accessed by the routines within the program that the tag resides.  All RSLogix 5000/Studio 5000 applications written for Halton Region must use Controller scoped tags exclusively. Program scoped tags are not permitted anywhere in a PLC program.

### Tagname

#### Every Tag in RSLogix 5000 must have a name that is less than 40 alpha-numeric characters in length. Halton Region only allows the following characters to appear in a tag name:

##### Upper and lower case letters from the English Language alphabet (a-z, A-Z)

##### Numerical characters (0-9)

##### The underscore “_” character.

##### The dot “.” Character.

#### All tag names must start with an alphabetic character (Letter “a.” from the above list). All tags must be named in accordance with the requirements of this document. For example; device driver tags must be named according to the Halton coding standard for the particular device, and PLC system tags must start with “SYS_”.

#### UDTs used by the Region have been structured to optimize pass-through descriptions of tag comments.  However, limitations in the Logix 5000 software limit the nested levels to which a description can be passed through.  Programmers are responsible for ensuring the comment for every tag used within the ladder logic of the program accurately describes the function of the tag. For example, the default comment for the run status member of the BXX1_DEV1_DM device tag (BXX1_DEV1_DM1.DI_SS.Eng) is “Pump 1 Eng. Value”.  It must be manually modified to say “Pump 1 Run Status Eng. Value”.

### Data Type

#### An RSLogix 5000/Studio 5000 Tag uniquely identifies a memory location within the PLC processor. The type of information that can be stored in the memory location is referred to as a Data Type. Many data types are supported by Logix applications. Data types fall into one of four categories:

##### Predefined

##### Strings

##### Module Defined

##### User Defined (UDT)

### Predefined Data Types

#### The Programmer must always use the DINT data type for any integer value. The use of INT data type is only approved for messaging between Logix and SLC N type data files.

### Strings

#### The programmer shall not create or modify String data types.  Use of string data for any purpose in the PLC program must be approved by the Region.

### Module Defined Data Types

#### Module Defined data types are created by the PLC processor every time an I/O or communications card is added to the PLC backplane. These data types are created automatically by RSLogix 5000/Studio 5000, and cannot be added or modified by the user.

### User Defined Data Type

#### The User Defined data type (UDT) is a custom data type created by the user. The UDT can be thought of as a container or collection of data types referred to as members. Every member of a UDT is itself another data type, either Predefined, String (not used by Halton Region), or even another UDT. The entire collection is then identified as a single data type. When a tag is created by the user, the user must give the new tag a data type. When a tag is created and assigned a UDT as its type, memory is allocated for the base tag, and all of its corresponding members. Every member of a tag’s UDT structure is accessed using the dot “.” character.

#### Halton Region makes extensive use of UDTs when programming Logix family processors. The Programmer is expected to be familiar with the use of UDTs in RSLogix 5000/Studio 5000.

#### Halton Region has developed a series of UDTs to standardize deployment of various devices and system functions.  Each UDT has an accompanying programming guide outlining the various UDT members and AOIs used to implement the UDT function, and provide direction on common implementation methods and integration with HMI elements.

#### If a programmer believes that a piece of code being developed for a project would benefit from conversion to a UDT they should contact the Region of Halton SCADA group.

### Description

#### Tagname descriptions identify the function of the tag.  Tagname descriptions should contain a very clear text description of the function of the tag.  Any tags used in the HMI should have a description matching the PLC tag.

## Device Types

#### A Device Type represents a collection of devices that operate in a similar manner. Device Types can refer to equipment in the field, hardware on the PAC, or an entire process area in a plant.

### Field Device Type

#### A Field Device Type refers to a collection of equipment in the field that operates in an identical fashion. Examples of Field Device Types include but are not limited to:

##### Drive Motor: This represents any electro-mechanical motor that operates in a discrete manner (either on or off)

##### Variable Frequency:  This represents any electro-mechanical motor that in addition to discrete operation can have its speed modified (0-100% speed).

##### Valve: This represents a device that can regulate the rate of flow. A valve can be as large as a gate that separates two storage tanks, or as small as a ball valve in a braided hose.  The valve operates in a discrete manner (either open or closed), and can optionally have its intermediate position adjusted (0-100% open).

##### Analog Instrument: This represents a device that makes a real-time numerical measurement from the field. This includes (but is not limited to) chlorine residual analyzers, level transmitters, flow transmitters, turbidimeters, and speed / position transmitters.

### System Device Type

#### System Device types represent devices that are strictly connected to the PLC processor and the local I/O chassis. System Device Types include:

##### Analog Input: An analog input point on a local or remote I/O rack

##### Analog Output: An analog output point on a local or remote I/O rack

##### Digital Input: A digital input point on a local or remote I/O rack

##### Digital Output: A digital output point on a local or remote I/O rack

### Process Device Type

#### Process Device Types represents all information used to control a collection of Field Device Types within a process area according to a standard control philosophy. Process Device Types can be created or modified by the programmer as required. Example Process Device Types include but are not limited to:

##### Drive Motor 1 to 2: Used when verifying duty selection for a collection of 2 drive motors

##### Duty Assignment: Represents a single duty selection within a process.

### Device UDTs

#### Every Field Device Type has associated with it a Device UDT. The Device UDT represents a template data structure containing all pertinent information for the Field Device Type. The name of every Device UDT consists of five fragments separated by the underscore character.

##### The first two fragments are the string “SCADA_DEV” to indicate a SCADA Device Driver.

##### The third fragment describes actual Device Type.

##### The fourth fragment is the major version number. Major version numbers change when the corresponding Device Driver AOIs must be modified to accommodate the changes.

##### The fifth fragment is the minor version number. Minor version numbers change when a modification of the UDT type does not require any changes in the corresponding AOIs.

##### As an example, the name of the drive motor device type UDT (version 1.0) would be: “SCADA_DEV_MOTOR_1_0”

#### The programmer creates one controller scoped tag for every device type that is controlled by the PLC in the field. This controller scoped tag is called the Device Tag. The Device Tag must be named according to the Halton Region tagging standard. The data type of the Device Tag must be a Device UDT consistent with the Device Type.

#### Example: to create the drive motor for High Lift Pump 1 at the Burloak Water Treatment Plant; The programmer would create a single controller scoped tag named “BLJ_HLP1_DM1”. The data type of the controller tag would be “SCADA_DEV_MOTOR_1_0”. The version numbers correspond to the latest device type UDT version number available at the time the process area / station was programmed.

### System Device UDT

#### The System Device UDT represents a standard collection of data types used to control a System Device. The name of a System Device UDT consists of five fragments separated by the underscore character.

##### The first two fragments is the string “SCADA_SYS” which identifies it as a system device UDT.

##### The third fragment is a two letter string that identifies the system device UDT.

##### The fourth fragment is the major version number.

##### The fifth fragment is the minor version number.

##### Example: the system device UDT for a version 1.2 PLC digital input point would be: “SCADA_SYS_DI_1_2”.

### Process Device UDT

#### The Process Device UDT represents a standard collection of data types used to control a Process Device. The name of a Process Device UDT consists of 4 or 5 fragments separated by the underscore character.

##### The first two fragments are the string “SCADA_PRC” which identifies it as a system device UDT.

##### The third fragment is a 2-5 letter string that identifies the Process Device UDT.

##### The fourth optional fragment is a 2-5 letter string that further identifies the Process Device UDT.

##### The fifth fragment is the major version number.

##### The sixth fragment is the minor version number.

##### For example, the Process Device UDT for a version 1.0 Two Pump Duty Selection is:  “SCADA_PRC_PUMP_2DUTY_1_0”.

#### Process Devices are customized for each individual process area.

### Other UDTs

#### The Region may build UDTs with the expectation of incorporating them as members of more complex UDTs.

#### Any UDT not prefixed with “SCADA_” is generally a component of other UDTs and should not be used to create standalone tags within the PAC.

### Device Drivers

#### The Device Driver is a subroutine that is associated with a Device Type. The Device Driver can only manipulate data within its associated Device UDT. Subroutines within the “ACP” program manipulate data across multiple Device UDTs according to a process control narrative.

#### The continuous task called “Main_Task” contains all device drivers in a Program called “Device”. All Device Drivers are LD subroutines with an Add-on instruction within the “Device” Program. One Device Driver routine is created for every instance of a device type. Multiple instances of the same Device Type contain the exact same Add-on instruction, with all of the Device Tag prefixes modified for the specific Device Tag. The Device Driver routine must be named according to the Halton Region tagging standard. The driver routine name will hence be identical to the Device Tag name. The “Main” routine contains a collection of JSR instructions that execute each of the Device Drivers in sequence.

- Device Main Task

#### Within every instance of a Device Driver routine, the programmer can use the “Search and Replace” function (<ctrl><h>) to perform the required Device Tag substitution. The programmer should take care to ensure that the “Current Routine” option within the “Find Where” drop down box is selected; otherwise a disastrous Project-wide substitution may result.

- Performing a Device Tag substitution within an instance of a Device Driver.

#### The base load Application serves as a library of Device Drivers and Device UDTs. It is anticipated that this library will grow in size and encounter many revisions. The programmer must use the Device Drivers in the latest base load Application to interface all devices in the field. The programmer will select the Device Drivers and UDTs from the base load Application required for the process area / station under control. The final version of the PLC program need not contain all Device Drivers and UDTs, only those corresponding to the process area / station under control.

#### The programmer must notify Halton Region if a specific Device Type does not exist in the base load Application. Halton Region will determine if a change is required, and grant permission to either modify an existing Device Type or create a new Device Type.

### SCADA UDTs

#### Members of a UDT that belong to a Device Tag are referenced using the dot (.) character. Every Device UDT contains a set of tags that are provided for interfacing with the SCADA system.

#### The members of a SCADA Interface UDT are named according to fragments 5 and 6 in the Halton Region Tag Name Standard (with the character substitutions listed in the previous section).   Tags only intended for internal use are only referenced in the Device Add-On Instructions and are not explicitly mapped out of the device control AOI.

## Standard Project Folder Structure

#### RSLogix 5000/Studio 5000 projects are sub-divided into three different folders called Tasks, Programs, and Routines.

### Tasks

#### All programming, unless otherwise noted, is to take place in the Main Task (Main_Task), which is configured as a Continuous Task.

#### Periodic Tasks are not permitted, except for the following:

##### COMMS_MSG: Process MSG read instructions.

##### HISTORIAN: Log critical analog values within the corresponding FIFO buffer.

##### PIDE:  Enhanced PID subroutine

#### Event tasks are not permitted.

### Programs

#### Halton Region standard program layout uses five different Programs:

##### Main: This Program contains all Routines used to prepare the rest of the program for continuous operation.

##### Inputs: This Program maps all field Inputs from I/O card registers (Local:I.Data.0 for example) into the appropriate raw data register within a device tag.

##### Device: This Program executes all device routines once and updates the corresponding device tag member with new data.

##### ACP: This Program executes automatic control code according to the process control narratives for the applicable process area. All related device tags are updated according to the result of the ACP code.

##### Outputs: This Program maps all raw data registers within device tags to field outputs in I/O card registers (Local:O.Data.0 for example).

### Routines

#### Every Program contains one Routine called “Main”. The Main Routine contains LD code with a series of JSR blocks that call all other Routines within the Program.

## Main Program

#### The main program consists of six routines.  These are:

##### GEN_HK

##### Heartbeat

##### Security

##### S6_MajorFaults

##### S1_S2_S33_Processor_Status

##### S5_Minor_Faults

### GEN_HK

#### This is the General Housekeeping subroutine for the program.  The program is responsible for upkeep on the internal PLC clock.  The task also sets “flags” for Day Reset, Month Reset and Year Reset.  These flags are used by other subroutines for resetting items such as daily flow totals.

#### The routine contains the main PLC status UDT, which stores all of the PLC processor information.  This UDT is used in other programs.  When creating this tag, the “BXX” should be substituted with the Fragment 1 and 2 of the new program name.

### Heartbeat

#### The PLC peer-to-peer messaging heartbeat shall be programmed in this routine.  This heartbeat shall toggle between a value of one and zero, with a default of 30 seconds on and 30 seconds off.  The timing of this heartbeat may be adjusted with approval from Halton Region in the event of phantom communication alarms being observed due to message instruction execution timing.

#### If the PLC is an Autodialer PAC, the SCADA heartbeat will also be implemented in this routine.  The application writes its heartbeat (-1) to the Placeholder register, once every 10 Seconds.  If the alarm timer elapses (5 min), then the heartbeat alarm is issued.  If the heartbeat is received, it is reset back to 0, until the next heartbeat is received.

### Security

#### This is used by Halton Region’s SCADA department to monitor:

##### Mode changes in the controller i.e. remote program to remote run or after a program download; and,

##### Anytime an online edit occurs in the controller.

#### This software must not be removed or modified from its present state.

### S1_S2_S33_Processor_Status

#### This subroutine collects all processor status flags.  Programmers are not required to modify this subroutine.

### S5_Minor_Faults

#### This subroutine collects the ControlLogix version of the processor minor faults.

#### Programmers are not required to modify this subroutine.

#### S6_Major_Faults

#### This subroutine collects the ControlLogix version of the processor major faults and generate the fault code.

#### Programmers are not required to modify this subroutine.

## Inputs Program

#### The “Inputs” Program performs all input mapping, signal conditioning, and process alarming. The “Main” Routine within “Inputs” contains a collection of “JSR” instructions that calls the following subroutines

##### DI_MAP

##### AI_MAP

##### DI_EVAL

### Digital Input Map

#### The subroutine “DI_Map” moves all field generated digital raw values to the “Raw” member of the corresponding Device Tag. Each rung moves a single bit to the corresponding raw data member in the Device Tag. The documentation for each rung must clearly indicate the Rack, Slot, Point number, and the description of the data point from the field.

#### All discrete inputs are to be configured using the latest version of the SCADA_SYS_DI UDT, including spares.

- Rung from the "DI_Map" Subroutine

### Analog Input Map

#### The subroutine “AI_Map” moves all field generated analog raw values to the “Raw” member of the corresponding System Device UDT within each Device Tag. Every rung moves all analogs for a single card from the field to the corresponding raw data member in the System Device UDT. The documentation for each rung must clearly indicate the Rack and the Slot number for the analog input card.

- Rung from the "AI_Map" Subroutine

#### Halton Region does not perform Analog Scaling in the Analog I/O module. The RAW value is scaled only in the Analog Device Driver. This ensures that the same logic can be used in all Logix platforms irrespective of controller type.  All Analog Inputs are to be configured using the latest version of the SCADA_DEV_AIT UDT, including spares.

#### The following table shows the Integer Value signal for a 1756-IF8IH (ControlLogix) module for the corresponding tag element.

| Member Name | Signal Value (mA) | Data representation | Description |
| --- | --- | --- | --- |
| SYS_AIT_OC | 0 mA | -25.00 | Raw Value Open Circuit Limit |
| SYS_AIT_RANGE_MIN | 3.50 mA | -3.125 | Raw Value Range Minimum. |
| SYS_AIT_RANGE_MAX | 20.5 mA | 103.125 | Raw Value Range Maximum. |
| SYS_AIT_RAW_MIN | 4 mA | 0.00 | 4ma signal value |
| SYS_AIT_RAW_MAX | 20 mA | 100.00 | 20mA signal value |

- Input Signal to User Counts for a 1756-IF8IH module (ControlLogix)

#### Analog Input Scaling and Process Alarm generation is performed by the Analog Device Driver subroutines which are called from the Main routine in the Device Program.

### Digital Input Evaluation

#### The subroutine “DI_Eval” processes all digital inputs within each Device Tag using the Discrete_Input Add-on instruction.   Consult the SCADA_SYS_DI Programming Guide for details on implementing this AOI.

- Discrete_Input_V1 Add-On Instruction

## Device Program

#### The device program calls evaluation logic for system devices.  The table below lists available devices and their associated UDT:

| Device | UDT |
| --- | --- |
| Analog Input | SCADA_DEV_AIT |
| Pump/Motor | SCADA_DEV_MOTOR |
| Automatic Transfer Switch | SCADA_DEV_ATS |
| Generator | SCADA_DEV_GEN |
| Analog Valve | SCADA_DEV_VLV |
| Discrete Valve | SCADA_DEV_VLV |
| Power Monitor | SCADA_DEV_PRM |
| Rain Gauge | SCADA_DEV_WTN |

- List of user data types for common devices

#### Additional UDTs exist to implement secondary process functions or calculations that are often associated with a device.  These UDTs and their associated AOI should be deployed within the main device routine.

| Function | UDT |
| --- | --- |
| Overflow Totalizing and Reporting | SCADA_PRC_OVERFLOW |
| Rate of Change and Flatline Alarming | SCADA_PRC_TOLERANCE |
| Flow Estimation from change in Level | SCADA_PRC_VIRTUAL_FLOW |
| Sliding Average | SCADA_SLIDING_AVG |

- List of UDTs used to support device programming

#### Each program developed will have different devices connected to the PAC.  Programmers will need to customize the main subroutine to meet their program requirements.  The “Main” subroutine should process the device drivers in the following order:

##### Analogs

##### Pumps

##### Valves

##### ATS/Generator

##### Power Monitor

##### Rain Gauge

#### All Device Drivers are named after the device they control. The following figure shows a call to a Device Subroutine from the Main Routine in the Device Program.

- Device Subroutine JSR Instruction

#### Flow totalization within multiple PACs. Instantaneous values of flow read from other PACs should not be completed for totalization and should be completed at local PLC based upon hard-wire analog input.

#### Programmers should consult the individual programming guides for each device UDT for details on the available member objects and implementation instructions.

## ACP Program

#### The ACP program is responsible for coordinating all devices in the field according to control narratives presented to the programmer. The PLC is generally responsible for coordinating all devices within a process area (for example the primary clarifiers at the Burlington Skyway WWTP), or all devices within a remote station (for example the Garden Trails SPS).

#### The ACP consists of a minimum of six subroutines.  These are:

##### Duty_Alt

##### Duty_In

##### Duty_ACP

##### Duty_Out

##### Security

##### Alarm Dialer Interface (Alarms_Dialer_Waste or Alarms_Dialer_Water)

#### UDTs have been developed to standardize implementation for 2 Duty Pumps, 3 Duty Pumps, 4 Duty pumps, 2 Duty Transmitters, 3 Duty Transmitters, and 4 Duty Transmitters.  Consult the appropriate UDT programming guide for more information.

#### A brief description of each subroutine is shown below:

### Duty Alternations

#### The Duty Alternations routine (DTY_ALT) performs the following tasks:

#### Execution of all duty alternation AOIs for devices in the PAC.

### Duty Out

#### The Duty Translations routine (DTY_OUT) performs the following tasks:

##### Execution of all duty output assignment AOIs for devices in the PAC.

### Duty In

#### The Duty Translations routine (DTY_IN) performs the following tasks:

##### Execution of all duty input assignment AOIs for devices in the PAC.

### Duty ACP

#### The Duty ACP routine (DTY_ACP) performs the following tasks:

##### Execution of duty ACP AOIs for devices in the PLC as well as any custom control code required to meet programming objectives that cannot be achieved using the default duty ACP logic

### Device ACP

#### The Device ACP routines perform the custom auto control for the process area or remote station assigned to the PAC. The ladder code in this program uses various Device and Process UDTs to implement all automatic control algorithms outlined in the control narrative for that area. For example, the device ACP program will monitor the wet well level provided by level transmitter drivers, and activate duty / standby pumps as required.

#### The ACP routine cannot modify I/O points or SCADA interface data directly. This information is strictly processed by device driver routines, input / output mapping routines, and device duty routines.

### Security

#### This routine monitors the station or area security based on the status of security key switches and door contacts.

#### If the PLC is connected to an external security monitoring system, this routine should be deleted and the security alarms should be generated in the DI_EVAL subroutine from inputs from the security, as all status, control, and alarming logic is handled by the external system.

### Alarm Dialer Interface

#### The base load program contains two Alarm Dialer “Autodialer” Interface subroutines.  One is called “Alarms_Dialer_Waste” the other is called “Alarms_Dialer_Water.”  The “Alarms_Dialer_Water” subroutine is for North Water.  The “Alarms_Dialer_Waste” is dedicated for sites using a single general alarm for the whole plant.  Programmers are required to delete the ladder file which is not appropriate for the project being developed.

#### The Autodialer interface is used to collect all alarms for the PLC which triggers an Autodialer alarm.

#### Programmers are required to modify the plant Autodialer PLC to interface with the project they are developing.

#### Programmers are required to contact Halton Region for direction on how to modify the plant Autodialer PAC.

### Process UDT

#### Every process area is a collection of processes each named according to the Halton Region tagname convention.

#### Every process will have associated with it a “Process UDT”. The process UDT represents a template data structure containing all pertinent information for that process type. The name of every process UDT consists of five fragments separated by the underscore character.

#### The first fragment is the string “PRC” to indicate a process driver.

#### The second fragment is the actual device type. Where applicable, the device type must be identical to fragment 3 of the Halton Region tagging standard. For example, high lift pumping would be “HLP”.

#### The third fragment indicates a numerical range. The string “000” represents all devices (for example “HLP_000” represents all high lift pumps). The string “1to4” represents devices 1 to 4.

#### The fourth fragment is the major version number. Major version numbers change when the corresponding process control code within the ACP must be modified to accommodate the changes.

#### The fifth fragment is the minor version number. Minor version numbers change when a modification of the UDT type does not require any changes in the corresponding ACP code.

#### Example: the name of the high lift pump area process type UDT (version 2.0) would be: “DEV_HLP_000_2_0”

#### Every process in the field is then given a single controller scope tag named according to the Halton Region tagging standard. The tag data type is the corresponding process UDT type.

#### Example: The high lift pumps at the Burloak Water Treatment Plant. The programmer would create a single controller scoped tag called “BLC_HLP_000”. The data type of the controller tag would be “PRC_HLP_000_2_0”. The version numbers correspond to the latest device type UDT version number available at the time the process area or station was programmed. The string “SCADA” then prefixes the corresponding SCADA interface UDT for the process area. Hence the SCADA interface for the high lift pumps at Burloak is “SCADA_PRC_HLP_000_2_0”.

#### Process UDTs are considered custom for each PAC. The base load PLC program will have a selection of process UDTs only to demonstrate the use of duty sequencing and automatic control. The base load application will not archive all possible process area UDTs and their interaction with device UDTs.

## Outputs Program

#### The Outputs Program performs all output mapping and signal conditioning. The Main Routine contains a collection of “JSR” instructions to subroutines that process all digital and analog outputs.

#### There are two (2) main subroutines the main task calls.  These are:

##### DO_EVAL

##### AO

### DO_EVAL

#### The subroutine “DO_Eval” moves all internally generated digital control values to the corresponding field output register.

#### The subroutine “DO_Eval” processes all SCADA SYS_DO UDTs in the PLC program (one UDT per rung). Either the .Eng state or the .Sim state is transferred to the field output value according to the “Sim_Enable” bit. The documentation (rung comment) for each rung must clearly indicate the Rack, Slot, Point number, and the description of the data point from the field.

- Rung from the "DO_Eval" Subroutine

### AO

#### Every Analog Output UDT is processed in the Analog Output (AO) subroutine. The Analog Output subroutine is called from the Main routine. Every rung in the AO subroutine processes a single Analog Output.  If the analog output is associated with a device the necessary AOI parameters will be created as part of the device object.  If the analog output is not associated with a device, Programmers must create the necessary tags that will be compatible with the SCALE_FBD AOI. The base load program contains an example analog output evaluation rung.

#### The Programmer is responsible for ensuring all input parameters to the function block provide the desired output scaling to the field device.  Specifically, the “Limiting” parameter of the SCALE_FBD AOI must be set to true to ensure that the value sent to the card falls within the 4-20 mA operating range of the card and does not generate a fault.

#### The Analog Output Evaluation subroutine performs the following functions:

##### Scale the .Eng value into the raw value and send it to the analog output channel (if the output is not in simulation)

#### It is the responsibility of the Programmer to ensure that the correct scaling factors are used in the AOI. The following table shows the Integer Value signals for a 1756-OF8IH (ControlLogix) module for the corresponding tag element.

| Member Name | Signal Value (mA) | Data representation | Description |
| --- | --- | --- | --- |
| SYS_AO_RAW_MIN | 4 mA | 0 | Raw Value Range Minimum. |
| SYS_AO_RAW_MAX | 20 mA | 100 | Raw Value Range Maximum. |

- Output Signal to User Counts for a 1756-OF8IH module (ControlLogix)

## Function Block Diagram

#### Halton Region only approves the use of three function block diagram instructions.  These are:

##### SCL, within the SCALE_FBD AOI

##### PIDE

##### Moving Average, within the Moving_Average AOI

#### All function blocks have parameters associated with them that must be configured within the AOI block or programmed through ladder logic prior to calling the function block.

### PIDE Program

#### All PIDE function blocks are to be called from the Periodic Task PIDE.  The task is configured to run every 1000 mS with a priority of 11.

#### Two subroutines are required for every Enhanced PID (PIDE) block used for auto control. The base load application has two PIDE subroutines that are used in conjunction with the BXX_DEV1_VLV driver. The two PIDE subroutines are prefixed by the device tag (BXX_DEV1_LD and BXX_DEV1_FB)

#### When creating a new PID subroutine, the name of the Main Program should identify the device it is controlling.  The name of the subsequent “_LD” and “_FB” subroutines must use the same name.

#### The Ladder logic is placed in a routine called, “BXX_DEV1_LD.”

#### The Ladder subroutine conditions the setpoint and process value parameters before passing all values to the PID_ENHANCED member. The auto and manual mode status bits are sent to the PID_EHNANCED member as well. The manual position setpoint is passed directly to the control variable when the PIDE block is placed in manual mode.

##### Once all parameters have been properly set in the PID_ENHANCED member, the Function Block subroutine is called, and the PID_ENHANCED member is loaded into the corresponding function block.

##### Once the Function Block subroutine is finished, the results are placed back into the PID_ENHANCED member.

#### The ladder diagram consists of twelve rungs.  The function of each rung is described below:

| Rung | Description |
| --- | --- |
| 0 | This rung always keeps the PIDE loop enabled |
| 1 | This rung moves the PLT-AUTO process variable into the PIDE loop PV. The tag shown in the base load should be replaced with the appropriate PV tag. |
| 2 | This rung moves the auto PV maximum engineering value into the PV max value and the SP max value. The hard-coded numbers of 100 should be changed to reflect the operational range. |
| 3 | This rung moves the auto PV minimum engineering value into the PV min and the SP min value. The hard-coded number of 0 can be changed to reflect the operational range. |
| 4 | If the PID loop is in manual, this rung moves the PLT-MAN set point into the PIDE MAN_CV. The tag shown in the base load should be replaced with the appropriate .SCADA.AO_CT tag. |
| 5 | This rung moves the device minimum engineering value into the PIDE CV Min value. |
| 6 | This rung moves the device maximum engineering value into the PIDE CV Max value. |
| 7 | This rung sets PV Tracking and PRogProgReq bits on. These are used by the PIDE loop when it is running in Auto. |
| 8 | If the device is in plant manual mode, this rung sets the PIDE to Program Manual Mode. |
| 9 | If the device is in plant auto mode, this rung sets the PIDE to Program Auto Mode |
| 10 | If the PIDE is in auto this rung moves the CV from the Function Block into the Auto Set point assignment. The tag shown in the base load should be replaced with the appropriate .Auto_Speed_Spt tag. |
| 11 | This rung calls the function block subroutine. |

- PIDE Ladder Diagram Rung Functions

#### The function block diagram is placed in a routine called, “BXX_DEV1_FB.”

#### The Function Block subroutine contains a single Function Block that executes the PIDE instruction. Note that the Enhanced PID function block is not available as an instruction in the LD language.

#### When creating the PIDE function block the tagname of the block is the same as the name of the program, appended with “_PIDE.”

### Moving Average

#### Moving average instructions are to be placed in the Main_Task\Device Program.

#### Consult the SCADA_PRC_SLIDING_AVG Programming Guide for more details on implementing moving average calculations.

## COMMS_MSG Program

#### The COMMS_MSG periodic task is used for inter-PAC/PLC communications.

### Inter-PAC/PLC Communications

#### All data exchanged between Allen Bradley Ethernet devices uses the LD message block read (MSG) instruction.

#### A message read instruction has the destination PAC/PLC read the required data from the source PAC/PLC. Halton Region does not permit the use of message write instructions (from source PAC/PLC to destination PAC/PLC).

#### All message reads must have heartbeat detection logic associated with the code to verify integrity of the data transfer.  All heartbeats are to be implemented using a periodic on/off boolean signal, cycling at a frequency that will not trigger false alarms due to latency between message read attempts.  A period of 30 seconds on/30 seconds off is recommended.  If the heartbeat timeout alarm occurs, any processes that rely on the remote data must be brought to a safe state as quickly and safely as possible.

#### All messaging shall be implemented using the SCADA_SYS_MESSAGE UDT.  Consult the SCADA_SYS_MESSAGE Programming Guide for more details on implementing this UDT.

#### All MSG Block instructions are performed in the Main routine in the COMMS_MSG program within the COMMS_MSG periodic task. The COMMS_MSG periodic task is executed once every second with priority 10. Automatic output processing is disabled, as this task does not need to activate any field outputs. The following figure shows all configuration settings for the COMMS_MSG periodic task.

- COMMS_MSG Task Configuration Properties

### Destination Registers

#### Logix family PLC processors can exchange information with both Logix and SLC PLC processors using the same MSG read instruction.

### Logix Family Processors

#### In cases where the MSG read instruction reads data from another Logix family PLC processor, then the source and destination tags are specified during configuration of the MSG read instruction.

#### Information from the source tag is read directly into the destination tag. Array mapping is not always required (see next section on non-Logix family processors). The following figures show the configuration of a CIP Data Table Read type MSG instruction:

- CIP Message Read Instruction Configuration Tab

##### Message Type: Select “CIP Data Table Read”

##### Source Element: Enter the tag name in the source PAC

##### Number of Elements: Enter the number of elements in the source PLC tag.  When using the SCADA_SYS_MSG UDT this value is 1.

##### Destination Element: Enter the tag name in the destination PAC. Since the Halton Region Logix Standards must apply to both programs, the Source and Destination elements for all CIP read type instructions should be the same.

- CIP Message Read Instruction Communication Tab

##### Connected: leave unchecked.

##### Path: The communication path to the device must be manually entered.  Halton Region does not permit the addition of target controllers to the IO Configuration.

### Non-Logix Family Processors

#### See Appendix B for details on configuring messaging with SLC PACs.

## HISTORIAN Program

#### The purpose of the HISTORIAN Programs is to store critical analog values (such as chlorine residual and turbidity) in the PLC memory for a period of at least 5 days, so that if there is a problem with the SCADA Historian, critical values can be extracted out of the PAC.

#### The “HISTORIAN” task is a periodic task that executes once every 2.25 minutes, but only stores a value every 4.5 minutes. This task contains one program called “HISTORIAN” with a single routine called “Main”. Every critical analog value has a FIFO (first-in-first-out) stack within the SCADA_PRC_HISTORIAN UDT that holds up to 5 days’ worth of time-stamped values.

#### Programmers are required to customize the subroutine to log all “Critical” analog values. Critical Values are those that are required for compliance or C of A reporting. These tags are to be confirmed with compliance, operations, and the gatekeeper.  Consult the SCADA_PRC_Historian Programming Guide for details on implementing this UDT.

#### PLC Historian configuration data is stored in an XML file at \\BXXCPU01\Ops for use with the SCADA PLC data extraction tool.  The following properties are required for the configuration:

#### TagName – the name of the PLC Historian Tag for ControlLogix systems

#### HistorianTagName – the name of the Tag in Historian

#### ArrayLength - The total number of values stored in the PLC Historian Tag

#### IPAddress – The IP address of the Controller where the PLC Historian Tag Resides

#### TagDescription – The description of the data being logged

#### ValueRegister - The starting location for data values in SLC 500 Systems

#### YearRegister – The starting location for year values in SLC 500 Systems

#### MonthRegister – The starting location for month values in SLC 500 systems

#### DayRegister – The starting location for day values in SLC 500 Systems

#### HourRegister – The starting location for hour values in SLC 500 systems

#### MinuteRegister – The starting location for minute values in SLC 500 systems

#### Programmers shall provide the Gatekeeper with text files containing the PLC Historian Configurations using the formats below, based on the controller platform.   Text highlighted yellow is to be replaced with information related to the PLC Historian Tag. The Gatekeeper shall then make the appropriate insertions into the XML file and test the PLC Extraction Tool.

#### <Tag>

#### <TagName>MSRCRA1AI_CV</TagName>

#### <HistorianTagName>MSRCRA1AI-CV</HistorianTagName>

#### <ArrayLength>119</ArrayLength>

#### <IPAddress>192.168.124.101</IPAddress>

#### <TagDescription>MSR DAS Downloader Chlorine</TagDescription>

#### </Tag>

#### <Tag>

#### <HistorianTagName>WDSCRA3AI-CV</HistorianTagName>

#### <ArrayLength>240</ArrayLength>

#### <IPAddress>192.168.184.101</IPAddress>

#### <TagDescription>WDS1 DAS Downloader Reservoir Free Chlorine</TagDescription>

#### <ValueRegister>F70:0</ValueRegister>

#### <YearRegister>N61:0</YearRegister>

#### <MonthRegister>N62:0</MonthRegister>

#### <DayRegister>N63:0</DayRegister>

#### <HourRegister>N64:0</HourRegister>

#### <MinuteRegister>N65:0</MinuteRegister>

#### </Tag>

#### The following figure shows all configuration settings for the HISTORIAN task.

- Historian Task Configuration

## Application Specific Programming Examples

### Critical Alarm Reminder Sample Source Code

#### The critical alarm reminder source code is installed in the Autodialer PLC at each plant.

#### If a critical alarm exists, the HMI writes to a register in the Autodialer PAC.  This starts a 12 second off timer.  The timer starts a second 15-minute timer.  If the Operator acknowledges the alarm, the 12 second timer will end and the 15-minute timer will not continue.  If the 15-minute timer elapses, the HMI will read the bit and activate the Critical Alarm Reminder Pop-up.

#### The HMI functions are described in detail in Section 6.

#### Programmers should not need to modify or update this code.

### Autodialer Verification System Sample Source Code

#### The Autodialer verification system code is installed in the Autodialer PLC at each plant.

#### The Autodialer PLC is programmed to verify itself once every half hour, with an alarm test.

#### Every half hour, the PLC will latch in a test alarm.  The test alarm sends an output to the Autodialer BICM3 module.  When the Autodialer BICM3 module receives this input, it turns the unacknowledged alarm output to the PLC on.  When the PLC sees the output change state, it confirms that the Autodialer is functional and ends the test.

#### The Autodialer’s Master PLC polls the Autodialer to determine if one of the following alarm conditions is true:

##### The phone line has failed.

##### The verification system has failed.

##### The Autodialer has had an unacknowledged alarm for ten minutes.

#### Any of the above conditions will cause the Mater Autodialer to generate an Autodialer alarm indicating a failure with its slave Autodialer.

#### A detailed summary of the Dialer Verification System operation is presented in detail in Section 7.

#### Programmers should not need to modify or update this code, unless they are installing a new Autodialer.

## Working Alone System – Waste Water

### Auto Dialer Programming

#### The Auto Dialer requires special programming for the Working Alone system and general plant alarming. Each plant has a programming sheet that can be accessed from Asset Center in the folder Auto Dialer Programming Documents. The Working Alone system has a dedicated channel and uses a group of phone numbers that is different from the other dialer alarms.

#### This code is from PLC SWY1 at the South West WWTP.

#### Enable the Working Alone System and Start the 2 hour timer.

- Enable the Working Alone System and Start the 2 hour Timer

#### When the 2 hour timer is done, the five (5) minute warning timer starts and the Operator Warning window is opened on the HMI. When the 5 minute timer is done the Operator Alarm window is opened.

- Working Alone Warning Window Timer

#### Calculate the remaining time left before operator acknowledgement and five (5) minute timer

- Working Alone Operator Acknowledgement Timer