## Guide
Colour Guide
These Values Should not Changed unless Directed by Halton Region
Optional Tags. Only include if Functionality is Needed
These values must be manually configured by the Programmer
This Column is provided as a development aid and should be deleted before attempting an intouch Import
51 | Sting length is too long. Either the Device Description must be shortened or the string concatenation edited within the cell to meet the character limit
Value is Partially or Fully Derived from another entry in worksheet
Instructions
1 | These templates are provided as an aid for HMI application development.
2 | Programmers are responsible for ensuring the tags created for their application are complete and correct, irrespective of any errors or ommissions in these templates
3 | In order to create tags for a device, Programmers shall change any cell highlighted orange to an appropriate value
4 | Programmers are required to remove any optional tags, highlighted blue, not required in their application.
5 | Any cell highlighted brown should not typically require modification as it will automatically configure itself based on the values in orange cells
6 | If tag descriptions in Column 3 are too long, and the device description cannot be shorted, then the existing standard descriptors may be modified
7 | Column D must be deleted before saving the templates as CSV files for DBLoad into Intouch
Special Instructions for SCADA_SYS_DI Dialer Alarms Sheet
1 | Each Dialer Alarm Consists of 4 Discrete Tags (Alarm, Raw Enable, Dialer Enable, Supervisor Enable) and a message tag (Disabled Reason)
2 | To Create a New Alarm, Copy the 6 Rows that constitute the alarm tagas and the two tag headers for the imort and paste them on the next available row
3 | Update the Alarm Tag and Tag Description. Note that parts of these cells are already auto-generated from other fields in the worksheet
4 | When the Alarm Tag and Alarm Description are filled out by the Programmer, all remaining tag names and descriptions are populated

## BXX Alarms
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX | Plant | Station BXX | 11 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_OVF1_FI1_DA_EL | BXX | Station BXX Overflow Loss of Echo | 33 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_OVF1_FI1_DA_EL.eng | No | Station BXX Overflow Loss of Echo | 0 | 0
BXX_OVF1_FI1_PB_EL_RE | BXX | Station BXX Overflow Loss of Echo Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1_DA_EL.RE | No | Station BXX Overflow Loss of Echo Enable | 0 | 0
BXX_OVF1_FI1_PB_EL_DE | BXX | Station BXX Overflow Loss of Echo Dialer En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1_DA_EL.DE | No | Station BXX Overflow Loss of Echo Dialer En | 0 | 0
BXX_OVF1_FI1_PB_EL_SR | BXX | Station BXX Overflow Loss of Echo Super En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1_DA_EL.SR | No | Station BXX Overflow Loss of Echo Super En | 0 | 0
BXX_WW01_LI1_DA_EL | BXX | Station BXX Wet Well 1 Loss of Echo | 35 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_WW01_LI1_DA_EL.eng | No | Station BXX Wet Well 1 Loss of Echo | 0 | 0
BXX_WW01_LI1_PB_EL_RE | BXX | Station BXX Wet Well 1 Loss of Echo Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1_DA_EL.RE | No | Station BXX Wet Well 1 Loss of Echo Enable | 0 | 0
BXX_WW01_LI1_PB_EL_DE | BXX | Station BXX Wet Well 1 Loss of Echo Dialer En | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1_DA_EL.DE | No | Station BXX Wet Well 1 Loss of Echo Dialer En | 0 | 0
BXX_WW01_LI1_PB_EL_SR | BXX | Station BXX Wet Well 1 Loss of Echo Super En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1_DA_EL.SR | No | Station BXX Wet Well 1 Loss of Echo Super En | 0 | 0
BXX_WW01_LE1_DA_HH | BXX | Station BXX Wet Well 1 High Level Float | 39 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_WW01_LE1_DA_HH.eng | No | Station BXX Wet Well 1 High Level Float | 0 | 0
BXX_WW01_LE1_PB_HH_RE | BXX | Station BXX Wet Well 1 High Level Float Enable | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LE1_DA_HH.RE | No | Station BXX Wet Well 1 High Level Float Enable | 0 | 0
BXX_WW01_LE1_PB_HH_DE | BXX | Station BXX Wet Well 1 High Level Float Dialer En | 49 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LE1_DA_HH.DE | No | Station BXX Wet Well 1 High Level Float Dialer En | 0 | 0
BXX_WW01_LE1_PB_HH_SR | BXX | Station BXX Wet Well 1 High Level Float Super En | 48 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LE1_DA_HH.SR | No | Station BXX Wet Well 1 High Level Float Super En | 0 | 0
BXX_WW02_LI1_DA_EL | BXX | Station BXX Wet Well 2 Loss of Echo | 35 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_WW02_LI1_DA_EL.eng | No | Station BXX Wet Well 2 Loss of Echo | 0 | 0
BXX_WW02_LI1_PB_EL_RE | BXX | Station BXX Wet Well 2 Loss of Echo Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1_DA_EL.RE | No | Station BXX Wet Well 2 Loss of Echo Enable | 0 | 0
BXX_WW02_LI1_PB_EL_DE | BXX | Station BXX Wet Well 2 Loss of Echo Dialer En | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1_DA_EL.DE | No | Station BXX Wet Well 2 Loss of Echo Dialer En | 0 | 0
BXX_WW02_LI1_PB_EL_SR | BXX | Station BXX Wet Well 2 Loss of Echo Super En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1_DA_EL.SR | No | Station BXX Wet Well 2 Loss of Echo Super En | 0 | 0
BXX_WW02_LE1_DA_HH | BXX | Station BXX Wet Well 2 High Level Float | 39 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_WW02_LE1_DA_HH.eng | No | Station BXX Wet Well 2 High Level Float | 0 | 0
BXX_WW02_LE1_PB_HH_RE | BXX | Station BXX Wet Well 2 High Level Float Enable | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LE1_DA_HH.RE | No | Station BXX Wet Well 2 High Level Float Enable | 0 | 0
BXX_WW02_LE1_PB_HH_DE | BXX | Station BXX Wet Well 2 High Level Float Dialer En | 49 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LE1_DA_HH.DE | No | Station BXX Wet Well 2 High Level Float Dialer En | 0 | 0
BXX_WW02_LE1_PB_HH_SR | BXX | Station BXX Wet Well 2 High Level Float Super En | 48 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LE1_DA_HH.SR | No | Station BXX Wet Well 2 High Level Float Super En | 0 | 0
BXX_PSB1_CP1_DA_JR | BXX | Station BXX Control Power Failure | 33 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_PSB1_CP1_DA_JR.eng | No | Station BXX Control Power Failure | 0 | 0
BXX_PSB1_CP1_PB_JR_RE | BXX | Station BXX Control Power Failure Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_CP1_DA_JR.RE | No | Station BXX Control Power Failure Enable | 0 | 0
BXX_PSB1_CP1_PB_JR_DE | BXX | Station BXX Control Power Failure Dialer En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_CP1_DA_JR.DE | No | Station BXX Control Power Failure Dialer En | 0 | 0
BXX_PSB1_CP1_PB_JR_SR | BXX | Station BXX Control Power Failure Super En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_CP1_DA_JR.SR | No | Station BXX Control Power Failure Super En | 0 | 0
BXX_UPS1_001_DA_GA | BXX | Station BXX Main UPS Fault | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_UPS1_001_DA_GA.eng | No | Station BXX Main UPS Fault | 0 | 0
BXX_UPS1_001_PB_GA_RE | BXX | Station BXX Main UPS Fault Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_001_DA_GA.RE | No | Station BXX Main UPS Fault Enable | 0 | 0
BXX_UPS1_001_PB_GA_DE | BXX | Station BXX Main UPS Fault Dialer En | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_001_DA_GA.DE | No | Station BXX Main UPS Fault Dialer En | 0 | 0
BXX_UPS1_001_PB_GA_SR | BXX | Station BXX Main UPS Fault Super En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_001_DA_GA.SR | No | Station BXX Main UPS Fault Super En | 0 | 0
BXX_UPS1_BT1_DA_JL | BXX | Station BXX Main UPS Low Battery | 32 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_UPS1_BT1_DA_JL.eng | No | Station BXX Main UPS Low Battery | 0 | 0
BXX_UPS1_BT1_PB_JL_RE | BXX | Station BXX Main UPS Low Battery Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_BT1_DA_JL.RE | No | Station BXX Main UPS Low Battery Enable | 0 | 0
BXX_UPS1_BT1_PB_JL_DE | BXX | Station BXX Main UPS Low Battery Dialer En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_BT1_DA_JL.DE | No | Station BXX Main UPS Low Battery Dialer En | 0 | 0
BXX_UPS1_BT1_PB_JL_SR | BXX | Station BXX Main UPS Low Battery Super En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_BT1_DA_JL.SR | No | Station BXX Main UPS Low Battery Super En | 0 | 0
BXX_PSB1_JI1_DA_GA | BXX | Station BXX Phase Failure | 25 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_PSB1_JI1_DA_GA.eng | No | Station BXX Phase Failure | 0 | 0
BXX_PSB1_JI1_PB_GA_RE | BXX | Station BXX Phase Failure Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_GA.RE | No | Station BXX Phase Failure Enable | 0 | 0
BXX_PSB1_JI1_PB_GA_DE | BXX | Station BXX Phase Failure Dialer En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_GA.DE | No | Station BXX Phase Failure Dialer En | 0 | 0
BXX_PSB1_JI1_PB_GA_SR | BXX | Station BXX Phase Failure Super En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_GA.SR | No | Station BXX Phase Failure Super En | 0 | 0
BXX_DDT1_LS1_DA_KA | BXX | Station BXX Diesel Flood | 24 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_DDT1_LS1_DA_KA.eng | No | Station BXX Diesel Flood | 0 | 0
BXX_DDT1_LS1_PB_KA_RE | BXX | Station BXX Diesel Flood Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDT1_LS1_DA_KA.RE | No | Station BXX Diesel Flood Enable | 0 | 0
BXX_DDT1_LS1_PB_KA_DE | BXX | Station BXX Diesel Flood Dialer En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDT1_LS1_DA_KA.DE | No | Station BXX Diesel Flood Dialer En | 0 | 0
BXX_DDT1_LS1_PB_KA_SR | BXX | Station BXX Diesel Flood Super En | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDT1_LS1_DA_KA.SR | No | Station BXX Diesel Flood Super En | 0 | 0
BXX_DDV1_LS1_DA_KA | BXX | Station BXX Diesel Tank Loss Vac Alarm | 38 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_DDV1_LS1_DA_KA.eng | No | Station BXX Diesel Tank Loss Vac Alarm | 0 | 0
BXX_DDV1_LS1_PB_KA_RE | BXX | Station BXX Diesel Tank Loss Vac Alarm Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDV1_LS1_DA_KA.RE | No | Station BXX Diesel Tank Loss Vac Alarm Enable | 0 | 0
BXX_DDV1_LS1_PB_KA_DE | BXX | Station BXX Diesel Tank Loss Vac Alarm Dialer En | 48 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDV1_LS1_DA_KA.DE | No | Station BXX Diesel Tank Loss Vac Alarm Dialer En | 0 | 0
BXX_DDV1_LS1_PB_KA_SR | BXX | Station BXX Diesel Tank Loss Vac Alarm Super En | 47 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDV1_LS1_DA_KA.SR | No | Station BXX Diesel Tank Loss Vac Alarm Super En | 0 | 0
BXX_PSB1_JI1_DA_NF | BXX | Station BXX Ground Fault | 24 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_PSB1_JI1_DA_NF.eng | No | Station BXX Ground Fault | 0 | 0
BXX_PSB1_JI1_PB_NF_RE | BXX | Station BXX Ground Fault Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_NF.RE | No | Station BXX Ground Fault Enable | 0 | 0
BXX_PSB1_JI1_PB_NF_DE | BXX | Station BXX Ground Fault Dialer En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_NF.DE | No | Station BXX Ground Fault Dialer En | 0 | 0
BXX_PSB1_JI1_PB_NF_SR | BXX | Station BXX Ground Fault Super En | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_NF.SR | No | Station BXX Ground Fault Super En | 0 | 0
BXX_GEN1_VV1_DA_SF | BXX | Station BXX Louver Failed to Open | 33 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_GEN1_VV1_DA_SF.eng | No | Station BXX Louver Failed to Open | 0 | 0
BXX_GEN1_VV1_PB_SF_RE | BXX | Station BXX Louver Failed to Open Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_VV1_DA_SF.RE | No | Station BXX Louver Failed to Open Enable | 0 | 0
BXX_GEN1_VV1_PB_SF_DE | BXX | Station BXX Louver Failed to Open Dialer En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_VV1_DA_SF.DE | No | Station BXX Louver Failed to Open Dialer En | 0 | 0
BXX_GEN1_VV1_PB_SF_SR | BXX | Station BXX Louver Failed to Open Super En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_VV1_DA_SF.SR | No | Station BXX Louver Failed to Open Super En | 0 | 0
BXX_PSB1_TI1_DA_TL | BXX | Station BXX Low Temperature | 27 | No | No | 0 | Yes | Off | Normal | Alarm | On | 57 | Direct | BXX | No | BXX_PSB1_TI1_DA_TL.eng | No | Station BXX Low Temperature | 0 | 0
BXX_PSB1_TI1_PB_TL_RE | BXX | Station BXX Low Temperature Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TL.RE | No | Station BXX Low Temperature Enable | 0 | 0
BXX_PSB1_TI1_PB_TL_DE | BXX | Station BXX Low Temperature Dialer En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TL.DE | No | Station BXX Low Temperature Dialer En | 0 | 0
BXX_PSB1_TI1_PB_TL_SR | BXX | Station BXX Low Temperature Super En | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TL.SR | No | Station BXX Low Temperature Super En | 0 | 0
BXX_PSB1_TI1_DA_TH | BXX | Station BXX High Temperature | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 56 | Direct | BXX | No | BXX_PSB1_TI1_DA_TH.eng | No | Station BXX High Temperature | 0 | 0
BXX_PSB1_TI1_PB_TH_RE | BXX | Station BXX High Temperature Enable | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TH.RE | No | Station BXX High Temperature Enable | 0 | 0
BXX_PSB1_TI1_PB_TH_DE | BXX | Station BXX High Temperature Dialer En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TH.DE | No | Station BXX High Temperature Dialer En | 0 | 0
BXX_PSB1_TI1_PB_TH_SR | BXX | Station BXX High Temperature Super En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TH.SR | No | Station BXX High Temperature Super En | 0 | 0
BXX_DW01_LE1_DA_KA | BXX | Station BXX Dry Well Flood | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_DW01_LE1_DA_KA.eng | No | Station BXX Dry Well Flood | 0 | 0
BXX_DW01_LE1_PB_KA_RE | BXX | Station BXX Dry Well Flood Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DW01_LE1_DA_KA.RE | No | Station BXX Dry Well Flood Enable | 0 | 0
BXX_DW01_LE1_PB_KA_DE | BXX | Station BXX Dry Well Flood Dialer En | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DW01_LE1_DA_KA.DE | No | Station BXX Dry Well Flood Dialer En | 0 | 0
BXX_DW01_LE1_PB_KA_SR | BXX | Station BXX Dry Well Flood Super En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DW01_LE1_DA_KA.SR | No | Station BXX Dry Well Flood Super En | 0 | 0
BXX_PSB1_001_DA_YA | BXX | Station BXX Fire Alarm | 22 | No | No | 0 | Yes | Off | Normal | Alarm | On | 1 | Direct | BXX | No | BXX_PSB1_001_DA_YA.eng | No | Station BXX Fire Alarm | 0 | 0
BXX_PSB1_001_PB_YA_RE | BXX | Station BXX Fire Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_001_DA_YA.RE | No | Station BXX Fire Alarm Enable | 0 | 0
BXX_PSB1_001_PB_YA_DE | BXX | Station BXX Fire Alarm Dialer En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_001_DA_YA.DE | No | Station BXX Fire Alarm Dialer En | 0 | 0
BXX_PSB1_001_PB_YA_SR | BXX | Station BXX Fire Alarm Super En | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_001_DA_YA.SR | No | Station BXX Fire Alarm Super En | 0 | 0
BXX_GDS1_GI1_DA_AR | BXX | Station BXX Gas Detector Failure | 32 | No | No | 0 | Yes | Off | Normal | Alarm | On | 12 | Direct | BXX | No | BXX_GDS1_GI1_DA_AR.eng | No | Station BXX Gas Detector Failure | 0 | 0
BXX_GDS1_GI1_PB_AR_RE | BXX | Station BXX Gas Detector Failure Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AR.RE | No | Station BXX Gas Detector Failure Enable | 0 | 0
BXX_GDS1_GI1_PB_AR_DE | BXX | Station BXX Gas Detector Failure Dialer En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AR.DE | No | Station BXX Gas Detector Failure Dialer En | 0 | 0
BXX_GDS1_GI1_PB_AR_SR | BXX | Station BXX Gas Detector Failure Super En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AR.SR | No | Station BXX Gas Detector Failure Super En | 0 | 0
BXX_GDS1_GI1_DA_AG | BXX | Station BXX Gas Detector Alarm | 30 | No | No | 0 | Yes | Off | Normal | Alarm | On | 10 | Direct | BXX | No | BXX_GDS1_GI1_DA_AG.eng | No | Station BXX Gas Detector Alarm | 0 | 0
BXX_GDS1_GI1_PB_AG_RE | BXX | Station BXX Gas Detector Alarm Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AG.RE | No | Station BXX Gas Detector Alarm Enable | 0 | 0
BXX_GDS1_GI1_PB_AG_DE | BXX | Station BXX Gas Detector Alarm Dialer En | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AG.DE | No | Station BXX Gas Detector Alarm Dialer En | 0 | 0
BXX_GDS1_GI1_PB_AG_SR | BXX | Station BXX Gas Detector Alarm Super En | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AG.SR | No | Station BXX Gas Detector Alarm Super En | 0 | 0
BXX_GDS1_GI1_DA_AW | BXX | Station BXX Gas Detector Warning | 32 | No | No | 0 | Yes | Off | Normal | Alarm | On | 310 | Direct | BXX | No | BXX_GDS1_GI1_DA_AW.eng | No | Station BXX Gas Detector Warning | 0 | 0
BXX_GDS1_GI1_PB_AW_RE | BXX | Station BXX Gas Detector Warning Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AW.RE | No | Station BXX Gas Detector Warning Enable | 0 | 0
BXX_GDS1_GI1_PB_AW_DE | BXX | Station BXX Gas Detector Warning Dialer En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AW.DE | No | Station BXX Gas Detector Warning Dialer En | 0 | 0
BXX_GDS1_GI1_PB_AW_SR | BXX | Station BXX Gas Detector Warning Super En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AW.SR | No | Station BXX Gas Detector Warning Super En | 0 | 0
BXX_PSU1_001_DA_GA | BXX | Station BXX Main 24VDC Power Fault | 34 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_PSU1_001_DA_GA.eng | No | Station BXX Main 24VDC Power Fault | 0 | 0
BXX_PSU1_001_PB_GA_RE | BXX | Station BXX Main 24VDC Power Fault Enable | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSU1_001_DA_GA.RE | No | Station BXX Main 24VDC Power Fault Enable | 0 | 0
BXX_PSU1_001_PB_GA_DE | BXX | Station BXX Main 24VDC Power Fault Dialer En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSU1_001_DA_GA.DE | No | Station BXX Main 24VDC Power Fault Dialer En | 0 | 0
BXX_PSU1_001_PB_GA_SR | BXX | Station BXX Main 24VDC Power Fault Super En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSU1_001_DA_GA.SR | No | Station BXX Main 24VDC Power Fault Super En | 0 | 0
BXX_BLS1_CP1_DA_GA | BXX | Station BXX Backup 24VDC Power Fault | 36 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_BLS1_CP1_DA_GA.eng | No | Station BXX Backup 24VDC Power Fault | 0 | 0
BXX_BLS1_CP1_PB_GA_RE | BXX | Station BXX Backup 24VDC Power Fault Enable | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_CP1_DA_GA.RE | No | Station BXX Backup 24VDC Power Fault Enable | 0 | 0
BXX_BLS1_CP1_PB_GA_DE | BXX | Station BXX Backup 24VDC Power Fault Dialer En | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_CP1_DA_GA.DE | No | Station BXX Backup 24VDC Power Fault Dialer En | 0 | 0
BXX_BLS1_CP1_PB_GA_SR | BXX | Station BXX Backup 24VDC Power Fault Super En | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_CP1_DA_GA.SR | No | Station BXX Backup 24VDC Power Fault Super En | 0 | 0
BXX_STN1_EY1_DA_SS | BXX | Station BXX Eyewash Station Active | 34 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_STN1_EY1_DA_SS.eng | No | Station BXX Eyewash Station Active | 0 | 0
BXX_STN1_EY1_PB_SS_RE | BXX | Station BXX Eyewash Station Active Enable | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_EY1_DA_SS.RE | No | Station BXX Eyewash Station Active Enable | 0 | 0
BXX_STN1_EY1_PB_SS_DE | BXX | Station BXX Eyewash Station Active Dialer En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_EY1_DA_SS.DE | No | Station BXX Eyewash Station Active Dialer En | 0 | 0
BXX_STN1_EY1_PB_SS_SR | BXX | Station BXX Eyewash Station Active Super En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_EY1_DA_SS.SR | No | Station BXX Eyewash Station Active Super En | 0 | 0
BXX_GEN1_JI1_DA_CD | BXX | Station BXX Generator Breaker Not Closed | 40 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_GEN1_JI1_DA_CD.eng | No | Station BXX Generator Breaker Not Closed | 0 | 0
BXX_GEN1_JI1_PB_CD_RE | BXX | Station BXX Generator Breaker Not Closed Enable | 47 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_JI1_DA_CD.RE | No | Station BXX Generator Breaker Not Closed Enable | 0 | 0
BXX_GEN1_JI1_PB_CD_DE | BXX | Station BXX Generator Breaker Not Closed Dialer En | 50 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_JI1_DA_CD.DE | No | Station BXX Generator Breaker Not Closed Dialer En | 0 | 0
BXX_GEN1_JI1_PB_CD_SR | BXX | Station BXX Generator Breaker Not Closed Super En | 49 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_JI1_DA_CD.SR | No | Station BXX Generator Breaker Not Closed Super En | 0 | 0
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_OVF1_FI1_PB_EL_RN | BXX | Station BXX Overflow Loss of Echo Dis Reason | 44 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_EL_RN | No | Station BXX Overflow Loss of Echo Dis Reason |  |  |  |  | 0 | 0
BXX_WW01_LI1_PB_EL_RN | BXX | Station BXX Wet Well 1 Loss of Echo Dis Reason | 46 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW01_LI1_PB_EL_RN | No | Station BXX Wet Well 1 Loss of Echo Dis Reason
BXX_WW01_LE1_PB_HH_RN | BXX | Station BXX Wet Well 1 High Level Float Dis Reason | 50 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW01_LE1_PB_HH_RN | No | Station BXX Wet Well 1 High Level Float Dis Reason
BXX_WW02_LI1_PB_EL_RN | BXX | Station BXX Wet Well 2 Loss of Echo Dis Reason | 46 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW02_LI1_PB_EL_RN | No | Station BXX Wet Well 2 Loss of Echo Dis Reason
BXX_WW02_LE1_PB_HH_RN | BXX | Station BXX Wet Well 2 High Level Float Dis Reason | 50 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW02_LE1_PB_HH_RN | No | Station BXX Wet Well 2 High Level Float Dis Reason
BXX_PSB1_CP1_PB_JR_RN | BXX | Station BXX Control Power Failure Dis Reason | 44 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_CP1_PB_JR_RN | No | Station BXX Control Power Failure Dis Reason
BXX_UPS1_001_PB_GA_RN | BXX | Station BXX Main UPS Fault Dis Reason | 37 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_UPS1_001_PB_GA_RN | No | Station BXX Main UPS Fault Dis Reason
BXX_UPS1_BT1_PB_JL_RN | BXX | Station BXX Main UPS Low Battery Dis Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_UPS1_BT1_PB_JL_RN | No | Station BXX Main UPS Low Battery Dis Reason
BXX_PSB1_JI1_PB_GA_RN | BXX | Station BXX Phase Failure Dis Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_JI1_PB_GA_RN | No | Station BXX Phase Failure Dis Reason
BXX_DDT1_LS1_PB_KA_RN | BXX | Station BXX Diesel Flood Dis Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DDT1_LS1_PB_KA_RN | No | Station BXX Diesel Flood Dis Reason
BXX_DDV1_LS1_PB_KA_RN | BXX | Station BXX Diesel Tank Loss Vac Alarm Dis Reason | 49 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DDV1_LS1_PB_KA_RN | No | Station BXX Diesel Tank Loss Vac Alarm Dis Reason
BXX_PSB1_JI1_PB_NF_RN | BXX | Station BXX Ground Fault Dis Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_JI1_PB_NF_RN | No | Station BXX Ground Fault Dis Reason
BXX_GEN1_VV1_PB_SF_RN | BXX | Station BXX Louver Failed to Open Dis Reason | 44 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_VV1_PB_SF_RN | No | Station BXX Louver Failed to Open Dis Reason
BXX_PSB1_TI1_PB_TL_RN | BXX | Station BXX Low Temperature Dis Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_TI1_PB_TL_RN | No | Station BXX Low Temperature Dis Reason
BXX_PSB1_TI1_PB_TH_RN | BXX | Station BXX High Temperature Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_TI1_PB_TH_RN | No | Station BXX High Temperature Dis Reason
BXX_DW01_LE1_PB_KA_RN | BXX | Station BXX High Temperature Enable Dis Reason | 46 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DW01_LE1_PB_KA_RN | No | Station BXX High Temperature Enable Dis Reason
BXX_PSB1_001_PB_YA_RN | BXX | Station BXX High Temperature Dialer En Dis Reason | 49 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_001_PB_YA_RN | No | Station BXX High Temperature Dialer En Dis Reason
BXX_GDS1_GI1_PB_AR_RN | BXX | Station BXX Gas Detector Failure Dis Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GDS1_GI1_PB_AR_RN | No | Station BXX Gas Detector Failure Dis Reason
BXX_GDS1_GI1_PB_AG_RN | BXX | Station BXX Gas Detector Alarm Dis Reason | 41 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GDS1_GI1_PB_AG_RN | No | Station BXX Gas Detector Alarm Dis Reason
BXX_GDS1_GI1_PB_AW_RN | BXX | Station BXX Gas Detector Warning Dis Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GDS1_GI1_PB_AW_RN | No | Station BXX Gas Detector Warning Dis Reason
BXX_PSU1_001_PB_GA_RN | BXX | Station BXX Main 24VDC Power Fault Dis Reason | 45 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSU1_001_PB_GA_RN | No | Station BXX Main 24VDC Power Fault Dis Reason
BXX_BLS1_CP1_PB_GA_RN | BXX | Station BXX Backup 24VDC Power Fault Dis Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_BLS1_CP1_PB_GA_RN | No | Station BXX Backup 24VDC Power Fault Dis Reason
BXX_STN1_EY1_PB_SS_RN | BXX | Station BXX Eyewash Station Active Dis Reason | 45 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_STN1_EY1_PB_SS_RN | No | Station BXX Eyewash Station Active Dis Reason
BXX_GEN1_JI1_PB_CD_RN | BXX | Station BXX Generator Breaker Not Closed Dis Rsn | 48 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_JI1_PB_CD_RN | No | Station BXX Generator Breaker Not Closed Dis Rsn

## SCADA_DEV_RPU
:mode=ask |  |  | Description Lengths
:IOAccess | Application | Topic | 5 | AdviseActive | DDEProtocol | SecApplication | SecTopic | SecAdviseActive | SecDDEProtocol | FailoverExpression | FailoverDeadband | DFOFlag | FBDFlag | FailbackDeadband
BXX | \\BXXCPU01\ABCIP | BXX | 3 | Yes | No | \\BXXCPU02\ABCIP | BXX | Yes | No |  | 0 | Yes | Yes | 5
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX | Plant | BXX PLC | 7 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1 | BXX | BXX Controller Status | 21 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO.DIsc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_PLC1_KS1_DI_PM | BXX_PLC1 | BXX Key Program Mode Status | 27 | No | Yes | 900 | Yes | Off | Off | Program | None | 1 | Direct | BXX | No | BXX_PLC1.KEY_PROGRAM | No | BXX Key Program Mode Status | 0 | 0
BXX_PLC1_KS1_DI_RM | BXX_PLC1 | BXX Key Run Mode Status | 23 | No | Yes | 900 | Yes | Off | Off | Run | None | 1 | Direct | BXX | No | BXX_PLC1.KEY_RUN | No | BXX Key Run Mode Status | 0 | 0
BXX_PLC1_F91_DA_EN | BXX_PLC1 | BXX Forces Enabled | 18 | No | Yes | 900 | Yes | Off | Disabled | Enabled | On | 10 | Direct | BXX | No | BXX_PLC1.FORCES_ENABLED | No | BXX Forces Enabled | 0 | 0
BXX_PLC1_F61_DA_SS | BXX_PLC1 | BXX Minor Fault IO Alarm | 24 | No | No | 0 | Yes | Off | Normal | Fault | On | 10 | Direct | BXX | No | BXX_PLC1.MINORFAULT_IO | No | BXX Minor Fault IO Alarm | 2 | 0
BXX_PLC1_F71_DA_SS | BXX_PLC1 | BXX Forces Present | 18 | No | No | 0 | Yes | Off | Disabled | Present | On | 275 | Direct | BXX | No | BXX_PLC1.FORCES_PRESENT | No | BXX Forces Present | 0 | 0
BXX_PLC1_F31_DA_SS | BXX_PLC1 | BXX Major Fault Watchdog Alarm | 30 | No | No | 0 | Yes | Off | Normal | Fault | On | 10 | Direct | BXX | No | BXX_PLC1.MAJORFAULT_WATCHDOG | No | BXX Major Fault Watchdog Alarm | 2 | 0
BXX_PLC1_JI1_DA_BT | BXX_PLC1 | BXX Minor Fault Battery Alarm | 29 | No | No | 0 | Yes | Off | Normal | Fault | On | 10 | Direct | BXX | No | BXX_PLC1.MINORFAULT_BATTERY_LOW | No | BXX Minor Fault Battery Alarm | 2 | 0
BXX_PLC1_F21_DA_SS | BXX_PLC1 | BXX Major Fault Startup Alarm | 29 | No | No | 0 | Yes | Off | Normal | Fault | On | 10 | Direct | BXX | No | BXX_PLC1.MAJORFAULT_STARTUP | No | BXX Major Fault Startup Alarm | 2 | 0
BXX_PLC1_F81_DI_SS | BXX_PLC1 | BXX Minor Faults | 16 | No | Yes | 900 | Yes | Off | Normal | Fault | None | 1 | Direct | BXX | No | BXX_PLC1.MINOR_FAULT_PROGRAM | No | BXX Minor Faults | 0 | 0
BXX_PLC1_CK1_PB_SU | BXX | BXX Set PLC Date/Time | 21 | No | Yes | 900 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_PLC1.DO_SU | No | BXX Set PLC Date/Time | 0 | 0
BXX_PLC1_001_DI_TM | BXX_PLC1 | BXX Controller Test Mode Status | 31 | No | Yes | 900 | Yes | Off | Off | Test | None | 1 | Direct | BXX | No | BXX_PLC1.CONTROLLER_TEST | No | BXX Controller Test Mode Status | 0 | 0
BXX_PLC1_001_DI_RE | BXX_PLC1 | BXX Run mode status | 19 | No | Yes | 900 | Yes | Off | Off | Run | None | 1 | Direct | BXX | No | BXX_PLC1.CONTROLLER_RUN | No | BXX Run mode status | 0 | 0
BXX_PLC1_KS1_DI_RE | BXX_PLC1 | BXX Key Remote Mode Status | 26 | No | Yes | 900 | Yes | Off | Off | Remote | None | 1 | Direct | BXX | No | BXX_PLC1.KEY_REMOTE | No | BXX Key Remote Mode Status | 0 | 0
BXX_PLC1_001_DI_CN | BXX | BXX-HMI Communication Status | 28 | No | No | 0 | Yes | On | Down | Ok | None | 1 | Direct | BXX | No | $SYS$Status | No | BXX-HMI Communication Status | 0 | 0
BXX_PLC1_001_DA_CN | BXX_PLC1 | BXX Polling Status Down | 23 | No | No | 0 | Yes | On | Down | Ok | Off | 90 | Direct | BXXCPU01_1 | Yes | BXX_PLC1_001_DA_CN | No | BXX Polling Status Down | 0 | 0
BXX_PLC1_001_DA_FL | BXX_PLC1 | BXX Controller Faulted Status | 29 | No | No | 0 | Yes | Off | Normal | Fault | On | 1 | Direct | BXX | No | BXX_PLC1.CONTROLLER_FAULTED | No | BXX Controller Faulted Status | 0 | 0
BXX_PLC1_001_DI_PM | BXX_PLC1 | BXX Controller Program Mode Status | 34 | No | No | 0 | Yes | Off | Off | Program | On | 1 | Direct | BXX | No | BXX_PLC1.CONTROLLER_PROGRAM | No | BXX Controller Program Mode Status | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_PLC1_CK1_AI_YY | BXX_PLC1 | BXX Date - Year | 15 | No | No | 0 | Yes | No | 0 | 0 | Year | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 9999 | Linear | BXX | No | BXX_PLC1.CK.AI_YY | No | BXX Date - Year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_SN | BXX_PLC1 | BXX Date - Second Setting | 25 | No | No | 0 | Yes | No | 0 | 0 | s | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_PLC1.CK.AO_SN | No | BXX Date - Second Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_F31_AI_CV | BXX_PLC1 | BXX Major Fault Code | 21 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 1000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000 | Linear | BXX | No | BXX_PLC1.MAJOR_FAULT_CODE | No | BXX Major Fault Code | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_F21_AI_CV | BXX_PLC1 | BXX Major Fault Information | 27 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 1000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000 | Linear | BXX | No | BXX_PLC1.MAJOR_FAULT_INFO | No | BXX Major Fault Information | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_SN | BXX_PLC1 | BXX Date - Second | 17 | No | No | 0 | Yes | No | 0 | 0 | s | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_PLC1.CK.AI_SN | No | BXX Date - Second | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_MM | BXX_PLC1 | BXX Date - Month | 16 | No | No | 0 | Yes | No | 0 | 0 | Month | 0 | 0 | 12 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 12 | Linear | BXX | No | BXX_PLC1.CK.AI_MM | No | BXX Date - Month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_MS | BXX_PLC1 | BXX Date - Minutes | 18 | No | No | 0 | Yes | No | 0 | 0 | Min | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_PLC1.CK.AI_MS | No | BXX Date - Minutes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_HS | BXX_PLC1 | BXX Date - Hour | 15 | No | No | 0 | Yes | No | 0 | 0 | Hr | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_PLC1.CK.AI_HS | No | BXX Date - Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_DY | BXX_PLC1 | BXX Date - Day | 14 | No | No | 0 | Yes | No | 0 | 0 | Day | 0 | 0 | 31 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 31 | Linear | BXX | No | BXX_PLC1.CK.AI_DY | No | BXX Date - Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_MS | BXX | BXX Date - Minutes Setting | 26 | No | No | 0 | Yes | No | 0 | 0 | Min | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_PLC1.CK.AO_MS | No | BXX Date - Minutes Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_DY | BXX | BXX Date - Day Setting | 22 | No | No | 0 | Yes | No | 0 | 0 | Day | 0 | 0 | 31 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 31 | Linear | BXX | No | BXX_PLC1.CK.AO_DY | No | BXX Date - Day Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_MM | BXX | BXX Date - Month Setting | 24 | No | No | 0 | Yes | No | 0 | 0 | Month | 0 | 0 | 12 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 12 | Linear | BXX | No | BXX_PLC1.CK.AO_MM | No | BXX Date - Month Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_HS | BXX | BXX Date - Hour Setting | 23 | No | No | 0 | Yes | No | 0 | 0 | Hr | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_PLC1.CK.AO_HS | No | BXX Date - Hour Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_YY | BXX | BXX Date - Year Setting | 23 | No | No | 0 | Yes | No | 0 | 0 | Year | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 9999 | Linear | BXX | No | BXX_PLC1.CK.AO_YY | No | BXX Date - Year Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_F11_AI_CV | BXX_PLC1 | BXX Major Fault Type | 20 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 1000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000 | Linear | BXX | No | BXX_PLC1.MAJOR_FAULT_TYPE | No | BXX Major Fault Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## SCADA_SYS_DI Dialer Alarms
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX | Plant | BXX PLC | 7 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_AAA1_BB1_GA_CC | BXX | Alarm Description | 17 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_AAA1_BB1.GA_CC.eng | No | Alarm Description | 0 | 0
BXX_AAA1_BB1_GA_RE | BXX | Alarm Description Enable | 24 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_AAA1_BB1.GA_CC.RE | No | Alarm Description Enable | 0 | 0
BXX_AAA1_BB1_GA_DE | BXX | Alarm Description Dialer En | 27 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_AAA1_BB1.GA_CC.DE | No | Alarm Description Dialer En | 0 | 0
BXX_AAA1_BB1_GA_SR | BXX | Alarm Description Super En | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_AAA1_BB1.GA_CC.SR | No | Alarm Description Super En | 0 | 0
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_AAA1_BB1_GA_RN | BXX | Alarm Description Dis Reason | 28 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_AAA1_BB1_GA_RN | No | Alarm Description Dis Reason
:IODisc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_EEE1_FF1_DA_GG | BXX | Alarm Description 2 | 19 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_EEE1_FF1.DA_GG.eng | No | Alarm Description 2 | 0 | 0
BXX_EEE1_FF1_DA_GG_RE | BXX | Alarm Description 2 Enable | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_EEE1_FF1.DA_GG.RE | No | Alarm Description 2 Enable | 0 | 0
BXX_EEE1_FF1_DA_GG_DE | BXX | Alarm Description 2 Dialer En | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_EEE1_FF1.DA_GG.DE | No | Alarm Description 2 Dialer En | 0 | 0
BXX_EEE1_FF1_DA_GG_SR | BXX | Alarm Description 2 Super En | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_EEE1_FF1.DA_GG.SR | No | Alarm Description 2 Super En | 0 | 0
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_EEE1_FF1_DA_GG_RN | BXX | Alarm Description 2 Dis Reason | 30 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_EEE1_FF1_DA_GG_RN | No | Alarm Description 2 Dis Reason
:IODisc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_HHH1_II1_DA_JJ | BXX | Alarm Description 3 | 19 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_HHH1_II1.DA_JJ.eng | No | Alarm Description 3 | 0 | 0
BXX_HHH1_II1_DA_JJ_RE | BXX | Alarm Description 3 Enable | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_HHH1_II1.DA_JJ.RE | No | Alarm Description 3 Enable | 0 | 0
BXX_HHH1_II1_DA_JJ_DE | BXX | Alarm Description 3 Dialer En | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_HHH1_II1.DA_JJ.DE | No | Alarm Description 3 Dialer En | 0 | 0
BXX_HHH1_II1_DA_JJ_SR | BXX | Alarm Description 3 Super En | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_HHH1_II1.DA_JJ.SR | No | Alarm Description 3 Super En | 0 | 0
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_HHH1_II1_DA_JJ_RN | BXX | Alarm Description 3 Dis Reason | 30 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_HHH1_II1_DA_JJ_RN | No | Alarm Description 3 Dis Reason

## SCADA_DEV_AIT
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DEV1_FI1 | BXX | Sample Flow | 11 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms Group | 25 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DEV1_FI1_DI_AD | BXX_DSAB | Sample Flow Disabled Analog Alarm | 33 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_DEV1_FI1.DI_AD | No | Sample Flow Disabled Analog Alarm | 0 | 0
BXX_DEV1_FI1_DI_SC | BXX_DEV1_FI1 | Sample Flow Scan Status | 23 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.DI_SC | No | Sample Flow Scan Status | 0 | 0
BXX_DEV1_FI1_DA_LL | BXX_DEV1_FI1 | Sample Flow LOLO Alarm | 22 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DEV1_FI1.DA_LL | No | Sample Flow LOLO Alarm | 0 | 0
BXX_DEV1_FI1_DA_ER | BXX_DEV1_FI1 | Sample Flow Signal Error Alarm | 30 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DEV1_FI1.DA_ER | No | Sample Flow Signal Error Alarm | 0 | 0
BXX_DEV1_FI1_PB_SM | BXX_DEV1_FI1 | Sample Flow Alarm Test | 22 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_SM | No | Sample Flow Alarm Test | 0 | 0
BXX_DEV1_FI1_PB_SV | BXX_DEV1_FI1 | Sample Flow Override Enable | 27 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_SV | No | Sample Flow Override Enable | 0 | 0
BXX_DEV1_FI1_PB_AE | BXX_DEV1_FI1 | Sample Flow Alarm Enable | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_AE.RE | No | Sample Flow Alarm Enable | 0 | 0
BXX_DEV1_FI1_PB_HI | BXX_DEV1_FI1 | Sample Flow High Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_HI.RE | No | Sample Flow High Alarm Enable | 0 | 0
BXX_DEV1_FI1_PB_LO | BXX_DEV1_FI1 | Sample Flow Low Alarm Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_LO.RE | No | Sample Flow Low Alarm Enable | 0 | 0
BXX_DEV1_FI1_PB_LL | BXX_DEV1_FI1 | Sample Flow LOLO Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_LL.RE | No | Sample Flow LOLO Alarm Enable | 0 | 0
BXX_DEV1_FI1_PB_ER | BXX_DEV1_FI1 | Sample Flow Signal Error Alarm En | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_ER.RE | No | Sample Flow Signal Error Alarm En | 0 | 0
BXX_DEV1_FI1_PB_SC | BXX_DEV1_FI1 | Sample Flow Scan Enable | 23 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_SC | No | Sample Flow Scan Enable | 0 | 0
BXX_DEV1_FI1_DA_HH | BXX_DEV1_FI1 | Sample Flow HIHI Alarm | 22 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DEV1_FI1.DA_HH | No | Sample Flow HIHI Alarm | 0 | 0
BXX_DEV1_FI1_DA_HI | BXX_DEV1_FI1 | Sample Flow HI Alarm | 20 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DEV1_FI1.DA_HI | No | Sample Flow HI Alarm | 0 | 0
BXX_DEV1_FI1_PB_HH | BXX_DEV1_FI1 | Sample Flow HIHI Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_HH.RE | No | Sample Flow HIHI Alarm Enable | 0 | 0
BXX_DEV1_FI1_PB_AR | BXX_DEV1_FI1 | Sample Flow Alarm Reset | 23 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_AR | No | Sample Flow Alarm Reset | 0 | 0
BXX_DEV1_FI1_DA_LO | BXX_DEV1_FI1 | Sample Flow LO Alarm | 20 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DEV1_FI1.DA_LO | No | Sample Flow LO Alarm | 0 | 0
BXX_DEV1_FI1_PB_MM | BXX_DEV1_FI1 | Sample Flow Enable Limit Tracking | 33 | No | Yes | 600 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_MM | No | Sample Flow Enable Limit Tracking | 0 | 0
BXX_DEV1_FI1_PB_RS | BXX_DEV1_FI1 | Sample Flow Totalizer Reset | 27 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_RS | No | Sample Flow Totalizer Reset | 0 | 0
BXX_DEV1_FI1_PB_HI_DE | BXX_DEV1_FI1 | Sample Flow High Alarm Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_HI.DE | No | Sample Flow High Alarm Dialer Enable | 0 | 0
BXX_DEV1_FI1_PB_LO_DE | BXX_DEV1_FI1 | Sample Flow Low Alarm Dialer Enable | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_LO.DE | No | Sample Flow Low Alarm Dialer Enable | 0 | 0
BXX_DEV1_FI1_PB_LL_DE | BXX_DEV1_FI1 | Sample Flow LOLO Alarm Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_LL.DE | No | Sample Flow LOLO Alarm Dialer Enable | 0 | 0
BXX_DEV1_FI1_PB_ER_.DE | BXX_DEV1_FI1 | Sample Flow Signal Error Alarm Dialer En | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_ER.DE | No | Sample Flow Signal Error Alarm Dialer En | 0 | 0
BXX_DEV1_FI1_PB_HH_DE | BXX_DEV1_FI1 | Sample Flow HIHI Alarm Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_HH.DE | No | Sample Flow HIHI Alarm Dialer Enable | 0 | 0
BXX_DEV1_FI1_PB_AE_DE | BXX_DEV1_FI1 | Sample Flow Alarms Dialer Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_AE.DE | No | Sample Flow Alarms Dialer Enable | 0 | 0
BXX_DEV1_FI1_PB_HI_SR | BXX_DEV1_FI1 | Sample Flow High Alarm Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_HI.SR | No | Sample Flow High Alarm Sup Enable | 0 | 0
BXX_DEV1_FI1_PB_LO_SR | BXX_DEV1_FI1 | Sample Flow Low Alarm Sup Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_LO.SR | No | Sample Flow Low Alarm Sup Enable | 0 | 0
BXX_DEV1_FI1_PB_LL_SR | BXX_DEV1_FI1 | Sample Flow LOLO Alarm Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_LL.SR | No | Sample Flow LOLO Alarm Sup Enable | 0 | 0
BXX_DEV1_FI1_PB_ER_SR | BXX_DEV1_FI1 | Sample Flow Signal Error Alarm Sup En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_ER.SR | No | Sample Flow Signal Error Alarm Sup En | 0 | 0
BXX_DEV1_FI1_PB_HH_SR | BXX_DEV1_FI1 | Sample Flow HIHI Alarm Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_HH.SR | No | Sample Flow HIHI Alarm Sup Enable | 0 | 0
BXX_DEV1_FI1_PB_AE_SR | BXX_DEV1_FI1 | Sample Flow Alarms Sup Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FI1.PB_AE.SR | No | Sample Flow Alarms Sup Enable | 0 | 0
:MemoryInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinValue | MaxValue | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
ANIN_DEC | $System | Analog Signal Decimal Points - Indirect | 39 | No | No | 0 | Yes | No | 0 | 0 |  | 1096810496 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Analog Signal Decimal Points - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ANIN_DC2 | $System | Analog Input Units 2 Decimal Points - Indirect | 46 | No | No | 0 | Yes | No | 0 | 0 |  | 2 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Analog Input Units 2 Decimal Points - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ANIN_DC3 | $System | Analog Input Units 3 Decimal Points - Indirect | 46 | No | No | 0 | Yes | No | 0 | 0 |  | 2 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Analog Input Units 3 Decimal Points - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DEV1_FI1_AI_VI | BXX_DEV1_FI1 | Sample Flow Number of Visible Eng Values | 40 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_DEV1_FI1.AI_VI | No | Sample Flow Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AI_DC | BXX_DEV1_FI1 | Sample Flow Precision | 21 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_FI1.AI_DC | No | Sample Flow Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_E2_DC | BXX_DEV1_FI1 | Sample Flow Eng Value 2 Precision | 33 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_FI1.E2_DC | No | Sample Flow Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_E3_DC | BXX_DEV1_FI1 | Sample Flow Eng Value 3 Precision | 33 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_FI1.E3_DC | No | Sample Flow Eng Value 3 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DEV1_FI1_SN_LL | BXX_DEV1_FI1 | Sample Flow LOLO Alarm Delay | 28 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DEV1_FI1.SN_LL | No | Sample Flow LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_SN_HI | BXX_DEV1_FI1 | Sample Flow High Alarm Delay | 28 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DEV1_FI1.SN_HI | No | Sample Flow High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AI_CV | BXX_DEV1_FI1 | Sample Flow Current Value | 25 | Yes | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AI_CV | No | Sample Flow Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AI_ND | BXX_DEV1_FI1 | Sample Flow Min Value Today | 27 | Yes | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AI_ND | No | Sample Flow Min Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AI_NP | BXX_DEV1_FI1 | Sample Flow Max Value Today | 27 | Yes | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AI_NP | No | Sample Flow Max Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AI_XD | BXX_DEV1_FI1 | Sample Flow Min Value Yesterday | 31 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AI_XD | No | Sample Flow Min Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AI_XP | BXX_DEV1_FI1 | Sample Flow Max Value Yesterday | 31 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AI_XP | No | Sample Flow Max Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AI_TD | BXX_DEV1_FI1 | Sample Flow Total Today | 23 | Yes | No | 0 | Yes | No | 0 | 0 | L | 0 | 0 | 20000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 20000 | Linear | BXX | No | BXX_DEV1_FI1.AI_TD | No | Sample Flow Total Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AI_YT | BXX_DEV1_FI1 | Sample Flow Total Yesterday | 27 | Yes | No | 0 | Yes | No | 0 | 0 | L | 0 | 0 | 20000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 20000 | Linear | BXX | No | BXX_DEV1_FI1.AI_YT | No | Sample Flow Total Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AI_AT | BXX_DEV1_FI1 | Sample Flow Average | 19 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AI_AT | No | Sample Flow Average | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AO_XM | BXX_DEV1_FI1 | Sample Flow Span Setpoint | 25 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AO_XM | No | Sample Flow Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AO_LO | BXX_DEV1_FI1 | Sample Flow Low Setpoint | 24 | No | Yes | 600 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AO_LO | No | Sample Flow Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AO_HH | BXX_DEV1_FI1 | Sample Flow HIHI Setpoint | 25 | No | Yes | 600 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AO_HH | No | Sample Flow HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_E2_CV | BXX_DEV1_FI1 | Sample Flow Units 2 | 19 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_FI1.E2_CV | No | Sample Flow Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AO_HI | BXX_DEV1_FI1 | Sample Flow High Setpoint | 25 | No | Yes | 600 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AO_HI | No | Sample Flow High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AO_SV | BXX_DEV1_FI1 | Sample Flow Override Value | 26 | No | Yes | 700 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AO_SV | No | Sample Flow Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AO_EM | BXX_DEV1_FI1 | Sample Flow Zero Setpoint | 25 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AO_EM | No | Sample Flow Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_E3_CV | BXX_DEV1_FI1 | Sample Flow Units 3 | 19 | No | No | 0 | Yes | No | 0 | 0 | mA | 4 | 4 | 20 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 4 | 20 | Linear | BXX | No | BXX_DEV1_FI1.E3_CV | No | Sample Flow Units 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_SN_HH | BXX_DEV1_FI1 | Sample Flow HIHI Alarm Delay | 28 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DEV1_FI1.SN_HH | No | Sample Flow HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_SN_LO | BXX_DEV1_FI1 | Sample Flow Low Alarm Delay | 27 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DEV1_FI1.SN_LO | No | Sample Flow Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FI1_AO_LL | BXX_DEV1_FI1 | Sample Flow LOLO Setpoint | 25 | No | Yes | 600 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DEV1_FI1.AO_LL | No | Sample Flow LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_DEV1_FI1_DI_NM | BXX_DEV1_FI1 | BXX_DEV1_FI1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_DEV1_FI1_PB_HH_RN | BXX_DEV1_FI1 | Sample Flow HIHI Alarm Disabled Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FI1_PB_HH_RN | No | Sample Flow HIHI Alarm Disabled Reason
BXX_DEV1_FI1_PB_HI_RN | BXX_DEV1_FI1 | Sample Flow High Alarm Disabled Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FI1_PB_HI_RN | No | Sample Flow High Alarm Disabled Reason
BXX_DEV1_FI1_PB_LO_RN | BXX_DEV1_FI1 | Sample Flow Low Alarm Disabled Reason | 37 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FI1_PB_LO_RN | No | Sample Flow Low Alarm Disabled Reason
BXX_DEV1_FI1_PB_LL_RN | BXX_DEV1_FI1 | Sample Flow LOLO Alarm Disabled Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FI1_PB_LL_RN | No | Sample Flow LOLO Alarm Disabled Reason
BXX_DEV1_FI1_PB_ER_RN | BXX_DEV1_FI1 | Sample Flow Sig Error Alarm Dis Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FI1_PB_ER_RN | No | Sample Flow Sig Error Alarm Dis Reason
BXX_DEV1_FI1_PB_AE_RN | BXX_DEV1_FI1 | Sample Flow Alarms Disabled Reason | 34 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FI1_PB_AE_RN | No | Sample Flow Alarms Disabled Reason
:IndirectDisc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:IndirectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## SCADA_DEV_MOTOR
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DEV1_DM1 | BXX | Sample Motor | 12 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms Group | 25 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1 | BXX_DEV1_DM1 | Sample Motor Speed | 18 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1 | BXX_DEV1_DM1 | Sample Motor Stroke | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryDisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DEV1_DM1_DI_AD | BXX_DSAB | Sample Motor Disabled Alarm | 27 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_DEV1_DM1.DI_AD | No | Sample Motor Disabled Alarm | 0 | 0
BXX_DEV1_DM1_DI_CL | BXX_DEV1_DM1 | Sample Motor Control Mode | 25 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_CL.eng | No | Sample Motor Control Mode | 0 | 0
BXX_DEV1_DM1_DI_SK | BXX_DEV1_DM1 | Sample Motor Stroke Control Mode | 32 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_SK.eng | No | Sample Motor Stroke Control Mode | 0 | 0
BXX_DEV1_DM1_DI_SS | BXX_DEV1_DM1 | Sample Motor Running Status | 27 | Yes | Yes | 700 | Yes | Off | Stopped | Running | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_SS.eng | No | Sample Motor Running Status | 0 | 0
BXX_DEV1_DM1_DA_ES | BXX_DEV1_DM1 | Sample Motor E-Stop | 19 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_DEV1_DM1.DA_ES.eng | No | Sample Motor E-Stop | 0 | 0
BXX_DEV1_DM1_DA_RA | BXX_DEV1_DM1 | Sample Motor Overload | 21 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_DEV1_DM1.DA_RA.eng | No | Sample Motor Overload | 0 | 0
BXX_DEV1_DM1_DA_PL | BXX_DEV1_DM1 | Sample Motor Loss of Pressure | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 60 | Direct | BXX | No | BXX_DEV1_DM1.DA_PL.eng | No | Sample Motor Loss of Pressure | 0 | 0
BXX_DEV1_DM1_DA_PH | BXX_DEV1_DM1 | Sample Motor High Discharge Pressure | 36 | No | No | 0 | Yes | Off | Normal | Alarm | On | 60 | Direct | BXX | No | BXX_DEV1_DM1.DA_PH.eng | No | Sample Motor High Discharge Pressure | 0 | 0
BXX_DEV1_DM1_DA_DF | BXX_DEV1_DM1 | Sample Motor Not Ready | 22 | No | No | 0 | Yes | Off | Normal | Not Ready | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_DF.eng | No | Sample Motor Not Ready | 0 | 0
BXX_DEV1_DM1_DA_MA | BXX_DEV1_DM1 | Sample Motor Loss of Prime | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_MA.eng | No | Sample Motor Loss of Prime | 0 | 0
BXX_DEV1_DM1_DA_VM | BXX_DEV1_DM1 | Sample Motor Vacuum Alarm | 25 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_VA.eng | No | Sample Motor Vacuum Alarm | 0 | 0
BXX_DEV1_DM1_DA_GA | BXX_DEV1_DM1 | Sample Motor Soft Starter/VFD Fault | 35 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_GA.eng | No | Sample Motor Soft Starter/VFD Fault | 0 | 0
BXX_DEV1_DM1_DA_HA | BXX_DEV1_DM1 | Sample Motor Overtorque | 23 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_HA.eng | No | Sample Motor Overtorque | 0 | 0
BXX_DEV1_DM1_DA_BT | BXX_DEV1_DM1 | Sample Motor Bearing Temperature | 32 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_BT.eng | No | Sample Motor Bearing Temperature | 0 | 0
BXX_DEV1_DM1_DA_WA | BXX_DEV1_DM1 | Sample Motor Winding Temperature | 32 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_WA.eng | No | Sample Motor Winding Temperature | 0 | 0
BXX_DEV1_DM1_DA_TH | BXX_DEV1_DM1 | Sample Motor High Temperature | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_TH.eng | No | Sample Motor High Temperature | 0 | 0
BXX_DEV1_DM1_DA_TA | BXX_DEV1_DM1 | Sample Motor Temp/Leak Alarm | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_TA.eng | No | Sample Motor Temp/Leak Alarm | 0 | 0
BXX_DEV1_DM1_DA_FA | BXX_DEV1_DM1 | Sample Motor No Flow | 20 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_DEV1_DM1.DA_FA.eng | No | Sample Motor No Flow | 0 | 0
BXX_DEV1_DM1_DI_AA | BXX_DEV1_DM1 | Sample Motor Auto Mode | 22 | No | Yes | 700 | Yes | Off | PLT-MAN | AUTO | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_AA | No | Sample Motor Auto Mode | 0 | 0
BXX_DEV1_DM1_DI_AS | BXX_DEV1_DM1 | Sample Motor Auto Stroke | 24 | No | Yes | 700 | Yes | Off | PLT-MAN | AUTO | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_AS | No | Sample Motor Auto Stroke | 0 | 0
BXX_DEV1_DM1_DI_PM | BXX_DEV1_DM1 | Sample Motor Plant Manual Mode | 30 | No | Yes | 700 | Yes | Off | AUTO | PLT-MAN | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_PM | No | Sample Motor Plant Manual Mode | 0 | 0
BXX_DEV1_DM1_DI_MS | BXX_DEV1_DM1 | Sample Motor Plant Manual Stroke | 32 | No | Yes | 700 | Yes | Off | AUTO | PLT-MAN | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_MS | No | Sample Motor Plant Manual Stroke | 0 | 0
BXX_DEV1_DM1_DI_OF | BXX_DEV1_DM1 | Sample Motor On Backup Control | 30 | No | Yes | 700 | Yes | Off | Normal | Backup | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_OF.eng | No | Sample Motor On Backup Control | 0 | 0
BXX_DEV1_DM1_PB_PM | BXX_DEV1_DM1 | Sample Motor Plant Manual Mode RQ | 33 | No | Yes | 600 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_PM | No | Sample Motor Plant Manual Mode RQ | 0 | 0
BXX_DEV1_DM1_PB_MS | BXX_DEV1_DM1 | Sample Motor Plant Manual Stroke RQ | 35 | No | Yes | 600 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_MS | No | Sample Motor Plant Manual Stroke RQ | 0 | 0
BXX_DEV1_DM1_PB_PT | BXX_DEV1_DM1 | Sample Motor Plant Manual Start | 31 | No | Yes | 600 | Yes | Off | Normal | Start | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_PT | No | Sample Motor Plant Manual Start | 0 | 0
BXX_DEV1_DM1_PB_PP | BXX_DEV1_DM1 | Sample Motor Plant Manual Stop | 30 | No | Yes | 600 | Yes | Off | Normal | Stop | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_PP | No | Sample Motor Plant Manual Stop | 0 | 0
BXX_DEV1_DM1_PB_AR | BXX_DEV1_DM1 | Sample Motor Alarm Ack | 22 | No | Yes | 600 | Yes | Off | Normal | Ack | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_AR | No | Sample Motor Alarm Ack | 0 | 0
BXX_DEV1_DM1_PB_RT | BXX_DEV1_DM1 | Sample Motor Runtime Reset | 26 | No | Yes | 600 | Yes | Off | Normal | Reset | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_RT | No | Sample Motor Runtime Reset | 0 | 0
BXX_DEV1_DM1_DA_SF | BXX_DEV1_DM1 | Sample Motor Failed To Start | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_DEV1_DM1.DA_SF | No | Sample Motor Failed To Start | 0 | 0
BXX_DEV1_DM1_DA_XF | BXX_DEV1_DM1 | Sample Motor Failed To Stop | 27 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_DEV1_DM1.DA_XF | No | Sample Motor Failed To Stop | 0 | 0
BXX_DEV1_DM1_DA_SU | BXX_DEV1_DM1 | Sample Motor Uncommanded Start | 30 | No | No | 0 | Yes | Off | Normal | Alarm | On | 53 | Direct | BXX | No | BXX_DEV1_DM1.DA_SU | No | Sample Motor Uncommanded Start | 0 | 0
BXX_DEV1_DM1_DA_XU | BXX_DEV1_DM1 | Sample Motor Uncommanded Stop | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 54 | Direct | BXX | No | BXX_DEV1_DM1.DA_XU | No | Sample Motor Uncommanded Stop | 0 | 0
BXX_DEV1_DM1_DI_BP | BXX_DEV1_DM1 | Sample Motor Bypass Mode | 24 | No | Yes | 700 | Yes | Off | Normal | Bypass | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_BP.eng | No | Sample Motor Bypass Mode | 0 | 0
BXX_DEV1_DM1_DI_ST | BXX_DEV1_DM1 | Sample Motor Hardwired Start | 28 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_ST.eng | No | Sample Motor Hardwired Start | 0 | 0
BXX_DEV1_DM1_DI_SP | BXX_DEV1_DM1 | Sample Motor Hardwired Stop | 27 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DI_SP.eng | No | Sample Motor Hardwired Stop | 0 | 0
BXX_DEV1_DM1_PB_SU | BXX_DEV1_DM1 | Sample Motor Uncomm Start Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_SU.RE | No | Sample Motor Uncomm Start Alarm En | 0 | 0
BXX_DEV1_DM1_PB_SF | BXX_DEV1_DM1 | Sample Motor Failed To Start Alarm En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_SF.RE | No | Sample Motor Failed To Start Alarm En | 0 | 0
BXX_DEV1_DM1_PB_XF | BXX_DEV1_DM1 | Sample Motor Failed To Stop Alarm En | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_XF.RE | No | Sample Motor Failed To Stop Alarm En | 0 | 0
BXX_DEV1_DM1_PB_XU | BXX_DEV1_DM1 | Sample Motor Uncomm. Stop Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_XU.RE | No | Sample Motor Uncomm. Stop Alarm En | 0 | 0
BXX_DEV1_DM1_PB_SM | BXX_DEV1_DM1 | Sample Motor Simulate Alarms PB | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_SM | No | Sample Motor Simulate Alarms PB | 0 | 0
BXX_DEV1_DM1_PB_AE | BXX_DEV1_DM1 | Sample Motor Alarm Enable | 25 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_AE.RE | No | Sample Motor Alarm Enable | 0 | 0
BXX_DEV1_DM1_PB_SU_DE | BXX_DEV1_DM1 | Sample Motor Uncomm Start Dialer En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_SU.DE | No | Sample Motor Uncomm Start Dialer En | 0 | 0
BXX_DEV1_DM1_PB_SF_DE | BXX_DEV1_DM1 | Sample Motor Failed To Start Dialer En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_SF.DE | No | Sample Motor Failed To Start Dialer En | 0 | 0
BXX_DEV1_DM1_PB_XF_DE | BXX_DEV1_DM1 | Sample Motor Failed to Stop Dialer En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_XF.DE | No | Sample Motor Failed to Stop Dialer En | 0 | 0
BXX_DEV1_DM1_PB_XU_DE | BXX_DEV1_DM1 | Sample Motor Uncomm Stop Dialer En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_XU.DE | No | Sample Motor Uncomm Stop Dialer En | 0 | 0
BXX_DEV1_DM1_PB_AE_DE | BXX_DEV1_DM1 | Sample Motor Alarms Dialer Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_AE.DE | No | Sample Motor Alarms Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_SU_SR | BXX_DEV1_DM1 | Sample Motor Uncomm. Start Sup En | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_SU.SR | No | Sample Motor Uncomm. Start Sup En | 0 | 0
BXX_DEV1_DM1_PB_SF_SR | BXX_DEV1_DM1 | Sample Motor Failed To Start Sup En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_SF.SR | No | Sample Motor Failed To Start Sup En | 0 | 0
BXX_DEV1_DM1_PB_XF_SR | BXX_DEV1_DM1 | Sample Motor Failed To Stop Sup En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_XF.SR | No | Sample Motor Failed To Stop Sup En | 0 | 0
BXX_DEV1_DM1_PB_XU_SR | BXX_DEV1_DM1 | Sample Motor Uncomm. Stop Sup En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_XU.SR | No | Sample Motor Uncomm. Stop Sup En | 0 | 0
BXX_DEV1_DM1_PB_AE_SR | BXX_DEV1_DM1 | Sample Motor Alarms Sup Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.PB_AE.SR | No | Sample Motor Alarms Sup Enable | 0 | 0
BXX_DEV1_SI1_DI_SC | BXX_DEV1_SI1 | Sample Motor Speed Scan Status | 30 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.DI_SC | No | Sample Motor Speed Scan Status | 0 | 0
BXX_DEV1_SI1_PB_SC | BXX_DEV1_SI1 | Sample Motor Speed Scan Enable | 30 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_SC | No | Sample Motor Speed Scan Enable | 0 | 0
BXX_DEV1_SI1_DA_ER | BXX_DEV1_SI1 | Sample Motor Speed Signal Error | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DEV1_SI1.DA_ER | No | Sample Motor Speed Signal Error | 0 | 0
BXX_DEV1_SI1_PB_ER | BXX_DEV1_SI1 | Sample Motor Speed Sig Error Alarm En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_ER.RE | No | Sample Motor Speed Sig Error Alarm En | 0 | 0
BXX_DEV1_SI1_PB_SV | BXX_DEV1_SI1 | Sample Motor Speed Override Enable | 34 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_SV | No | Sample Motor Speed Override Enable | 0 | 0
BXX_DEV1_SI1_DA_ZA | BXX_DEV1_SI1 | Sample Motor Speed Deviation Alarm | 34 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DEV1_SI1.DA_ZA | No | Sample Motor Speed Deviation Alarm | 0 | 0
BXX_DEV1_SI1_PB_ZA | BXX_DEV1_SI1 | Sample Motor Speed Deviation Alarm En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_ZA.RE | No | Sample Motor Speed Deviation Alarm En | 0 | 0
BXX_DEV1_SI1_PB_ZA_DE | BXX_DEV1_SI1 | Sample Motor Deviation Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_ZA.DE | No | Sample Motor Deviation Dialer Enable | 0 | 0
BXX_DEV1_SI1_PB_ZA_SR | BXX_DEV1_SI1 | Sample Motor Deviation Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_ZA.SR | No | Sample Motor Deviation Sup Enable | 0 | 0
BXX_DEV1_SK1_DI_SC | BXX_DEV1_SK1 | Sample Motor Stroke Scan Status | 31 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_DEV1_SK1.DI_SC | No | Sample Motor Stroke Scan Status | 0 | 0
BXX_DEV1_SK1_PB_SC | BXX_DEV1_SK1 | Sample Motor Stroke Scan Enable | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_SK1.PB_SC | No | Sample Motor Stroke Scan Enable | 0 | 0
BXX_DEV1_SK1_DA_ER | BXX_DEV1_SK1 | Sample Motor Stroke Signal Error | 32 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DEV1_SK1.DA_ER | No | Sample Motor Stroke Signal Error | 0 | 0
BXX_DEV1_SK1_PB_ER | BXX_DEV1_SK1 | Sample Motor Stroke Sig Error Alarm En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SK1.PB_ER.RE | No | Sample Motor Stroke Sig Error Alarm En | 0 | 0
BXX_DEV1_SK1_PB_SV | BXX_DEV1_SK1 | Sample Motor Stroke Override Enable | 35 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_SK1.PB_SV | No | Sample Motor Stroke Override Enable | 0 | 0
BXX_DEV1_SK1_DA_ZA | BXX_DEV1_SK1 | Sample Motor Stroke Deviation Alarm | 35 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DEV1_SK1.DA_ZA | No | Sample Motor Stroke Deviation Alarm | 0 | 0
BXX_DEV1_SK1_PB_ZA | BXX_DEV1_SK1 | Sample Motor Stroke Deviation Alarm En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SK1.PB_ZA.RE | No | Sample Motor Stroke Deviation Alarm En | 0 | 0
BXX_DEV1_SK1_PB_ZA_DE | BXX_DEV1_SK1 | Sample Motor Stroke Deviation Dialer Enable | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SK1.PB_ZA.DE | No | Sample Motor Stroke Deviation Dialer Enable | 0 | 0
BXX_DEV1_SK1_PB_ZA_SR | BXX_DEV1_SK1 | Sample Motor Stroke Deviation Sup Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SK1.PB_ZA.SR | No | Sample Motor Stroke Deviation Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_ES_RE | BXX_DEV1_DM1 | Sample Motor E-Stop Enable | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_ES.RE | No | Sample Motor E-Stop Enable | 0 | 0
BXX_DEV1_DM1_PB_RA_RE | BXX_DEV1_DM1 | Sample Motor Overload Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_RA.RE | No | Sample Motor Overload Enable | 0 | 0
BXX_DEV1_DM1_PB_PL_RE | BXX_DEV1_DM1 | Sample Motor Loss of Pressure Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_PL.RE | No | Sample Motor Loss of Pressure Enable | 0 | 0
BXX_DEV1_DM1_PB_PH_RE | BXX_DEV1_DM1 | Sample Motor High Disch Pressure Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_PH.RE | No | Sample Motor High Disch Pressure Enable | 0 | 0
BXX_DEV1_DM1_PB_DF_RE | BXX_DEV1_DM1 | Sample Motor Not Ready Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_DF.RE | No | Sample Motor Not Ready Enable | 0 | 0
BXX_DEV1_DM1_PB_MA_RE | BXX_DEV1_DM1 | Sample Motor Loss of Prime Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_MA.RE | No | Sample Motor Loss of Prime Enable | 0 | 0
BXX_DEV1_DM1_PB_VM_RE | BXX_DEV1_DM1 | Sample Motor Vacuum Alarm Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_VA.RE | No | Sample Motor Vacuum Alarm Enable | 0 | 0
BXX_DEV1_DM1_PB_GA_RE | BXX_DEV1_DM1 | Sample Motor Soft Starter/VFD Fault Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_GA.RE | No | Sample Motor Soft Starter/VFD Fault Enable | 0 | 0
BXX_DEV1_DM1_PB_HA_RE | BXX_DEV1_DM1 | Sample Motor Overtorque Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_HA.RE | No | Sample Motor Overtorque Enable | 0 | 0
BXX_DEV1_DM1_PB_BT_RE | BXX_DEV1_DM1 | Sample Motor Bearing Temperature Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_BT.RE | No | Sample Motor Bearing Temperature Enable | 0 | 0
BXX_DEV1_DM1_PB_WA_RE | BXX_DEV1_DM1 | Sample Motor Winding Temperature Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_WA.RE | No | Sample Motor Winding Temperature Enable | 0 | 0
BXX_DEV1_DM1_PB_TH_RE | BXX_DEV1_DM1 | Sample Motor High Temperature Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_TH.RE | No | Sample Motor High Temperature Enable | 0 | 0
BXX_DEV1_DM1_PB_TA_RE | BXX_DEV1_DM1 | Sample Motor Temp/Leak Alarm Enable | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_TA.RE | No | Sample Motor Temp/Leak Alarm Enable | 0 | 0
BXX_DEV1_DM1_PB_FA_RE | BXX_DEV1_DM1 | Sample Motor No Flow Enable | 27 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_FA.RE | No | Sample Motor No Flow Enable | 0 | 0
BXX_DEV1_DM1_PB_ES_DE | BXX_DEV1_DM1 | Sample Motor E-Stop Dialer Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_ES.DE | No | Sample Motor E-Stop Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_RA_DE | BXX_DEV1_DM1 | Sample Motor Overload Dialer Enable | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_RA.DE | No | Sample Motor Overload Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_PL_DE | BXX_DEV1_DM1 | Sample Motor Loss of Pressure Dialer Enable | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_PL.DE | No | Sample Motor Loss of Pressure Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_PH_DE | BXX_DEV1_DM1 | Sample Motor High Disch Pressure Dialer Enable | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_PH.DE | No | Sample Motor High Disch Pressure Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_DF_DE | BXX_DEV1_DM1 | Sample Motor Not Ready Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_DF.DE | No | Sample Motor Not Ready Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_MA_DE | BXX_DEV1_DM1 | Sample Motor Loss of Prime Dialer Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_MA.DE | No | Sample Motor Loss of Prime Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_VM_DE | BXX_DEV1_DM1 | Sample Motor Vacuum Alarm Dialer Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_VA.DE | No | Sample Motor Vacuum Alarm Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_GA_DE | BXX_DEV1_DM1 | Sample Motor Soft Starter/VFD Fault Dialer Enable | 49 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_GA.DE | No | Sample Motor Soft Starter/VFD Fault Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_HA_DE | BXX_DEV1_DM1 | Sample Motor Overtorque Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_HA.DE | No | Sample Motor Overtorque Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_BT_DE | BXX_DEV1_DM1 | Sample Motor Bearing Temp Dialer Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_BT.DE | No | Sample Motor Bearing Temp Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_WA_DE | BXX_DEV1_DM1 | Sample Motor Winding Temp Dialer Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_WA.DE | No | Sample Motor Winding Temp Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_TH_DE | BXX_DEV1_DM1 | Sample Motor High Temp Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_TH.DE | No | Sample Motor High Temp Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_TA_DE | BXX_DEV1_DM1 | Sample Motor Temp/Leak Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_TA.DE | No | Sample Motor Temp/Leak Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_FA_DE | BXX_DEV1_DM1 | Sample Motor No Flow Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_FA.DE | No | Sample Motor No Flow Dialer Enable | 0 | 0
BXX_DEV1_DM1_PB_ES_SR | BXX_DEV1_DM1 | Sample Motor E-Stop Sup Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_ES.SR | No | Sample Motor E-Stop Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_RA_SR | BXX_DEV1_DM1 | Sample Motor Overload Sup Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_RA.SR | No | Sample Motor Overload Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_PL_SR | BXX_DEV1_DM1 | Sample Motor Loss of Pressure Sup Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_PL.SR | No | Sample Motor Loss of Pressure Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_PH_SR | BXX_DEV1_DM1 | Sample Motor High Disch Pressure Sup Enable | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_PH.SR | No | Sample Motor High Disch Pressure Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_DF_SR | BXX_DEV1_DM1 | Sample Motor Not Ready Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_DF.SR | No | Sample Motor Not Ready Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_MA_SR | BXX_DEV1_DM1 | Sample Motor Loss of Prime Sup Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_MA.SR | No | Sample Motor Loss of Prime Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_VM_SR | BXX_DEV1_DM1 | Sample Motor Vacuum Alarm Sup Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_VA.SR | No | Sample Motor Vacuum Alarm Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_GA_SR | BXX_DEV1_DM1 | Sample Motor Soft Starter/VFD Fault Sup Enable | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_GA.SR | No | Sample Motor Soft Starter/VFD Fault Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_HA_SR | BXX_DEV1_DM1 | Sample Motor Overtorque Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_HA.SR | No | Sample Motor Overtorque Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_BT_SR | BXX_DEV1_DM1 | Sample Motor Bearing Temp Sup Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_BT.SR | No | Sample Motor Bearing Temp Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_WA_SR | BXX_DEV1_DM1 | Sample Motor Winding Temp Sup Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_WA.SR | No | Sample Motor Winding Temp Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_TH_SR | BXX_DEV1_DM1 | Sample Motor High Temp Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_TH.SR | No | Sample Motor High Temp Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_TA_SR | BXX_DEV1_DM1 | Sample Motor Temp/Leak Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_TA.SR | No | Sample Motor Temp/Leak Sup Enable | 0 | 0
BXX_DEV1_DM1_PB_FA_SR | BXX_DEV1_DM1 | Sample Motor No Flow Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_DM1.DA_FA.SR | No | Sample Motor No Flow Sup Enable | 0 | 0
:MemoryInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinValue | MaxValue | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
PMP_VIS1 | $System | Pump Internal Visibility Link - Indirect | 40 | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS2 | $System | Pump Internal Visibility Link - Indirect | 40 | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS3 | $System | Pump Internal Visibility Link - Indirect | 40 | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS4 | $System | Pump Speed Setpoint Visiblity Control - Indirect | 48 | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Speed Setpoint Visiblity Control - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DEV1_DM1_AI_TD | BXX_DEV1_DM1 | Sample Motor Starts Today | 25 | No | No | 0 | Yes | No | 0 | 0 | Starts | 0 | 0 | 1000000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_DEV1_DM1.AI_TD | No | Sample Motor Starts Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_DM1_AI_MT | BXX_DEV1_DM1 | Sample Motor Starts This Month | 30 | No | No | 0 | Yes | No | 0 | 0 | Starts | 0 | 0 | 1000000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_DEV1_DM1.AI_MT | No | Sample Motor Starts This Month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_DM1_AI_MX | BXX_DEV1_DM1 | Sample Motor Total Starts | 25 | Yes | No | 0 | Yes | No | 0 | 0 | Starts | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_DEV1_DM1.AI_MX | No | Sample Motor Total Starts | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_VI | BXX_DEV1_SI1 | Sample Motor Speed Number of Visible Eng Values | 47 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_DEV1_SI1.AI_VI | No | Sample Motor Speed Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_DC | BXX_DEV1_SI1 | Sample Motor Speed Precision | 28 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_SI1.AI_DC | No | Sample Motor Speed Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_E2_DC | BXX_DEV1_SI1 | Sample Motor Speed Eng Value 2 Precision | 40 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_SI1.E2_DC | No | Sample Motor Speed Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_E3_DC | BXX_DEV1_SI1 | Sample Motor Speed Eng Value 3 Precision | 40 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_SI1.E3_DC | No | Sample Motor Speed Eng Value 3 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AI_VI | BXX_DEV1_SK1 | Sample Motor Stroke Number of Visible Eng Values | 48 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_DEV1_SK1.AI_VI | No | Sample Motor Stroke Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AI_DC | BXX_DEV1_SK1 | Sample Motor Stroke Precision | 29 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_SK1.AI_DC | No | Sample Motor Stroke Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_E2_DC | BXX_DEV1_SK1 | Sample Motor Stroke Eng Value 2 Precision | 41 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_SK1.E2_DC | No | Sample Motor Stroke Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_E3_DC | BXX_DEV1_SK1 | Sample Motor Stroke Eng Value 3 Precision | 41 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_SK1.E3_DC | No | Sample Motor Stroke Eng Value 3 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DEV1_DM1_AI_RT | BXX_DEV1_DM1 | Sample Motor Runtime (Hours) | 28 | Yes | No | 0 | Yes | No | 0 | 0 | h | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_DEV1_DM1.AI_RT | No | Sample Motor Runtime (Hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_DM1_SI_CT | BXX_DEV1_DM1 | Sample Motor Manual Speed Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_DM1.SI_CT | No | Sample Motor Manual Speed Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_DM1_SK_RT | BXX_DEV1_DM1 | Sample Motor Manual Stroke Setpoint | 35 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_DM1.SK_CT | No | Sample Motor Manual Stroke Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_DM1_AO_CV | BXX_DEV1_DM1 | Sample Motor Speed Command | 26 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_DM1.AO_CT | No | Sample Motor Speed Command | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_DM1_AO_SK | BXX_DEV1_DM1 | Sample Motor Stroke Command | 27 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_DM1.AO_SK | No | Sample Motor Stroke Command | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_CV | BXX_DEV1_SI1 | Sample Motor Speed Current Value | 32 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AI_CV | No | Sample Motor Speed Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_ND | BXX_DEV1_SI1 | Sample Motor Speed Min Value Today | 34 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AI_ND | No | Sample Motor Speed Min Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_NP | BXX_DEV1_SI1 | Sample Motor Speed Max Value Today | 34 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AI_NP | No | Sample Motor Speed Max Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_XD | BXX_DEV1_SI1 | Sample Motor Speed Min Value Yesterday | 38 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AI_XD | No | Sample Motor Speed Min Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_XP | BXX_DEV1_SI1 | Sample Motor Speed Max Value Yesterday | 38 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AI_XP | No | Sample Motor Speed Max Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_XM | BXX_DEV1_SI1 | Sample Motor Speed Span Setpoint | 32 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_XM | No | Sample Motor Speed Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_EM | BXX_DEV1_SI1 | Sample Motor Speed Zero Setpoint | 32 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_EM | No | Sample Motor Speed Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_SV | BXX_DEV1_SI1 | Sample Motor Speed Override Value | 33 | No | Yes | 700 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_SV | No | Sample Motor Speed Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_SN_ZA | BXX_DEV1_SI1 | Sample Motor Speed Deviation Alarm Delay | 40 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DEV1_SI1.SN_LO | No | Sample Motor Speed Deviation Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_ZA | BXX_DEV1_SI1 | Sample Motor Speed Deviation Setpoint | 37 | No | Yes | 600 | Yes | No | 0 | 0 | None | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_LL | No | Sample Motor Speed Deviation Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_E3_CV | BXX_DEV1_SI1 | Sample Motor Speed Units 3 | 26 | No | No | 0 | Yes | No | 0 | 0 | mA | 4 | 4 | 20 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 4 | 20 | Linear | BXX | No | BXX_DEV1_SI1.E3_CV | No | Sample Motor Speed Units 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_E2_CV | BXX_DEV1_SI1 | Sample Motor Speed Units 2 | 26 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.E2_CV | No | Sample Motor Speed Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AI_CV | BXX_DEV1_SK1 | Sample Motor Stroke Current Value | 33 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.AI_CV | No | Sample Motor Stroke Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AI_ND | BXX_DEV1_SK1 | Sample Motor Stroke Min Value Today | 35 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.AI_ND | No | Sample Motor Stroke Min Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AI_NP | BXX_DEV1_SK1 | Sample Motor Stroke Max Value Today | 35 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.AI_NP | No | Sample Motor Stroke Max Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AI_XD | BXX_DEV1_SK1 | Sample Motor Stroke Min Value Yesterday | 39 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.AI_XD | No | Sample Motor Stroke Min Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AI_XP | BXX_DEV1_SK1 | Sample Motor Stroke Max Value Yesterday | 39 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.AI_XP | No | Sample Motor Stroke Max Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AO_XM | BXX_DEV1_SK1 | Sample Motor Stroke Span Setpoint | 33 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.AO_XM | No | Sample Motor Stroke Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AO_EM | BXX_DEV1_SK1 | Sample Motor Stroke Zero Setpoint | 33 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.AO_EM | No | Sample Motor Stroke Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AO_SV | BXX_DEV1_SK1 | Sample Motor Stroke Override Value | 34 | No | Yes | 700 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.AO_SV | No | Sample Motor Stroke Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_SN_ZA | BXX_DEV1_SK1 | Sample Motor Stroke Deviation Alarm Delay | 41 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DEV1_SK1.SN_LO | No | Sample Motor Stroke Deviation Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_AO_ZA | BXX_DEV1_SK1 | Sample Motor Stroke Deviation Setpoint | 38 | No | Yes | 600 | Yes | No | 0 | 0 | None | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.AO_LL | No | Sample Motor Stroke Deviation Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_E3_CV | BXX_DEV1_SK1 | Sample Motor Stroke Units 3 | 27 | No | No | 0 | Yes | No | 0 | 0 | mA | 4 | 4 | 20 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 4 | 20 | Linear | BXX | No | BXX_DEV1_SK1.E3_CV | No | Sample Motor Stroke Units 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SK1_E2_CV | BXX_DEV1_SK1 | Sample Motor Stroke Units 2 | 27 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SK1.E2_CV | No | Sample Motor Stroke Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_DEV1_DM1_DI_NM | BXX_DEV1_DM1 | BXX_DEV1_DM1 | 12 | No | No | 0 | Yes | 24 | BXX_DEV1_DM1 | BXX_DEV1_DM1
BXX_DEV1_SI1_DI_NM | BXX_DEV1_SI1 | BXX_DEV1_SI1 | 12 | No | No | 0 | Yes | 24 | BXX_DEV1_SI1 | BXX_DEV1_SI1
BXX_DEV1_SK1_DI_NM | BXX_DEV1_SK1 | BXX_DEV1_SK1 | 12 | No | No | 0 | Yes | 24 | BXX_DEV1_SK1 | BXX_DEV1_SK1
PMP_NAME | $System | Pump Name - Indirect | 20 | No | No | 0 | Yes | 131
PMP_SI_NAME | $System | Pump Feedback Tagname | 21 | No | No | 0 | Yes | 131
PMP_SK_NAME | $System | Stroke Feedback Tagname | 23 | No | No | 0 | Yes | 131
ALRM_PGRP | $System | Pump Alarm Query | 16 | No | No | 0 | Yes | 64 |  | Pump Alarm Query
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_DEV1_DM1_PB_SU_RN | BXX_DEV1_DM1 | Sample Motor Uncomm. Start Dis Reason | 37 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_SU_RN | No | Sample Motor Uncomm. Start Dis Reason
BXX_DEV1_DM1_PB_SF_RN | BXX_DEV1_DM1 | Sample Motor Failed To Start Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_SF_RN | No | Sample Motor Failed To Start Dis Reason
BXX_DEV1_DM1_PB_XF_RN | BXX_DEV1_DM1 | Sample Motor Failed To Stop Dis Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_XF_RN | No | Sample Motor Failed To Stop Dis Reason
BXX_DEV1_DM1_PB_XU_RN | BXX_DEV1_DM1 | Sample Motor Uncomm Stop Disabled Reason | 40 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_XU_RN | No | Sample Motor Uncomm Stop Disabled Reason
BXX_DEV1_DM1_PB_AE_RN | BXX_DEV1_DM1 | Sample Motor Alarms Disabled Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_AE_RN | No | Sample Motor Alarms Disabled Reason
BXX_DEV1_DM1_PB_ES_SR | BXX_DEV1_DM1 | Sample Motor E-Stop Disabled Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_ES_SR | No | Sample Motor E-Stop Disabled Reason
BXX_DEV1_DM1_PB_RA_SR | BXX_DEV1_DM1 | Sample Motor Overload Disabled Reason | 37 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_RA_SR | No | Sample Motor Overload Disabled Reason
BXX_DEV1_DM1_PB_PL_SR | BXX_DEV1_DM1 | Sample Motor Loss of Pressure Disabled Reason | 45 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_PL_SR | No | Sample Motor Loss of Pressure Disabled Reason
BXX_DEV1_DM1_PB_PH_SR | BXX_DEV1_DM1 | Sample Motor High Disch Pressure Disabled Reason | 48 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_PH_SR | No | Sample Motor High Disch Pressure Disabled Reason
BXX_DEV1_DM1_PB_DF_SR | BXX_DEV1_DM1 | Sample Motor Not Ready Disabled Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_DF_SR | No | Sample Motor Not Ready Disabled Reason
BXX_DEV1_DM1_PB_MA_SR | BXX_DEV1_DM1 | Sample Motor Loss of Prime Disabled Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_MA_SR | No | Sample Motor Loss of Prime Disabled Reason
BXX_DEV1_DM1_PB_VM_SR | BXX_DEV1_DM1 | Sample Motor Vacuum Alarm Disabled Reason | 41 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_VM_SR | No | Sample Motor Vacuum Alarm Disabled Reason
BXX_DEV1_DM1_PB_GA_SR | BXX_DEV1_DM1 | Sample Motor Soft Starter/VFD Fault Disabled Reason | 51 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_GA_SR | No | Sample Motor Soft Starter/VFD Fault Disabled Reason
BXX_DEV1_DM1_PB_HA_SR | BXX_DEV1_DM1 | Sample Motor Overtorque Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_HA_SR | No | Sample Motor Overtorque Disabled Reason
BXX_DEV1_DM1_PB_BT_SR | BXX_DEV1_DM1 | Sample Motor Bearing Temp Disabled Reason | 41 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_BT_SR | No | Sample Motor Bearing Temp Disabled Reason
BXX_DEV1_DM1_PB_WA_SR | BXX_DEV1_DM1 | Sample Motor Winding Temp Disabled Reason | 41 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_WA_SR | No | Sample Motor Winding Temp Disabled Reason
BXX_DEV1_DM1_PB_TH_SR | BXX_DEV1_DM1 | Sample Motor High Temp Disabled Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_TH_SR | No | Sample Motor High Temp Disabled Reason
BXX_DEV1_DM1_PB_TA_SR | BXX_DEV1_DM1 | Sample Motor Temp/Leak Disabled Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_TA_SR | No | Sample Motor Temp/Leak Disabled Reason
BXX_DEV1_DM1_PB_FA_SR | BXX_DEV1_DM1 | Sample Motor No Flow Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_DM1_PB_FA_SR | No | Sample Motor No Flow Disabled Reason
BXX_DEV1_SI1_PB_ZA_RN | BXX_DEV1_SI1 | Sample Motor Speed Deviation Disabled Reason | 44 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_SI1_PB_ZA_RN | No | Sample Motor Speed Deviation Disabled Reason
BXX_DEV1_SK1_PB_ZA_RN | BXX_DEV1_SK1 | Sample Motor Stroke Deviation Disabled Reason | 45 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_SK1_PB_ZA_RN | No | Sample Motor Stroke Deviation Disabled Reason
:IndirectDisc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DI_SC | $System | Pump Feedback On Scan Indirect Tag | 34 | No | 0 | No
PMP_DM_DI_AA | $System | Pump Plant Auto Mode Status - Indirect | 38 | No | 0 | No
PMP_DM_DI_AS | $System | Pump Plant Auto Stroke Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_CL | $System | Pump Control Mode - Indirect | 28 | No | 0 | No
PMP_DM_DI_MS | $System | Pump Plant Manual Stroke Status - Indirect | 42 | No | 0 | No
PMP_DM_DI_PM | $System | Pump Plant Manual Mode Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_SK | $System | Pump Stroke Control Mode - Indirect | 35 | No | 0 | No
PMP_DM_DI_SS | $System | Pump Running Status - Indirect | 30 | No | 0 | No
PMP_DM_PB_AR | $System | Pump Alarm Ack. Req. - Indirect | 31 | No | 0 | No
PMP_DM_PB_MS | $System | Pump Plant Manual Stroke Req. - Indirect | 40 | No | 0 | No
PMP_DM_PB_PM | $System | Pump Plant Manual Mode Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PP | $System | Pump Plant Manual Stop Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PT | $System | Pump Plant Manual Start Req. - Indirect | 39 | No | 0 | No
PMP_DM_PB_RT | $System | Pump Runtime Reset - Indirect | 29 | No | 0 | No
PMP_PB_AE | $System | Pump Alarm Enable Pushbutton Indirect Tag | 41 | No | 0 | No
PMP_PB_ER | $System | Pump Speed Signal Error Enable Indirect Tag | 43 | No | 0 | No
PMP_PB_SC | $System | Pump Speed Feedback Scan Enable Indirect Tag | 44 | No | 0 | No
PMP_PB_SF | $System | Pump Fail To Start Enable Ind. Tag | 34 | No | 0 | No
PMP_PB_SM | $System | Pump Simulate Alarms Pushbutton Indirect Tag | 44 | No | 0 | No
PMP_PB_SU | $System | Pump Fail To Stop Enable Ind. Tag | 33 | No | 0 | No
PMP_PB_SV | $System | Pump Simulate Feedback Indirect Tag | 35 | No | 0 | No
PMP_PB_XF | $System | Pump Uncommanded Start Enable Ind. Tag | 38 | No | 0 | No
PMP_PB_XU | $System | Pump Uncommanded Stop Enable Ind. Tag | 37 | No | 0 | No
PMP_PB_ZA | $System | Pump Deviation Alarm Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_DA_ER | $System | Stroke Feedback Signal Error Indirect Tag | 41 | No | 0 | No
PMP_SK_DI_SC | $System | Stroke Feedback on Scan Indirect Tag | 36 | No | 0 | No
PMP_SK_PB_ER | $System | Stroke Feedback Signal Error Enable Indirect Tag | 48 | No | 0 | No
PMP_SK_PB_SC | $System | Stroke Feedback Scan Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_PB_SV | $System | Stroke Feedback Simulate Value Indirect Tag | 43 | No | 0 | No
PMP_SK_PB_ZA | $System | Stroke Feedback Deviation Alarm Enable Ind. Tag | 47 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DC2 | $System | Pump Signal Engineering Units 2 - Indirect | 42 | No | 0 | No
PMP_DC3 | $System | Pump Signal Engineering Units 3 - Indirect | 42 | No | 0 | No
PMP_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_AI_CV | $System | Pump Signal Feedback Indirect Tag | 33 | No | 0 | No
PMP_AI_VI | $System | Pump Signal Feedback Visible Values Ind. Tag | 44 | No | 0 | No
PMP_AO_SV | $System | Pump Feedback Override Value Indirect Tag | 41 | No | 0 | No
PMP_AO_ZA | $System | Deviation Alarm Setpoint Indirect Tag | 37 | No | 0 | No
PMP_DMAI_RT | $System | Pump Runtime - Indirect | 23 | No | 0 | No
PMP_E1_EM | $System | Pump Feedback Zero Indirect Tag | 31 | No | 0 | No
PMP_E1_XM | $System | Pump Feedback Span Indirect Tag | 31 | No | 0 | No
PMP_E2_CV | $System | Pump Feedback Secondary Eng Value Ind. Tag | 42 | No | 0 | No
PMP_E3_CV | $System | Pump Feedback Tertiary Eng Value Indirect Tag | 45 | No | 0 | No
PMP_SIAO_CT | $System | VFD Pump Manual Speed Setpoint - Indirect Analog | 48 | No | 0 | No
PMP_SK_DC2 | $System | Pump Stroke Signal Engineering Units 2 - Indirect | 49 | No | 0 | No
PMP_SK_DC3 | $System | Pump Stroke Signal Engineering Units 3 - Indirect | 49 | No | 0 | No
PMP_SK_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_SK_AI_CV | $System | Stroke Feedback Indirect Tag | 28 | No | 0 | No
PMP_SK_AI_VI | $System | Stroke Feedback Number of Visible Units Ind. Tag | 48 | No | 0 | No
PMP_SK_AO_CT | $System | VFD Pump Stroke Setpoint - Indirect Analog | 42 | No | 0 | No
PMP_SK_AO_SV | $System | Stroke Feedback Simulation Value Indirect Tag | 45 | No | 0 | No
PMP_SK_AO_ZA | $System | Stroke Deviation Setpoint Indirect Tag | 38 | No | 0 | No
PMP_SK_E1_EM | $System | Stroke Feedback Zero Scale Indirect Tag | 39 | No | 0 | No
PMP_SK_E1_XM | $System | Stroke Feedback Spane Indirect Tag | 34 | No | 0 | No
PMP_SK_E2_CV | $System | Stroke Feedback Secondary Units Indirect Tag | 44 | No | 0 | No
PMP_SK_E3_CV | $System | Stroke Feedback Tertiary Units Indirect Tag | 43 | No | 0 | No
PMP_SK_SN_ZA | $System | Stroke Deviation Alarm Delay Indirect Tag | 41 | No | 0 | No
PMP_SN_ZA | $System | Deviation Alarm Delay Time Indirect Tag | 39 | No | 0 | No
:IndirectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_SRV | $System | Pump Alarm Group Server Indirect Tag | 36 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
PMP_DM_GRP | $System | Pump Group - Indirect | 21

## SCADA_DEV_VLV
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DEV1_FV1 | BXX | Sample Valve | 12 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms Group | 25 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1 | BXX_DEV1_FV1 | Sample Valve Position | 21 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DEV1_FV1_DI_AD | BXX_DSAB | Sample Valve Disabled Alarm | 27 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_DEV1_FV1.DI_AD | No | Sample Valve Disabled Alarm | 0 | 0
BXX_DEV1_FV1_DI_CL | BXX_DEV1_FV1 | Sample Valve Control Mode | 25 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.DI_CL.eng | No | Sample Valve Control Mode | 0 | 0
BXX_DEV1_FV1_DI_OD | BXX_DEV1_FV1 | Sample Valve Open Status | 24 | Yes | Yes | 700 | Yes | Off | Stopped | Running | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.DI_OD.eng | No | Sample Valve Open Status | 0 | 0
BXX_DEV1_FV1_DI_CD | BXX_DEV1_FV1 | Sample Valve Closed Status | 26 | Yes | Yes | 700 | Yes | Off | Stopped | Running | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.DI_CD.eng | No | Sample Valve Closed Status | 0 | 0
BXX_DEV1_FV1_DI_AA | BXX_DEV1_FV1 | Sample Valve Auto Mode | 22 | No | Yes | 700 | Yes | Off | PLT-MAN | AUTO | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.DI_AA | No | Sample Valve Auto Mode | 0 | 0
BXX_DEV1_FV1_DI_PM | BXX_DEV1_FV1 | Sample Valve Plant Manual Mode | 30 | No | Yes | 700 | Yes | Off | AUTO | PLT-MAN | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.DI_PM | No | Sample Valve Plant Manual Mode | 0 | 0
BXX_DEV1_FV1_PB_PM | BXX_DEV1_FV1 | Sample Valve Plant Manual Mode RQ | 33 | No | Yes | 600 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_PM | No | Sample Valve Plant Manual Mode RQ | 0 | 0
BXX_DEV1_FV1_PB_PO | BXX_DEV1_FV1 | Sample Valve Plant Manual Open | 30 | No | Yes | 600 | Yes | Off | Normal | Start | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_PO | No | Sample Valve Plant Manual Open | 0 | 0
BXX_DEV1_FV1_PB_PC | BXX_DEV1_FV1 | Sample Valve Plant Manual Close | 31 | No | Yes | 600 | Yes | Off | Normal | Stop | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_PC | No | Sample Valve Plant Manual Close | 0 | 0
BXX_DEV1_FV1_PB_AR | BXX_DEV1_FV1 | Sample Valve Alarm Ack | 22 | No | Yes | 600 | Yes | Off | Normal | Ack | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_AR | No | Sample Valve Alarm Ack | 0 | 0
BXX_DEV1_FV1_DA_SF | BXX_DEV1_FV1 | Sample Valve Failed To Open | 27 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_DEV1_FV1.DA_SF | No | Sample Valve Failed To Open | 0 | 0
BXX_DEV1_FV1_DA_XF | BXX_DEV1_FV1 | Sample Valve Failed To Close | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_DEV1_FV1.DA_XF | No | Sample Valve Failed To Close | 0 | 0
BXX_DEV1_FV1_DA_SU | BXX_DEV1_FV1 | Sample Valve Uncommanded Open | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 53 | Direct | BXX | No | BXX_DEV1_FV1.DA_SU | No | Sample Valve Uncommanded Open | 0 | 0
BXX_DEV1_FV1_DA_XU | BXX_DEV1_FV1 | Sample Valve Uncommanded Close | 30 | No | No | 0 | Yes | Off | Normal | Alarm | On | 54 | Direct | BXX | No | BXX_DEV1_FV1.DA_XU | No | Sample Valve Uncommanded Close | 0 | 0
BXX_DEV1_FV1_PB_SU | BXX_DEV1_FV1 | Sample Valve Uncomm Open Alarm En | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_SU.RE | No | Sample Valve Uncomm Open Alarm En | 0 | 0
BXX_DEV1_FV1_PB_SF | BXX_DEV1_FV1 | Sample Valve Failed To Open Alarm En | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_SF.RE | No | Sample Valve Failed To Open Alarm En | 0 | 0
BXX_DEV1_FV1_PB_XF | BXX_DEV1_FV1 | Sample Valve Failed To Close Alarm En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_XF.RE | No | Sample Valve Failed To Close Alarm En | 0 | 0
BXX_DEV1_FV1_PB_XU | BXX_DEV1_FV1 | Sample Valve Uncomm. Close Alarm En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_XU.RE | No | Sample Valve Uncomm. Close Alarm En | 0 | 0
BXX_DEV1_FV1_PB_SM | BXX_DEV1_FV1 | Sample Valve Simulate Alarms PB | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_SM | No | Sample Valve Simulate Alarms PB | 0 | 0
BXX_DEV1_FV1_PB_AE | BXX_DEV1_FV1 | Sample Valve Alarm Enable | 25 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_AE.RE | No | Sample Valve Alarm Enable | 0 | 0
BXX_DEV1_FV1_PB_SU_DE | BXX_DEV1_FV1 | Sample Valve Uncomm Open Dialer En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_SU.DE | No | Sample Valve Uncomm Open Dialer En | 0 | 0
BXX_DEV1_FV1_PB_SF_DE | BXX_DEV1_FV1 | Sample Valve Failed To Open Dialer En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_SF.DE | No | Sample Valve Failed To Open Dialer En | 0 | 0
BXX_DEV1_FV1_PB_XF_DE | BXX_DEV1_FV1 | Sample Valve Failed to Close Dialer En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_XF.DE | No | Sample Valve Failed to Close Dialer En | 0 | 0
BXX_DEV1_FV1_PB_XU_DE | BXX_DEV1_FV1 | Sample Valve Uncomm Close Dialer En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_XU.DE | No | Sample Valve Uncomm Close Dialer En | 0 | 0
BXX_DEV1_FV1_PB_AE_DE | BXX_DEV1_FV1 | Sample Valve Alarms Dialer Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_AE.DE | No | Sample Valve Alarms Dialer Enable | 0 | 0
BXX_DEV1_FV1_PB_SU_SR | BXX_DEV1_FV1 | Sample Valve Uncomm. Open Sup En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_SU.SR | No | Sample Valve Uncomm. Open Sup En | 0 | 0
BXX_DEV1_FV1_PB_SF_SR | BXX_DEV1_FV1 | Sample Valve Failed To Open Sup En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_SF.SR | No | Sample Valve Failed To Open Sup En | 0 | 0
BXX_DEV1_FV1_PB_XF_SR | BXX_DEV1_FV1 | Sample Valve Failed To Open Sup En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_XF.SR | No | Sample Valve Failed To Open Sup En | 0 | 0
BXX_DEV1_FV1_PB_XU_SR | BXX_DEV1_FV1 | Sample Valve Uncomm. Open Sup En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_XU.SR | No | Sample Valve Uncomm. Open Sup En | 0 | 0
BXX_DEV1_FV1_PB_AE_SR | BXX_DEV1_FV1 | Sample Valve Alarms Sup Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.PB_AE.SR | No | Sample Valve Alarms Sup Enable | 0 | 0
BXX_MXV1_ZI1_DI_SC | BXX_MXV1_ZI1 | Sample Valve Position Scan Status | 33 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_MXV1_ZI1.DI_SC | No | Sample Valve Position Scan Status | 0 | 0
BXX_MXV1_ZI1_PB_SC | BXX_MXV1_ZI1 | Sample Valve Position Scan Enable | 33 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_MXV1_ZI1.PB_SC | No | Sample Valve Position Scan Enable | 0 | 0
BXX_MXV1_ZI1_DA_ER | BXX_MXV1_ZI1 | Sample Valve Position Signal Error | 34 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_MXV1_ZI1.DA_ER | No | Sample Valve Position Signal Error | 0 | 0
BXX_MXV1_ZI1_PB_ER | BXX_MXV1_ZI1 | Sample Valve Position Sig Error Alarm En | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_MXV1_ZI1.PB_ER.RE | No | Sample Valve Position Sig Error Alarm En | 0 | 0
BXX_MXV1_ZI1_PB_SV | BXX_MXV1_ZI1 | Sample Valve Position Override Enable | 37 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_MXV1_ZI1.PB_SV | No | Sample Valve Position Override Enable | 0 | 0
BXX_MXV1_ZI1_DA_ZA | BXX_MXV1_ZI1 | Sample Valve Position Deviation Alarm | 37 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_MXV1_ZI1.DA_ZA | No | Sample Valve Position Deviation Alarm | 0 | 0
BXX_MXV1_ZI1_PB_ZA | BXX_MXV1_ZI1 | Sample Valve Position Deviation Alarm En | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_MXV1_ZI1.PB_ZA.RE | No | Sample Valve Position Deviation Alarm En | 0 | 0
BXX_MXV1_ZI1_PB_ZA_DE | BXX_MXV1_ZI1 | Sample Valve Deviation Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_MXV1_ZI1.PB_ZA.DE | No | Sample Valve Deviation Dialer Enable | 0 | 0
BXX_MXV1_ZI1_PB_ZA_SR | BXX_MXV1_ZI1 | Sample Valve Deviation Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_MXV1_ZI1.PB_ZA.SR | No | Sample Valve Deviation Sup Enable | 0 | 0
BXX_DEV1_FV1_DA_GA | BXX_DEV1_FV1 | Sample Valve General Alarm | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_DEV1_FV1.DA_GA.eng | No | Sample Valve General Alarm | 0 | 0
BXX_DEV1_FV1_PB_GA_RE | BXX_DEV1_FV1 | Sample Valve General Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.DA_GA.RE | No | Sample Valve General Alarm Enable | 0 | 0
BXX_DEV1_FV1_PB_GA_DE | BXX_DEV1_FV1 | Sample Valve General Alarm Dialer Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.DA_GA.DE | No | Sample Valve General Alarm Dialer Enable | 0 | 0
BXX_DEV1_FV1_PB_GA_SR | BXX_DEV1_FV1 | Sample Valve General Alarm Sup Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_FV1.DA_GA.SR | No | Sample Valve General Alarm Sup Enable | 0 | 0
:MemoryInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinValue | MaxValue | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
VLV_VIS1 | $System | Visibility Control for Analog Valve Feedback |  | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 1 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Visibility Control for Analog Valve Feedback | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VLV_VIS2 | $System | Visibility Control for Analog Valve Control |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 1 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Visibility Control for Analog Valve Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VLV_VIS3 | $System | Visibility Control for Discrete Valve Features |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 1 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Visibility Control for Discrete Valve Features | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_MXV1_ZI1_AI_VI | BXX_MXV1_ZI1 | Sample Valve Position Number of Vis Eng Values | 46 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_MXV1_ZI1.AI_VI | No | Sample Valve Position Number of Vis Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AI_DC | BXX_MXV1_ZI1 | Sample Valve Position Precision | 31 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_MXV1_ZI1.AI_DC | No | Sample Valve Position Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_E2_DC | BXX_MXV1_ZI1 | Sample Valve Position Eng Value 2 Precision | 43 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_MXV1_ZI1.E2_DC | No | Sample Valve Position Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_E3_DC | BXX_MXV1_ZI1 | Sample Valve Position Eng Value 3 Precision | 43 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_MXV1_ZI1.E3_DC | No | Sample Valve Position Eng Value 3 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DEV1_FV1_CV_CT | BXX_DEV1_FV1 | Sample Valve Manual Position Setpoint | 37 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_FV1.CV_CT | No | Sample Valve Manual Position Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_FV1_AO_CV | BXX_DEV1_FV1 | Sample Valve Position Command | 29 | No | No | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 1 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_FV1.AO_CT | No | Sample Valve Position Command | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AI_CV | BXX_MXV1_ZI1 | Sample Valve Position Current Value | 35 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 1 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.AI_CV | No | Sample Valve Position Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AI_ND | BXX_MXV1_ZI1 | Sample Valve Position Min Value Today | 37 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 1 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.AI_ND | No | Sample Valve Position Min Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AI_NP | BXX_MXV1_ZI1 | Sample Valve Position Max Value Today | 37 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 1 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.AI_NP | No | Sample Valve Position Max Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AI_XD | BXX_MXV1_ZI1 | Sample Valve Position Min Value Yesterday | 41 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.AI_XD | No | Sample Valve Position Min Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AI_XP | BXX_MXV1_ZI1 | Sample Valve Position Max Value Yesterday | 41 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.AI_XP | No | Sample Valve Position Max Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AO_XM | BXX_MXV1_ZI1 | Sample Valve Position Span Setpoint | 35 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.AO_XM | No | Sample Valve Position Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AO_EM | BXX_MXV1_ZI1 | Sample Valve Position Zero Setpoint | 35 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.AO_EM | No | Sample Valve Position Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AO_SV | BXX_MXV1_ZI1 | Sample Valve Position Override Value | 36 | No | Yes | 700 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.AO_SV | No | Sample Valve Position Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_SN_ZA | BXX_MXV1_ZI1 | Sample Valve Position Deviation Alarm Delay | 43 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_MXV1_ZI1.SN_LO | No | Sample Valve Position Deviation Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_AO_ZA | BXX_MXV1_ZI1 | Sample Valve Position Deviation Setpoint | 40 | No | Yes | 600 | Yes | No | 0 | 0 | None | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.AO_LL | No | Sample Valve Position Deviation Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_E3_CV | BXX_MXV1_ZI1 | Sample Valve Position Units 3 | 29 | No | No | 0 | Yes | No | 0 | 0 | mA | 4 | 4 | 20 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 4 | 20 | Linear | BXX | No | BXX_MXV1_ZI1.E3_CV | No | Sample Valve Position Units 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_MXV1_ZI1_E2_CV | BXX_MXV1_ZI1 | Sample Valve Position Units 2 | 29 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_MXV1_ZI1.E2_CV | No | Sample Valve Position Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_DEV1_FV1_DI_NM | BXX_DEV1_FV1 | BXX_DEV1_FV1 | 12 | No | No | 0 | Yes | 24 | BXX_DEV1_FV1 | BXX_DEV1_FV1
BXX_MXV1_ZI1_DI_NM | BXX_MXV1_ZI1 | BXX_MXV1_ZI1 | 12 | No | No | 0 | Yes | 24 | BXX_MXV1_ZI1 | BXX_MXV1_ZI1
VLV_NAME | $System | Valve Name - Indirect | 21 | No | No | 0 | Yes | 64
VLV_FBNAME | $System | Valve Feedback Tag Name | 23 | No | No | 0 | Yes | 64
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_DEV1_FV1_PB_SU_RN | BXX_DEV1_FV1 | Sample Valve Uncomm. Start Dis Reason | 37 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FV1_PB_SU_RN | No | Sample Valve Uncomm. Start Dis Reason
BXX_DEV1_FV1_PB_SF_RN | BXX_DEV1_FV1 | Sample Valve Failed To Start Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FV1_PB_SF_RN | No | Sample Valve Failed To Start Dis Reason
BXX_DEV1_FV1_PB_XF_RN | BXX_DEV1_FV1 | Sample Valve Failed To Stop Dis Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FV1_PB_XF_RN | No | Sample Valve Failed To Stop Dis Reason
BXX_DEV1_FV1_PB_XU_RN | BXX_DEV1_FV1 | Sample Valve Uncomm Stop Disabled Reason | 40 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FV1_PB_XU_RN | No | Sample Valve Uncomm Stop Disabled Reason
BXX_DEV1_FV1_PB_AE_RN | BXX_DEV1_FV1 | Sample Valve Alarms Disabled Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FV1_PB_AE_RN | No | Sample Valve Alarms Disabled Reason
BXX_DEV1_FV1_PB_GA_SR | BXX_DEV1_FV1 | Sample Valve General Alarm Disabled Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DEV1_FV1_PB_GA_SR | No | Sample Valve General Alarm Disabled Reason
:IndirectDisc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
VLV_DI_SC | $System | Valve Feedback on Scan Indirect Tag | 35 | No | 0 | No
VLV_FX_DI_AA | $System | Valve Plant Auto Mode Status - Indirect | 39 | No | 0 | No
VLV_FX_DI_CD | $System | Valve Closed Status - Indirect | 30 | No | 0 | No
VLV_FX_DI_CL | $System | Valve Control Mode - Indirect | 29 | No | 0 | No
VLV_FX_DI_OD | $System | Valve Opened Status - Indirect | 30 | No | 0 | No
VLV_FX_DI_PM | $System | Valve Plant Manual Mode Status - Indirect | 41 | No | 0 | No
VLV_FX_PB_AR | $System | Valve Alarm Acknowledge Request - Indirect | 42 | No | 0 | No
VLV_FX_PB_PC | $System | Valve Plant Manual Close Request - Indirect | 43 | No | 0 | No
VLV_FX_PB_PM | $System | Valve Plant Manual Mode Request - Indirect | 42 | No | 0 | No
VLV_FX_PB_PO | $System | Valve Plant Open Request - Indirect | 35 | No | 0 | No
VLV_PB_AE | $System | Valve Alarm Enable PB Indirect Tag | 34 | No | 0 | No
VLV_PB_ER | $System | Valve Feedback Signal Error Alarm Enable Ind. Tag | 49 | No | 0 | No
VLV_PB_SC | $System | Valve Feedback On Scan PB Indirect Tag | 38 | No | 0 | No
VLV_PB_SF | $System | Valve Fail to Open Alarm Enable PB Indirect Tag | 47 | No | 0 | No
VLV_PB_SM | $System | Valve Simulate Alarms PB Indirect Tag | 37 | No | 0 | No
VLV_PB_SU | $System | Valve Uncommanded Open Alarm En PB Indirect Tag | 47 | No | 0 | No
VLV_PB_SV | $System | Simulate Valve Feedback PB Indirect Tag | 39 | No | 0 | No
VLV_PB_XF | $System | Valve Fail to Close Alarm En PB Indirect Tag | 44 | No | 0 | No
VLV_PB_XU | $System | Valve Uncommanded Close Alarm En PB Indirect Tag | 48 | No | 0 | No
VLV_PB_ZA | $System | Valve Feedback Deviation Alarm En PB Indirect Tag | 49 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
VLV_DC2 | $System | Valve Feedback Secondary Units Presision Ind. Tag | 49 | No | 0 | No
VLV_DC3 | $System | Valve Feedback Tertiary Units Presision Ind. Tag | 48 | No | 0 | No
VLV_DEC | $System | Valve Feedback Presision Ind. Tag | 33 | No | 0 | No
VLV_AI_CV | $System | Valve Position Feedback Indirect Tag | 36 | No | 0 | No
VLV_AI_VI | $System | Valve Feedback Number of Visible Units Ind. Tag | 47 | No | 0 | No
VLV_AO_SV | $System | Valve Feedback Simulation Value Indirect Tag | 44 | No | 0 | No
VLV_AO_ZA | $System | Valve Deviation Alarm Setpoint Indirect Tag | 43 | No | 0 | No
VLV_E1_EM | $System | Valve Feedback Engineering Zero Indirect Tag | 44 | No | 0 | No
VLV_E1_XM | $System | Valve Feedback Span Indirect Tag | 32 | No | 0 | No
VLV_E2_CV | $System | Valve Feedback Secondary Units Indirect Tag | 43 | No | 0 | No
VLV_E3_CV | $System | Valve Feedback Tertiary Units Indirect Tag | 42 | No | 0 | No
VLV_MV_AO_CT | $System | Modulating Valve Manual Setpoint Entry - Indirect | 49 | No | 0 | No
VLV_SN_ZA | $System | Valve Feedback Deviation Alarm Delay Time Ind. Tag | 50 | No | 0 | No
:IndirectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
VLV_SRV | $System | Valve Alarm Server Indirect Tag | 31 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
VLV_FX_GRP | $System | Valve Group - Indirect | 22

## SCADA_DEV_ATS
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_ATS1_SG1 | BXXGEN1DE1 | Sample ATS | 10 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms Group | 25 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_ATS1_SG1_DI_AD | BXX_DSAB | Sample ATS Disabled Alarm | 25 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_ATS1_SG1.DI_AD | No | Sample ATS Disabled Alarm | 0 | 0
BXX_ATS1_SG1_DI_CL | BXX_ATS1_SG1 | Sample ATS Control Mode | 23 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DI_CL.eng | No | Sample ATS Control Mode | 0 | 0
BXX_ATS1_SG1_DI_JN | BXX_ATS1_SG1 | Sample ATS Normal Power | 23 | No | Yes | 700 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DI_JN.eng | No | Sample ATS Normal Power | 0 | 0
BXX_ATS1_SG1_DA_JE | BXX_ATS1_SG1 | Sample ATS On Emergency Power | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_ATS1_SG1.DA_JE.eng | No | Sample ATS On Emergency Power | 0 | 0
BXX_ATS1_SG1_PB_AR | BXX_ATS1_SG1 | Sample ATS Alarm Ack | 20 | No | Yes | 600 | Yes | Off | Normal | Ack | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_AR | No | Sample ATS Alarm Ack | 0 | 0
BXX_ATS1_SG1_PB_RT | BXX_ATS1_SG1 | Sample ATS Runtime Reset | 24 | No | Yes | 600 | Yes | Off | Normal | Reset | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_RT | No | Sample ATS Runtime Reset | 0 | 0
BXX_ATS1_SG1_PB_PO | BXX_ATS1_SG1 | Sample ATS Start Test Request | 29 | No | Yes | 600 | Yes | Off | Normal | Start | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_PO | No | Sample ATS Start Test Request | 0 | 0
BXX_ATS1_SG1_PB_PC | BXX_ATS1_SG1 | Sample ATS Stop Test Request | 28 | No | Yes | 600 | Yes | Off | Normal | Stop | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_PC | No | Sample ATS Stop Test Request | 0 | 0
BXX_ATS1_SG1_DA_JR | BXX_ATS1_SG1 | Sample ATS Failed To Transfer | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_ATS1_SG1.DA_JR | No | Sample ATS Failed To Transfer | 0 | 0
BXX_ATS1_SG1_DA_RM | BXX_ATS1_SG1 | Sample ATS Not in Auto | 22 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_ATS1_SG1.DA_RM | No | Sample ATS Not in Auto | 0 | 0
BXX_ATS1_SG1_PB_JR | BXX_ATS1_SG1 | Sample ATS Failed To Xfer En | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_JR.RE | No | Sample ATS Failed To Xfer En | 0 | 0
BXX_ATS1_SG1_PB_RM | BXX_ATS1_SG1 | Sample ATS Not in Auto Alarm En | 31 | No | No | 0 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_RM.RE | No | Sample ATS Not in Auto Alarm En | 0 | 0
BXX_ATS1_SG1_PB_SM | BXX_ATS1_SG1 | Sample ATS Simulate Alarms PB | 29 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_SM | No | Sample ATS Simulate Alarms PB | 0 | 0
BXX_ATS1_SG1_PB_AE | BXX_ATS1_SG1 | Sample ATS Alarm Enable | 23 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_AE.RE | No | Sample ATS Alarm Enable | 0 | 0
BXX_ATS1_SG1_PB_JR_DE | BXX_ATS1_SG1 | Sample ATS Failed To Xfer Dialer En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_JR.DE | No | Sample ATS Failed To Xfer Dialer En | 0 | 0
BXX_ATS1_SG1_PB_RM_DE | BXX_ATS1_SG1 | Sample ATS Not In Auto Dialer En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_RM.DE | No | Sample ATS Not In Auto Dialer En | 0 | 0
BXX_ATS1_SG1_PB_AE_DE | BXX_ATS1_SG1 | Sample ATS Alarms Dialer Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_AE.DE | No | Sample ATS Alarms Dialer Enable | 0 | 0
BXX_ATS1_SG1_PB_JR_SR | BXX_ATS1_SG1 | Sample ATS Failed To Xfer Sup En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_JR.SR | No | Sample ATS Failed To Xfer Sup En | 0 | 0
BXX_ATS1_SG1_PB_RM_SR | BXX_ATS1_SG1 | Sample ATS Not In Auto Sup En | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_RM.SR | No | Sample ATS Not In Auto Sup En | 0 | 0
BXX_ATS1_SG1_PB_AE_SR | BXX_ATS1_SG1 | Sample ATS Alarms Sup Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_AE.SR | No | Sample ATS Alarms Sup Enable | 0 | 0
BXX_ATS1_SG1_PB_JE_RE | BXX_ATS1_SG1 | Sample ATS On Emergency Power Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DA_JE.RE | No | Sample ATS On Emergency Power Enable | 0 | 0
BXX_ATS1_SG1_PB_JE_DE | BXX_ATS1_SG1 | Sample ATS On Emergency Power Dialer Enable | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DA_JE.DE | No | Sample ATS On Emergency Power Dialer Enable | 0 | 0
BXX_ATS1_SG1_PB_JE_SR | BXX_ATS1_SG1 | Sample ATS On Emerg Power Sup Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DA_JE.SR | No | Sample ATS On Emerg Power Sup Enable | 0 | 0
:IOInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_ATS1_SG1_AI_TD | BXX_ATS1_SG1 | Sample ATS Transfers Today | 26 | No | No | 0 | Yes | No | 0 | 0 | Starts | 0 | 0 | 1000000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_ATS1_SG1.AI_TD | No | Sample ATS Transfers Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_ATS1_SG1_AI_MT | BXX_ATS1_SG1 | Sample ATS Transfers This Month | 31 | No | No | 0 | Yes | No | 0 | 0 | Starts | 0 | 0 | 1000000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_ATS1_SG1.AI_MT | No | Sample ATS Transfers This Month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_ATS1_SG1_AI_MX | BXX_ATS1_SG1 | Sample ATS Total Transfers | 26 | Yes | No | 0 | Yes | No | 0 | 0 | Starts | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_ATS1_SG1.AI_MX | No | Sample ATS Total Transfers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_ATS1_SG1_AI_RT | BXX_ATS1_SG1 | Sample ATS Hours on Emerg. Power | 32 | Yes | No | 0 | Yes | No | 0 | 0 | h | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_ATS1_SG1.AI_RT | No | Sample ATS Hours on Emerg. Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_ATS1_SG1_DI_NM | BXX_ATS1_SG1 | BXX_ATS1_SG1 | 12 | No | No | 0 | Yes | 24 | BXX_ATS1_SG1 | BXX_ATS1_SG1
ATS_NAME | $System | ATS Name | 8 | No | No | 0 | Yes | 64
:IOMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_ATS1_SG1_PB_SF_RN | BXX_ATS1_SG1 | Sample ATS Failed To Start Dis Reason | 37 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_ATS1_SG1_PB_SF_RN | No | Sample ATS Failed To Start Dis Reason
BXX_ATS1_SG1_PB_XF_RN | BXX_ATS1_SG1 | Sample ATS Failed To Stop Dis Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_ATS1_SG1_PB_XF_RN | No | Sample ATS Failed To Stop Dis Reason
BXX_ATS1_SG1_PB_AE_RN | BXX_ATS1_SG1 | Sample ATS Alarms Disabled Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_ATS1_SG1_PB_AE_RN | No | Sample ATS Alarms Disabled Reason
BXX_ATS1_SG1_PB_JE_SR | BXX_ATS1_SG1 | Sample ATS on Emerg Power Disabled Reason | 41 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_ATS1_SG1_PB_JE_SR | No | Sample ATS on Emerg Power Disabled Reason
:IndirectDisc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ATS_DA_JE | $System | ATS On Emergency Power Indirect Tag |  | No | 0 | No
ATS_DI_CL | $System | ATS Control Mode Indirect Tag |  | No | 0 | No
ATS_DI_JN | $System | ATS on Normal Power Indirect Tag |  | No | 0 | No
ATS_PB_AE | $System | ATS Alarm Enable Indirect Tag |  | No | 0 | No
ATS_PB_JR | $System | ATS Fail to Transfer Enable PB Indirect Tag |  | No | 0 | No
ATS_PB_PP | $System | ATS Plant Manual Stop Req. - Indirect |  | No | 0 | No
ATS_PB_PT | $System | ATS Plant Manual Start Req. - Indirect |  | No | 0 | No
ATS_PB_RM | $System | ATS Fail to Transfer Enable PB Indirect Tag |  | No | 0 | No
ATS_PB_RT | $System | ATS Runtime Reset Indirect Tag |  | No | 0 | No
ATS_PB_SM | $System | ATS Simulate Alarms PB Indirect Tag |  | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ATS_AI_RT | $System | ATS Runtime Indirect Tag | 24 | No | 0 | No

## SCADA_DEV_GEN
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_GEN1_DE1 | BXX | Sample Generator | 16 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms Group | 25 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryDisc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
ATS_VIS1 | $System | ATS Visible on Generator Pop-up Control | 39 | No | No | 0 | Yes | On |  |  | None | 1 | Duty Select Info Button Visibility | 0 | 0
ATS_VIS2 | $System | Controls Visiblity of Test Buttons | 34 | No | No | 0 | Yes | On |  |  | None | 1 | Duty Select Info Button Visibility | 0 | 0
:IODisc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_GEN1_DE1_DI_AD | BXX_DSAB | Sample Generator Disabled Alarm | 31 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_GEN1_DE1.DI_AD | No | Sample Generator Disabled Alarm | 0 | 0
BXX_GEN1_DE1_DI_CL | BXX_GEN1_DE1 | Sample Generator Control Mode | 29 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DI_CL.eng | No | Sample Generator Control Mode | 0 | 0
BXX_GEN1_DE1_DI_SS | BXX_GEN1_DE1 | Sample Generator Running Status | 31 | No | No | 0 | Yes | Off | Stopped | Running | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DI_SS.eng | No | Sample Generator Running Status | 0 | 0
BXX_GEN1_DE1_DA_SS | BXX_GEN1_DE1 | Sample Generator Running Alarm | 30 | Yes | No | 0 | Yes | Off | Stopped | Running | On | 63 | Direct | BXX | No | BXX_GEN1_DE1.DA_SS.eng | No | Sample Generator Running Alarm | 0 | 0
BXX_GEN1_DE1_DA_ES | BXX_GEN1_DE1 | Sample Generator E-Stop | 23 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_GEN1_DE1.DA_ES.eng | No | Sample Generator E-Stop | 0 | 0
BXX_GEN1_DE1_DA_JW | BXX_GEN1_DE1 | Sample Generator Warning | 24 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_GEN1_DE1.DA_JW.eng | No | Sample Generator Warning | 0 | 0
BXX_GEN1_DE1_DA_GA | BXX_GEN1_DE1 | Sample Generator Fault | 22 | No | No | 0 | Yes | Off | Normal | Alarm | On | 95 | Direct | BXX | No | BXX_GEN1_DE1.DA_GA.eng | No | Sample Generator Fault | 0 | 0
BXX_GEN1_DE1_PB_RT | BXX_GEN1_DE1 | Sample Generator Runtime Reset | 30 | No | Yes | 600 | Yes | Off | Normal | Reset | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_RT | No | Sample Generator Runtime Reset | 0 | 0
BXX_GEN1_DE1_DA_SF | BXX_GEN1_DE1 | Sample Generator Failed To Start | 32 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_GEN1_DE1.DA_SF | No | Sample Generator Failed To Start | 0 | 0
BXX_GEN1_DE1_DA_XF | BXX_GEN1_DE1 | Sample Generator Failed To Stop | 31 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_GEN1_DE1.DA_XF | No | Sample Generator Failed To Stop | 0 | 0
BXX_GEN1_DE1_DA_RM | BXX_GEN1_DE1 | Sample Generator Not in Auto | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_GEN1_DE1.DA_RM | No | Sample Generator Not in Auto | 0 | 0
BXX_GEN1_DE1_PB_SF | BXX_GEN1_DE1 | Sample Generator Failed To Start Alarm En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_SF.RE | No | Sample Generator Failed To Start Alarm En | 0 | 0
BXX_GEN1_DE1_PB_XF | BXX_GEN1_DE1 | Sample Generator Failed To Stop Alarm En | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_XF.RE | No | Sample Generator Failed To Stop Alarm En | 0 | 0
BXX_GEN1_DE1_PB_RM | BXX_GEN1_DE1 | Sample Generator Not in Auto Alarm En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | On | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_RM.RE | No | Sample Generator Not in Auto Alarm En | 0 | 0
BXX_GEN1_DE1_PB_SM | BXX_GEN1_DE1 | Sample Generator Simulate Alarms PB | 35 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_SM | No | Sample Generator Simulate Alarms PB | 0 | 0
BXX_GEN1_DE1_PB_AE | BXX_GEN1_DE1 | Sample Generator Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_AE.RE | No | Sample Generator Alarm Enable | 0 | 0
BXX_GEN1_DE1_PB_SF_DE | BXX_GEN1_DE1 | Sample Generator Failed To Start Dialer En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_SF.DE | No | Sample Generator Failed To Start Dialer En | 0 | 0
BXX_GEN1_DE1_PB_XF_DE | BXX_GEN1_DE1 | Sample Generator Failed to Stop Dialer En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_XF.DE | No | Sample Generator Failed to Stop Dialer En | 0 | 0
BXX_GEN1_DE1_PB_RM_DE | BXX_GEN1_DE1 | Sample Generator Not In Auto Dialer En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_RM.DE | No | Sample Generator Not In Auto Dialer En | 0 | 0
BXX_GEN1_DE1_PB_AE_DE | BXX_GEN1_DE1 | Sample Generator Alarms Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_AE.DE | No | Sample Generator Alarms Dialer Enable | 0 | 0
BXX_GEN1_DE1_PB_SF_SR | BXX_GEN1_DE1 | Sample Generator Failed To Start Sup En | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_SF.SR | No | Sample Generator Failed To Start Sup En | 0 | 0
BXX_GEN1_DE1_PB_XF_SR | BXX_GEN1_DE1 | Sample Generator Failed To Stop Sup En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_XF.SR | No | Sample Generator Failed To Stop Sup En | 0 | 0
BXX_GEN1_DE1_PB_RM_SR | BXX_GEN1_DE1 | Sample Generator Not In Auto Sup En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_RM.SR | No | Sample Generator Not In Auto Sup En | 0 | 0
BXX_GEN1_DE1_PB_AE_SR | BXX_GEN1_DE1 | Sample Generator Alarms Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_AE.SR | No | Sample Generator Alarms Sup Enable | 0 | 0
BXX_GEN1_DE1_PB_ES_RE | BXX_GEN1_DE1 | Sample Generator E-Stop Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_ES.RE | No | Sample Generator E-Stop Enable | 0 | 0
BXX_GEN1_DE1_PB_JW_RE | BXX_GEN1_DE1 | Sample Generator Warning Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_JW.RE | No | Sample Generator Warning Enable | 0 | 0
BXX_GEN1_DE1_PB_GA_RE | BXX_GEN1_DE1 | Sample Generator Fault Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_GA.RE | No | Sample Generator Fault Enable | 0 | 0
BXX_GEN1_DE1_PB_ES_DE | BXX_GEN1_DE1 | Sample Generator E-Stop Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_ES.DE | No | Sample Generator E-Stop Dialer Enable | 0 | 0
BXX_GEN1_DE1_PB_JW_DE | BXX_GEN1_DE1 | Sample Generator Warning Dialer Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_JW.DE | No | Sample Generator Warning Dialer Enable | 0 | 0
BXX_GEN1_DE1_PB_GA_DE | BXX_GEN1_DE1 | Sample Generator Fault Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_GA.DE | No | Sample Generator Fault Dialer Enable | 0 | 0
BXX_GEN1_DE1_PB_ES_SR | BXX_GEN1_DE1 | Sample Generator E-Stop Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_ES.SR | No | Sample Generator E-Stop Sup Enable | 0 | 0
BXX_GEN1_DE1_PB_JW_SR | BXX_GEN1_DE1 | Sample Generator Warning Sup Enable | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_JW.SR | No | Sample Generator Warning Sup Enable | 0 | 0
BXX_GEN1_DE1_PB_GA_SR | BXX_GEN1_DE1 | Sample Generator Fault Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_GA.SR | No | Sample Generator Fault Sup Enable | 0 | 0
:IOInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_GEN1_DE1_AI_TD | BXX_GEN1_DE1 | Sample Generator Starts Today | 29 | No | No | 0 | Yes | No | 0 | 0 | Starts | 0 | 0 | 1000000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_GEN1_DE1.AI_TD | No | Sample Generator Starts Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_GEN1_DE1_AI_MT | BXX_GEN1_DE1 | Sample Generator Starts This Month | 34 | No | No | 0 | Yes | No | 0 | 0 | Starts | 0 | 0 | 1000000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_GEN1_DE1.AI_MT | No | Sample Generator Starts This Month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_GEN1_DE1_AI_MX | BXX_GEN1_DE1 | Sample Generator Total Starts | 29 | Yes | No | 0 | Yes | No | 0 | 0 | Starts | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_GEN1_DE1.AI_MX | No | Sample Generator Total Starts | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_GEN1_DE1_AI_RT | BXX_GEN1_DE1 | Sample Generator Runtime (Hours) | 32 | Yes | No | 0 | Yes | No | 0 | 0 | h | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_GEN1_DE1.AI_RT | No | Sample Generator Runtime (Hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_GEN1_DE1_DI_NM | BXX_GEN1_DE1 | BXX_GEN1_DE1 | 12 | No | No | 0 | Yes | 24 | BXX_GEN1_DE1 | BXX_GEN1_DE1
GEN_NAME | $System | Generator Name | 14 | No | No | 0 | Yes | 64
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_GEN1_DE1_PB_SF_RN | BXX_GEN1_DE1 | Sample Generator Failed To Start Dis Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_SF_RN | No | Sample Generator Failed To Start Dis Reason
BXX_GEN1_DE1_PB_XF_RN | BXX_GEN1_DE1 | Sample Generator Failed To Stop Dis Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_XF_RN | No | Sample Generator Failed To Stop Dis Reason
BXX_GEN1_DE1_PB_AE_RN | BXX_GEN1_DE1 | Sample Generator Alarms Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_AE_RN | No | Sample Generator Alarms Disabled Reason
BXX_GEN1_DE1_PB_RM_RN | BXX_GEN1_DE1 | Sample Generator Not In Auto Disabled Reason | 44 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_RM_RN | No | Sample Generator Not In Auto Disabled Reason
BXX_GEN1_DE1_PB_ES_RN | BXX_GEN1_DE1 | Sample Generator E-Stop Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_ES_RN | No | Sample Generator E-Stop Disabled Reason
BXX_GEN1_DE1_PB_JW_RN | BXX_GEN1_DE1 | Sample Generator Warning Disabled Reason | 40 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_JW_RN | No | Sample Generator Warning Disabled Reason
BXX_GEN1_DE1_PB_GA_RN | BXX_GEN1_DE1 | Sample Generator Fault Disabled Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_GA_RN | No | Sample Generator Fault Disabled Reason
:IndirectDisc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
GEN_DI_AA | $System | Generator in Auto Indirect Tag | 30 | No | 0 | No
GEN_DI_CL | $System | Generator Control Mode Indirect Tag | 35 | No | 0 | No
GEN_DI_SS | $System | Generator Running Indirect Tag | 30 | No | 0 | No
GEN_PB_AE | $System | Generator Alarms Enable PB Indirect Tag | 39 | No | 0 | No
GEN_PB_AR | $System | Generator Alarm Reset Indirect Tag | 34 | No | 0 | No
GEN_PB_RM | $System | Generator Not In Auto Enable PB Indirect Tag | 44 | No | 0 | No
GEN_PB_RT | $System | Generator Runtime Reset Indirect Tag | 36 | No | 0 | No
GEN_PB_SF | $System | Generator Fail to Start Enable PB Indirect Tag | 46 | No | 0 | No
GEN_PB_SM | $System | Generator Simulate Alarms PB Indirect Tag | 41 | No | 0 | No
GEN_PB_XF | $System | Generator Fail to Stop Enable Indirect Tag | 42 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
GEN_AI_RT | $System | Generator Runtime Indirect Tag | 30 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
GEN_GRP | $System | GENSET Group - Indirect | 23
:IndirectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
GEN_SRV | $System | Generator Alarm Server Indirect Tag | 35 | No | 0 | No

## SCADA_DEV_PRM
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_PRM1 | BXX | Location Power Monitor | 22 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinValue | MaxValue | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
PRM_VIS1 | $System | Power Monitor Visibility Link - Ethernet vis. | 45 | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_PRM1_IP1_AI_CV | BXX_PRM1 | Location Power Monitor IP Address Seg. 1 | 40 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.IP1AI_CV | No | Location Power Monitor IP Address Seg. 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_IP2_AI_CV | BXX_PRM1 | Location Power Monitor IP Address Seg. 2 | 40 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.IP2AI_CV | No | Location Power Monitor IP Address Seg. 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_IP3_AI_CV | BXX_PRM1 | Location Power Monitor IP Address Seg. 3 | 40 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.IP3AI_CV | No | Location Power Monitor IP Address Seg. 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_IP4_AI_CV | BXX_PRM1 | Location Power Monitor IP Address Seg. 4 | 40 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.IP4AI_CV | No | Location Power Monitor IP Address Seg. 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_GW1_AI_CV | BXX_PRM1 | Location Power Monitor Gateway Seg. 1 | 37 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.GW1AI_CV | No | Location Power Monitor Gateway Seg. 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_GW2_AI_CV | BXX_PRM1 | Location Power Monitor Gateway Seg. 2 | 37 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.GW2AI_CV | No | Location Power Monitor Gateway Seg. 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_GW3_AI_CV | BXX_PRM1 | Location Power Monitor Gateway Seg. 3 | 37 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.GW3AI_CV | No | Location Power Monitor Gateway Seg. 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_GW4_AI_CV | BXX_PRM1 | Location Power Monitor Gateway Seg. 4 | 37 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.GW4AI_CV | No | Location Power Monitor Gateway Seg. 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_SM1_AI_CV | BXX_PRM1 | Location Power Monitor Subnet Mask Seg. 1 | 41 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.SM1AI_CV | No | Location Power Monitor Subnet Mask Seg. 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_SM2_AI_CV | BXX_PRM1 | Location Power Monitor Subnet Mask Seg. 2 | 41 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.SM2AI_CV | No | Location Power Monitor Subnet Mask Seg. 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_MS3_AI_CV | BXX_PRM1 | Location Power Monitor Subnet Mask Seg. 3 | 41 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.MS3AI_CV | No | Location Power Monitor Subnet Mask Seg. 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_SM4_AI_CV | BXX_PRM1 | Location Power Monitor Subnet Mask Seg. 4 | 41 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 255 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 255 | Linear | BXX | No | BXX_PRM1.SM4AI_CV | No | Location Power Monitor Subnet Mask Seg. 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_PRM1_II1_AI_CV | BXX_PRM1 | Location Power Monitor L1 Current | 33 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 10000000300000000 | 0 | 0.1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.II1AI_CV | No | Location Power Monitor L1 Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_II2_AI_CV | BXX_PRM1 | Location Power Monitor L2 Current | 33 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 10000000300000000 | 0 | 0.1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.II2AI_CV | No | Location Power Monitor L2 Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_II3_AI_CV | BXX_PRM1 | Location Power Monitor L3 Current | 33 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 10000000300000000 | 0 | 0.1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.II3AI_CV | No | Location Power Monitor L3 Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_I4_AI_CV | BXX_PRM1 | Location Power Monitor Neutral Current | 38 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 10000000300000000 | 0 | 0.1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.I4AI_CV | No | Location Power Monitor Neutral Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_II6_AI_CV | BXX_PRM1 | Location Power Monitor 3 Phase Avg Current | 42 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 10000000300000000 | 0 | 0.1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.II6AI_CV | No | Location Power Monitor 3 Phase Avg Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_EI4_AI_CV | BXX_PRM1 | Location Power Monitor L1-L2 Voltage | 36 | Yes | No | 0 | Yes | No | 0 | 0 | V | 0 | 0 | 10000000300000000 | 0 | 0.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.EI4AI_CV | No | Location Power Monitor L1-L2 Voltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_EI5_AI_CV | BXX_PRM1 | Location Power Monitor L2-L3 Voltage | 36 | Yes | No | 0 | Yes | No | 0 | 0 | V | 0 | 0 | 10000000300000000 | 0 | 0.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.EI5AI_CV | No | Location Power Monitor L2-L3 Voltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_EI6_AI_CV | BXX_PRM1 | Location Power Monitor L3-L1 Voltage | 36 | Yes | No | 0 | Yes | No | 0 | 0 | V | 0 | 0 | 10000000300000000 | 0 | 0.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.EI6AI_CV | No | Location Power Monitor L3-L1 Voltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_EI8_AI_CV | BXX_PRM1 | Location Power Monitor Avg L-L Voltage | 38 | Yes | No | 0 | Yes | No | 0 | 0 | V | 0 | 0 | 10000000300000000 | 0 | 0.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.EI8AI_CV | No | Location Power Monitor Avg L-L Voltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_EI1_AI_CV | BXX_PRM1 | Location Power Monitor L1-N Voltage | 35 | Yes | No | 0 | Yes | No | 0 | 0 | V | 0 | 0 | 10000000300000000 | 0 | 0.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.EI1AI_CV | No | Location Power Monitor L1-N Voltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_EI2_AI_CV | BXX_PRM1 | Location Power Monitor L2-N Voltage | 35 | Yes | No | 0 | Yes | No | 0 | 0 | V | 0 | 0 | 10000000300000000 | 0 | 0.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.EI2AI_CV | No | Location Power Monitor L2-N Voltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_EI3_AI_CV | BXX_PRM1 | Location Power Monitor L3-N Voltage | 35 | Yes | No | 0 | Yes | No | 0 | 0 | V | 0 | 0 | 10000000300000000 | 0 | 0.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.EI3AI_CV | No | Location Power Monitor L3-N Voltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_EI7_AI_CV | BXX_PRM1 | Location Power Monitor Avg L-N Voltage | 38 | Yes | No | 0 | Yes | No | 0 | 0 | V | 0 | 0 | 10000000300000000 | 0 | 0.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.EI7AI_CV | No | Location Power Monitor Avg L-N Voltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_HZ1_AI_CV | BXX_PRM1 | Location Power Monitor Last Cycle Frequency | 43 | Yes | No | 0 | Yes | No | 0 | 0 | Hz | 0 | 0 | 70 | 0 | 0.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 70 | Linear | BXX | No | BXX_PRM1.HZ1AI_CV | No | Location Power Monitor Last Cycle Frequency | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_JI1_AI_CV | BXX_PRM1 | Location Power Monitor Line 1 Real Power | 40 | Yes | No | 0 | Yes | No | 0 | 0 | kW | 0 | -10000000300000000 | 10000000300000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | -10000000300000000 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.JI1AI_CV | No | Location Power Monitor Line 1 Real Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_JI2_AI_CV | BXX_PRM1 | Location Power Monitor Line 2 Real Power | 40 | Yes | No | 0 | Yes | No | 0 | 0 | kW | 0 | -10000000300000000 | 10000000300000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | -10000000300000000 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.JI2AI_CV | No | Location Power Monitor Line 2 Real Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_JI3_AI_CV | BXX_PRM1 | Location Power Monitor Line 3 Real Power | 40 | Yes | No | 0 | Yes | No | 0 | 0 | kW | 0 | -10000000300000000 | 10000000300000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | -10000000300000000 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.JI3AI_CV | No | Location Power Monitor Line 3 Real Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_J4_AI_CV | BXX_PRM1 | Location Power Monitor Total Real Power | 39 | Yes | No | 0 | Yes | No | 0 | 0 | kW | 0 | -10000000300000000 | 10000000300000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | -10000000300000000 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.J4AI_CV | No | Location Power Monitor Total Real Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_JI5_AI_CV | BXX_PRM1 | Location Power Monitor Total Reactive Power | 43 | Yes | No | 0 | Yes | No | 0 | 0 | kVAR | 0 | -10000000300000000 | 10000000300000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | -10000000300000000 | 10000000300000000 | Linear | BXX | No | BXX_PRM1.JI5AI_CV | No | Location Power Monitor Total Reactive Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_RP1_AI_CV | BXX_PRM1 | Location Power Monitor True Power Factor | 40 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0.1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_PRM1.RP1AI_CV | No | Location Power Monitor True Power Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_JH3_AI_CV | BXX_PRM1 | Location Power Monitor Net Real Power Consumed | 46 | Yes | No | 0 | Yes | No | 0 | 0 | GWh | 0 | -10000000 | 10000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | -10000000 | 10000000 | Linear | BXX | No | BXX_PRM1.JH3AI_CV | No | Location Power Monitor Net Real Power Consumed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_JH1_AI_CV | BXX_PRM1 | Location Power Monitor Net Real Power Consumed | 46 | Yes | No | 0 | Yes | No | 0 | 0 | KWh | 0 | -10000000 | 10000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | -10000000 | 10000000 | Linear | BXX | No | BXX_PRM1.JH1AI_CV | No | Location Power Monitor Net Real Power Consumed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_JH4_AI_CV | BXX_PRM1 | Location Power Monitor Net React Power Consumed | 47 | Yes | No | 0 | Yes | No | 0 | 0 | GVARH | 0 | -10000000 | 10000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | -10000000 | 10000000 | Linear | BXX | No | BXX_PRM1.JH4AI_CV | No | Location Power Monitor Net React Power Consumed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_JH2_AI_CV | BXX_PRM1 | Location Power Monitor Net React Power Consumed | 47 | Yes | No | 0 | Yes | No | 0 | 0 | KVARH | 0 | -10000000 | 10000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | -10000000 | 10000000 | Linear | BXX | No | BXX_PRM1.JH2AI_CV | No | Location Power Monitor Net React Power Consumed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_II5_AI_CV | BXX_PRM1 | Location Power Monitor Demand Current | 37 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 10000000 | 0 | 0.1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000 | Linear | BXX | No | BXX_PRM1.II5AI_CV | No | Location Power Monitor Demand Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PRM1_JI6_AI_CV | BXX_PRM1 | Location Power Monitor Demand Power | 35 | Yes | No | 0 | Yes | No | 0 | 0 | kW | 0 | 0 | 10000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10000000 | Linear | BXX | No | BXX_PRM1.JI6AI_CV | No | Location Power Monitor Demand Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_PRM1_AI_NM | BXX_PRM1 | BXX_PRM1 | 8 | No | No | 0 | Yes | 131 | BXX_PRM1 | BXXCPU01_1 | Yes | BXX_PRM1_AI_NM | No
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
PRM_NAME | $System | Power Monitor Name | 18 | No | No | 0 | Yes | 131
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PRM01_AI_IP | $System | Power Monitor Indirect IP Address Byte a | 40 | No | 0 | No
PRM02_AI_IP | $System | Power Monitor Indirect IP Address Byte b | 40 | No | 0 | No
PRM03_AI_IP | $System | Power Monitor Indirect IP Address Byte c | 40 | No | 0 | No
PRM04_AI_IP | $System | Power Monitor Indirect IP Address Byte d | 40 | No | 0 | No
PRM_E1_AI_CV | $System | Power Monitor Indirect Line 1 to Neutral Voltage | 48 | No | 0 | No
PRM_E2_AI_CV | $System | Power Monitor Indirect Line 2 to Neutral Voltage | 48 | No | 0 | No
PRM_E3_AI_CV | $System | Power Monitor Indirect Line 3 to Neutral Voltage | 48 | No | 0 | No
PRM_E4_AI_CV | $System | Power Monitor Indirect 3-Phase Avg L-N Voltage | 46 | No | 0 | No
PRM_EA_AI_CV | $System | Power Monitor Indirect Line 1 to Line 2 Voltage | 47 | No | 0 | No
PRM_EB_AI_CV | $System | Power Monitor Indirect Line 2 to Line 3 Voltage | 47 | No | 0 | No
PRM_EC_AI_CV | $System | Power Monitor Indirect Line 3 to Line 1 Voltage | 47 | No | 0 | No
PRM_EI_AI_CV | $System | Power Monitor Indirect L-L Average Voltage | 42 | No | 0 | No
PRM_G1_AI_IP | $System | Power Monitor Indirect Gateway IP | 33 | No | 0 | No
PRM_G2_AI_IP | $System | Power Monitor Indirect Gateway IP | 33 | No | 0 | No
PRM_G3_AI_IP | $System | Power Monitor Indirect Gateway IP | 33 | No | 0 | No
PRM_G4_AI_IP | $System | Power Monitor Indirect Gateway IP | 33 | No | 0 | No
PRM_HZ_AI_CV | $System | Power Monitor Indirect Frequency Last Cycle | 43 | No | 0 | No
PRM_I1_AI_CV | $System | Power Monitor Indirect Line 1 Current | 37 | No | 0 | No
PRM_I2_AI_CV | $System | Power Monitor Indirect Line 2 Current | 37 | No | 0 | No
PRM_I3_AI_CV | $System | Power Monitor Indirect Line 3 Current | 37 | No | 0 | No
PRM_I4_AI_CV | $System | Power Monitor Indirect Neutral Current | 38 | No | 0 | No
PRM_ID_AI_CV | $System | Power Monitor Indirect Current (Amps) Demand | 44 | No | 0 | No
PRM_II_AI_CV | $System | Power Monitor Indirect 3-Phase L-L Avg Current | 46 | No | 0 | No
PRM_J1_AI_CV | $System | Power Monitor Indirect RealPower Line 1 | 39 | No | 0 | No
PRM_J2_AI_CV | $System | Power Monitor Indirect RealPower Line 2 | 39 | No | 0 | No
PRM_J3_AI_CV | $System | Power Monitor Indirect RealPower Line 3 | 39 | No | 0 | No
PRM_JD_AI_CV | $System | Power Monitor Indirect Voltage Demand | 37 | No | 0 | No
PRM_JM_AI_CV | $System | Power Monitor Indirect GW Hours | 31 | No | 0 | No
PRM_JH_AI_CV | $System | Power Monitor Indirect kW Hours | 31 | No | 0 | No
PRM_JI_AI_CV | $System | Power Monitor Indirect Total RealPower | 38 | No | 0 | No
PRM_JN_AI_CV | $System | Power Monitor Indirect GVAR Hours | 33 | No | 0 | No
PRM_JV_AI_CV | $System | Power Monitor Indirect kVAR Hours | 33 | No | 0 | No
PRM_M1_AI_IP | $System | Power Monitor Indirect Subnet Mask Byte a | 42 | No | 0 | No
PRM_M2_AI_IP | $System | Power Monitor Indirect Subnet Mask Byte b | 42 | No | 0 | No
PRM_M3_AI_IP | $System | Power Monitor Indirect Subnet Mask Byte c | 42 | No | 0 | No
PRM_M4_AI_IP | $System | Power Monitor Indirect Subnet Mask Byte d | 42 | No | 0 | No

## SCADA_DEV_WTN
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_WTN1_FI1 | BXX | Rain Gauge | 10 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_WTN1_FI1_PB_EN | BXX_WTN1_FI1 | Rain Gauge Totalization Enable | 30 | No | Yes | 600 | Yes | Off | Disabled | Enabled | None | 900 | Direct | BXX | No | BXX_WTN1_FI1.PB_EN | No | Rain Gauge Totalization Enable | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_WTN1_FI1_AI_YM | BXX_WTN1_FI1 | Rain Gauge Last Month Total Rainfall | 36 | Yes | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_YM | No | Rain Gauge Last Month Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_L5 | BXX_WTN1_FI1 | Rain Gauge Last 5 Minutes Total Rainfall | 40 | Yes | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_L5 | No | Rain Gauge Last 5 Minutes Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_HT | BXX_WTN1_FI1 | Rain Gauge Current Hour Total Rainfall | 38 | No | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_HT | No | Rain Gauge Current Hour Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_YT | BXX_WTN1_FI1 | Rain Gauge Yesterday Total Rainfall | 35 | Yes | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_YT | No | Rain Gauge Yesterday Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AO_CF | BXX_WTN1_FI1 | Rain Gauge Rain Gauge Calibration Factor | 40 | No | Yes | 900 | Yes | No | 0 | 0 | mm/tip | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AO_CF | No | Rain Gauge Rain Gauge Calibration Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_C5 | BXX_WTN1_FI1 | Rain Gauge Current 5 Minutes Total Rainfall | 43 | No | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_C5 | No | Rain Gauge Current 5 Minutes Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_TD | BXX_WTN1_FI1 | Rain Gauge Current Day Total Rainfall | 37 | No | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_TD | No | Rain Gauge Current Day Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_TY | BXX_WTN1_FI1 | Rain Gauge Current Year Total Rainfall | 38 | Yes | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_TY | No | Rain Gauge Current Year Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_WT | BXX_WTN1_FI1 | Rain Gauge Current Week Total Rainfall | 38 | No | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_WT | No | Rain Gauge Current Week Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_YH | BXX_WTN1_FI1 | Rain Gauge Last Hour Total Rainfall | 35 | Yes | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_YH | No | Rain Gauge Last Hour Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_MT | BXX_WTN1_FI1 | Rain Gauge Current Month Total Rainfall | 39 | No | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_MT | No | Rain Gauge Current Month Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_YL | BXX_WTN1_FI1 | Rain Gauge Last Year Total Rainfall | 35 | No | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_YL | No | Rain Gauge Last Year Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WTN1_FI1_AI_YW | BXX_WTN1_FI1 | Rain Gauge Last Week Total Rainfall | 35 | No | No | 0 | Yes | No | 0 | 0 | mm | 0 | 0 | 5000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 5000 | Linear | BXX | No | BXX_WTN1_FI1.AI_YW | No | Rain Gauge Last Week Total Rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IndirectDisc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
WTN1_FI_PB_EN | $System | Enable Rainfall Totalization - Indirect | 39 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
WTN1_FI_AI_C5 | $System | Current 5 Minute Total Rainfall - Indirect | 42 | No | 0 | No
WTN1_FI_AI_HT | $System | Current Hour Total Rainfall - Indirect | 38 | No | 0 | No
WTN1_FI_AI_L5 | $System | Last 5 Minutes Total Rainfall - Indirect | 40 | No | 0 | No
WTN1_FI_AI_MT | $System | Current Month Total Rainfall - Indirect | 39 | No | 0 | No
WTN1_FI_AI_TD | $System | Current Day Total Rainfall - Indirect | 37 | No | 0 | No
WTN1_FI_AI_TY | $System | Current Year Total Rainfall - Indirect | 38 | No | 0 | No
WTN1_FI_AI_WT | $System | Current Week Total Rainfall - Indirect | 38 | No | 0 | No
WTN1_FI_AI_YH | $System | Last Hour Total Rainfall - Indirect | 35 | No | 0 | No
WTN1_FI_AI_YL | $System | Last Year Total Rainfall - Indirect | 35 | No | 0 | No
WTN1_FI_AI_YM | $System | Last Month Total Rainfall - Indirect | 36 | No | 0 | No
WTN1_FI_AI_YT | $System | Yesterday Total Rainfall - Indirect | 35 | No | 0 | No
WTN1_FI_AI_YW | $System | Last Week Total Rainfall - Indirect |  | No | 0 | No
WTN1_FI_AO_CF | $System | Rain Gauge Calibration Factor - Indirect | 40 | No | 0 | No
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## SCADA_PRC_PUMP_XDUTY
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DTY1_DP | BXX | Station Pump Duty | 17 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryDisc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
DTY_IN_VIS1 | $System | Duty Select Info Button Visibility | 34 | No | No | 0 | Yes | Off |  |  | None | 1 | Duty Select Info Button Visibility | 0 | 0
DTY_IN_D1_VIS1 | $System | Position 1 Device 1 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 1 Device 1 Selection Visibility | 0 | 0
DTY_IN_D1_VIS2 | $System | Position 1 Device 2 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 1 Device 2 Selection Visibility | 0 | 0
DTY_IN_D1_VIS3 | $System | Position 1 Device 3 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 1 Device 3 Selection Visibility | 0 | 0
DTY_IN_D1_VIS4 | $System | Position 1 Device 4 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 1 Device 4 Selection Visibility | 0 | 0
DTY_IN_D2_VIS1 | $System | Position 2 Device 1 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 2 Device 1 Selection Visibility | 0 | 0
DTY_IN_D2_VIS2 | $System | Position 2 Device 2 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 2 Device 2 Selection Visibility | 0 | 0
DTY_IN_D2_VIS3 | $System | Position 2 Device 3 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 2 Device 3 Selection Visibility | 0 | 0
DTY_IN_D2_VIS4 | $System | Position 2 Device 4 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 2 Device 4 Selection Visibility | 0 | 0
DTY_IN_D3_VIS1 | $System | Position 3 Device 1 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 3 Device 1 Selection Visibility | 0 | 0
DTY_IN_D3_VIS2 | $System | Position 3 Device 2 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 3 Device 2 Selection Visibility | 0 | 0
DTY_IN_D3_VIS3 | $System | Position 3 Device 3 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 3 Device 3 Selection Visibility | 0 | 0
DTY_IN_D3_VIS4 | $System | Position 3 Device 4 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 3 Device 4 Selection Visibility | 0 | 0
DTY_IN_D4_VIS1 | $System | Position 4 Device 1 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 4 Device 1 Selection Visibility | 0 | 0
DTY_IN_D4_VIS2 | $System | Position 4 Device 2 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 4 Device 2 Selection Visibility | 0 | 0
DTY_IN_D4_VIS3 | $System | Position 4 Device 3 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 4 Device 3 Selection Visibility | 0 | 0
DTY_IN_D4_VIS4 | $System | Position 4 Device 4 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 4 Device 4 Selection Visibility | 0 | 0
:IODisc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DTY1_DP1_DI_UE | BXX_DTY1_DP | Station Pump Duty Assignment Update Error | 41 | No | Yes | 673 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DTY1_DP.DI_UE | Yes | Station Pump Duty Assignment Update Error | 0 | 0
BXX_DTY1_DP1_PB_AU | BXX_DTY1_DP | Station Pump Duty Assignment Update | 35 | No | Yes | 613 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DTY1_DP.PB_AU | No | Station Pump Duty Assignment Update | 0 | 0
BXX_DTY1_DP1_PB_SU | BXX_DTY1_DP | Station Pump Duty Setpoint Update | 33 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DTY1_DP.PB_SU | No | Station Pump Duty Setpoint Update | 0 | 0
BXX_DTY1_DP1_DI_EE | BXX_DTY1_DP | Station Pump Duty Setpoint Update Error | 39 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DTY1_DP.DI_EE | No | Station Pump Duty Setpoint Update Error | 0 | 0
:IOInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DTY1_DP1_AI_CT | BXX_DTY1_DP | Station Pump Duty Pump 1 | 24 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AI_CT | Yes | Station Pump Duty Pump 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_CT | BXX_DTY1_DP | Station Pump Duty Pump 2 | 24 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_CT | Yes | Station Pump Duty Pump 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AI_CT | BXX_DTY1_DP | Station Pump Duty Pump 3 | 24 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AI_CT | Yes | Station Pump Duty Pump 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_CT | BXX_DTY1_DP | Station Pump Duty Pump 4 | 24 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_CT | Yes | Station Pump Duty Pump 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AI_TY | BXX_DTY1_DP | Station Pump Duty Days Remaining | 32 | No | Yes | 700 | Yes | No | 0 | 0 | Days | 0 | 0 | 10 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10 | Linear | BXX | No | BXX_DTY1_DP.AI_TY | Yes | Station Pump Duty Days Remaining | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_EN | BXX_DTY1_DP | Station Pump Duty Rotation Mode | 31 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DTY1_DP.AO_EN | No | Station Pump Duty Rotation Mode | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_CT | BXX_DTY1_DP | Station Pump Duty Pump 1 Entry | 30 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AO_CT | No | Station Pump Duty Pump 1 Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_CT | BXX_DTY1_DP | Station Pump Duty Pump 2 Entry | 30 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_CT | No | Station Pump Duty Pump 2 Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AO_CT | BXX_DTY1_DP | Station Pump Duty Pump 3 Entry | 30 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AO_CT | No | Station Pump Duty Pump 3 Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_CT | BXX_DTY1_DP | Station Pump Duty Pump 4 Entry | 30 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_CT | No | Station Pump Duty Pump 4 Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_DY | BXX_DTY1_DP | Station Pump Duty Rotation Daily Interval | 41 | No | Yes | 900 | Yes | No | 0 | 0 | d | 1 | 1 | 10 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 10 | Linear | BXX | No | BXX_DTY1_DP.AO_DY | No | Station Pump Duty Rotation Daily Interval | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_HS | BXX_DTY1_DP | Station Pump Duty Rotate Daily At Hour | 38 | No | Yes | 900 | Yes | No | 0 | 0 | hr | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_DTY1_DP.AO_HS | No | Station Pump Duty Rotate Daily At Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_MS | BXX_DTY1_DP | Station Pump Duty Rotate Daily At Minute | 40 | No | Yes | 900 | Yes | No | 0 | 0 | min | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_DTY1_DP.AO_MS | No | Station Pump Duty Rotate Daily At Minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_AI | BXX_DTY1_DP | Station Pump Duty Rotation Hourly Interval | 42 | No | Yes | 900 | Yes | No | 0 | 0 | Hours | 1 | 1 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 23 | Linear | BXX | No | BXX_DTY1_DP.AO_AI | No | Station Pump Duty Rotation Hourly Interval | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DTY1_DP1_AO_TS | BXX_DTY1_DP | Station Pump Duty 1 Start Level Entry | 37 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AO_TS | No | Station Pump Duty 1 Start Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_TS | BXX_DTY1_DP | Station Pump Duty 2 Start Level Entry | 37 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_TS | No | Station Pump Duty 2 Start Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AO_TS | BXX_DTY1_DP | Station Pump Duty 3 Start Level Entry | 37 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AO_TS | No | Station Pump Duty 3 Start Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_TS | BXX_DTY1_DP | Station Pump Duty 4 Start Level Entry | 37 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_TS | No | Station Pump Duty 4 Start Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_PS | BXX_DTY1_DP | Station Pump Duty 1 Stop Level Entry | 36 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AO_PS | No | Station Pump Duty 1 Stop Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_PS | BXX_DTY1_DP | Station Pump Duty 2 Stop Level Entry | 36 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_PS | No | Station Pump Duty 2 Stop Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AO_PS | BXX_DTY1_DP | Station Pump Duty 3 Stop Level Entry | 36 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AO_PS | No | Station Pump Duty 3 Stop Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_PS | BXX_DTY1_DP | Station Pump Duty 4 Stop Level Entry | 36 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_PS | No | Station Pump Duty 4 Stop Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AI_TS | BXX_DTY1_DP | Station Pump Duty 1 Start Level | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AI_TS | No | Station Pump Duty 1 Start Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_TS | BXX_DTY1_DP | Station Pump Duty 2 Start Level | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_TS | No | Station Pump Duty 2 Start Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AI_TS | BXX_DTY1_DP | Station Pump Duty 3 Start Level | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AI_TS | No | Station Pump Duty 3 Start Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_TS | BXX_DTY1_DP | Station Pump Duty 4 Start Level | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_TS | No | Station Pump Duty 4 Start Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AI_PS | BXX_DTY1_DP | Station Pump Duty 1 Stop Level | 30 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AI_PS | No | Station Pump Duty 1 Stop Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_PS | BXX_DTY1_DP | Station Pump Duty 2 Stop Level | 30 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_PS | No | Station Pump Duty 2 Stop Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AI_PS | BXX_DTY1_DP | Station Pump Duty 3 Stop Level | 30 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AI_PS | No | Station Pump Duty 3 Stop Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_PS | BXX_DTY1_DP | Station Pump Duty 4 Stop Level | 30 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_PS | No | Station Pump Duty 4 Stop Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AI_XD | BXX_DTY1_DP | Station Pump Duty 1 Level for Max. Speed | 40 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AI_XD | No | Station Pump Duty 1 Level for Max. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_XD | BXX_DTY1_DP | Station Pump Duty 2 Level for Max. Speed | 40 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_XD | No | Station Pump Duty 2 Level for Max. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AI_XD | BXX_DTY1_DP | Station Pump Duty 3 Level for Max. Speed | 40 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AI_XD | No | Station Pump Duty 3 Level for Max. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_XD | BXX_DTY1_DP | Station Pump Duty 4 Level for Max. Speed | 40 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_XD | No | Station Pump Duty 4 Level for Max. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_XD | BXX_DTY1_DP | Station Pump Duty 1 Level for Max. Speed Entry | 46 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AO_XD | No | Station Pump Duty 1 Level for Max. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_XD | BXX_DTY1_DP | Station Pump Duty 2 Level for Max. Speed Entry | 46 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_XD | No | Station Pump Duty 2 Level for Max. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AO_XD | BXX_DTY1_DP | Station Pump Duty 3 Level for Max. Speed Entry | 46 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AO_XD | No | Station Pump Duty 3 Level for Max. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_XD | BXX_DTY1_DP | Station Pump Duty 4 Level for Max. Speed Entry | 46 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_XD | No | Station Pump Duty 4 Level for Max. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AI_ND | BXX_DTY1_DP | Station Pump Duty 1 Level for Min. Speed | 40 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AI_ND | No | Station Pump Duty 1 Level for Min. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_ND | BXX_DTY1_DP | Station Pump Duty 2 Level for Min. Speed | 40 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_ND | No | Station Pump Duty 2 Level for Min. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AI_ND | BXX_DTY1_DP | Station Pump Duty 3 Level for Min. Speed | 40 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AI_ND | No | Station Pump Duty 3 Level for Min. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_ND | BXX_DTY1_DP | Station Pump Duty 4 Level for Min. Speed | 40 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_ND | No | Station Pump Duty 4 Level for Min. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_ND | BXX_DTY1_DP | Station Pump Duty 1 Level for Min. Speed Entry | 46 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AO_ND | No | Station Pump Duty 1 Level for Min. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_ND | BXX_DTY1_DP | Station Pump Duty 2 Level for Min. Speed Entry | 46 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_ND | No | Station Pump Duty 2 Level for Min. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AO_ND | BXX_DTY1_DP | Station Pump Duty 3 Level for Min. Speed Entry | 46 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AO_ND | No | Station Pump Duty 3 Level for Min. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_ND | BXX_DTY1_DP | Station Pump Duty 4 Level for Min. Speed Entry | 46 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_ND | No | Station Pump Duty 4 Level for Min. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
DTY_IN_DV1_NM | $System | Device 1 Name | 13 | No | No | 0 | No | 64
DTY_IN_DV2_NM | $System | Device 2 Name | 13 | No | No | 0 | No | 64
DTY_IN_DV3_NM | $System | Device 3 Name | 13 | No | No | 0 | No | 64
DTY_IN_DV4_NM | $System | Device 4 Name | 13 | No | No | 0 | No | 64
DTY_IN_D1_DP | $System | Description of Position 1 | 25 | No | No | 0 | No | 64
DTY_IN_D2_DP | $System | Description of Position 2 | 25 | No | No | 0 | No | 64
DTY_IN_D3_DP | $System | Description of Position 3 | 25 | No | No | 0 | No | 64
DTY_IN_D4_DP | $System | Description of Position 4 | 25 | No | No | 0 | No | 64
DTY_IN_DV_NM | $System | Duty Rotation Popup Device Type Description | 43 | No | No | 0 | No | 64
DTY_IN_INFO_LN1 | $System | Duty Select Info Popup Line 1 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 1 String
DTY_IN_INFO_LN2 | $System | Duty Select Info Popup Line 2 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 2 String
DTY_IN_INFO_LN3 | $System | Duty Select Info Popup Line 3 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 3 String
DTY_IN_INFO_LN4 | $System | Duty Select Info Popup Line 4 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 4 String
DTY_IN_INFO_LN5 | $System | Duty Select Info Popup Line 5 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 5 String
DTY_IN_INFO_LN6 | $System | Duty Select Info Popup Line 6 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 6 String
:IndirectDisc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
DTY_IN_DA_UE | $System | Duty Selection Assignment Update Error | 38 | No | 0 | No
DTY_IN_PB_AU | $System | Duty Selection Assignment Update Request | 40 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
DTY_IN_AI_DV | $System | Number of Devices for Duty Logic | 32 | No | 0 | No
DTY_IN_AI_TY | $System | Duty Timed Rotation Days Remaining | 34 | No | 0 | No
DTY_IN_AO_AI | $System | Duty Rotation Hour Setpoint | 27 | No | 0 | No
DTY_IN_AO_CT | $System | Duty Rotation Number of Days Setpoint | 37 | No | 0 | No
DTY_IN_AO_EN | $System | Duty Rotation Mode Select | 25 | No | 0 | No
DTY_IN_AO_HS | $System | Duty Timed Rotation Hour Setpoint | 33 | No | 0 | No
DTY_IN_AO_MS | $System | Duty Timed Rotation Minute Setpoint | 35 | No | 0 | No
DTY_IN_D1_AI_CT | $System | Duty 1 Assignment Current | 25 | No | 0 | No
DTY_IN_D1_AO_CT | $System | Duty 1 Assignment Entry | 23 | No | 0 | No
DTY_IN_D2_AI_CT | $System | Duty 2 Assignment Current | 25 | No | 0 | No
DTY_IN_D2_AO_CT | $System | Duty 2 Assignment Entry | 23 | No | 0 | No
DTY_IN_D3_AI_CT | $System | Duty 3 Assignment Current | 25 | No | 0 | No
DTY_IN_D3_AO_CT | $System | Duty 3 Assignment Entry | 23 | No | 0 | No
DTY_IN_D4_AI_CT | $System | Duty 4 Assignment Current | 25 | No | 0 | No
DTY_IN_D4_AO_CT | $System | Duty 4 Assignment Entry | 23 | No | 0 | No

## SCADA_PRC_XMTR_XDUTY
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DTY1_LI | BXX | Station Level Duty | 18 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DTY1_LI_1PB_EN | BXX_DTY1_LI | Station Level Duty Rotation Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 94 | Direct | BXX | No | BXX_DTY1_LI.PB_EN | No | Station Level Duty Rotation Enable | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DTY1_LI_1AO_CT | BXX_DTY1_LI | Station Level Duty Device Selected | 34 | No | Yes | 600 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_LI.AO_CT | No | Station Level Duty Device Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_LI_1AI_CV | BXX_DTY1_LI | Station Level Duty Transmitter | 30 | No | Yes | 600 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_LI.AI_CT | No | Station Level Duty Transmitter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
DTY_IN_DV1_NM | $System | Device 1 Name | 13 | No | No | 0 | No | 64
DTY_IN_DV2_NM | $System | Device 2 Name | 13 | No | No | 0 | No | 64
DTY_IN_D1_DP | $System | Description of Position 1 | 25 | No | No | 0 | No | 64
DTY_IN_D2_DP | $System | Description of Position 2 | 25 | No | No | 0 | No | 64
DTY_IN_D3_DP | $System | Description of Position 3 | 25 | No | No | 0 | No | 64
DTY_IN_D4_DP | $System | Description of Position 4 | 25 | No | No | 0 | No | 64
:IndirectDisc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
WW00_DY_PB_EN | $System | Duty Level Enable Indirect Tag | 30 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
WW00_DY_AI_CV | $System | Duty Level Selected Transmitter Indirect Tag | 44 | No | 0 | No
WW00_DY_AO_CT | $System | Duty Level Transmitter Selected Indirect Tag | 44 | No | 0 | No
0
0
0

## SCADA_PRC_OVERFLOW
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_OVF1_FI1 | BXX | Sample Overflow | 15 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms Group | 25 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_OVF1_FI1_DI_AD | BXX_DSAB | Sample Overflow Disabled Analog Alarm | 37 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_OVF1_FI1.DI_AD | No | Sample Overflow Disabled Analog Alarm | 0 | 0
BXX_OVF1_FI1_DI_SC | BXX_OVF1_FI1 | Sample Overflow Scan Status | 27 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.DI_SC | No | Sample Overflow Scan Status | 0 | 0
BXX_OVF1_FI1_DA_LL | BXX_OVF1_FI1 | Sample Overflow LOLO Alarm | 26 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_OVF1_FI1.DA_LL | No | Sample Overflow LOLO Alarm | 0 | 0
BXX_OVF1_FI1_DA_ER | BXX_OVF1_FI1 | Sample Overflow Signal Error Alarm | 34 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_OVF1_FI1.DA_ER | No | Sample Overflow Signal Error Alarm | 0 | 0
BXX_OVF1_FI1_PB_SM | BXX_OVF1_FI1 | Sample Overflow Alarm Test | 26 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_SM | No | Sample Overflow Alarm Test | 0 | 0
BXX_OVF1_FI1_PB_SV | BXX_OVF1_FI1 | Sample Overflow Override Enable | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_SV | No | Sample Overflow Override Enable | 0 | 0
BXX_OVF1_FI1_PB_AE | BXX_OVF1_FI1 | Sample Overflow Alarm Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_AE.RE | No | Sample Overflow Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_HI | BXX_OVF1_FI1 | Sample Overflow High Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HI.RE | No | Sample Overflow High Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_LO | BXX_OVF1_FI1 | Sample Overflow Low Alarm Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_LO.RE | No | Sample Overflow Low Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_LL | BXX_OVF1_FI1 | Sample Overflow LOLO Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_LL.RE | No | Sample Overflow LOLO Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_ER | BXX_OVF1_FI1 | Sample Overflow Signal Error Alarm En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_ER.RE | No | Sample Overflow Signal Error Alarm En | 0 | 0
BXX_OVF1_FI1_PB_SC | BXX_OVF1_FI1 | Sample Overflow Scan Enable | 27 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_SC | No | Sample Overflow Scan Enable | 0 | 0
BXX_OVF1_FI1_DA_HH | BXX_OVF1_FI1 | Sample Overflow HIHI Alarm | 26 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_OVF1_FI1.DA_HH | No | Sample Overflow HIHI Alarm | 0 | 0
BXX_OVF1_FI1_DA_HI | BXX_OVF1_FI1 | Sample Overflow HI Alarm | 24 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_OVF1_FI1.DA_HI | No | Sample Overflow HI Alarm | 0 | 0
BXX_OVF1_FI1_PB_HH | BXX_OVF1_FI1 | Sample Overflow HIHI Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HH.RE | No | Sample Overflow HIHI Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_AR | BXX_OVF1_FI1 | Sample Overflow Alarm Reset | 27 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_AR | No | Sample Overflow Alarm Reset | 0 | 0
BXX_OVF1_FI1_DA_LO | BXX_OVF1_FI1 | Sample Overflow LO Alarm | 24 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_OVF1_FI1.DA_LO | No | Sample Overflow LO Alarm | 0 | 0
BXX_OVF1_FI1_PB_MM | BXX_OVF1_FI1 | Sample Overflow Enable Limit Tracking | 37 | No | Yes | 600 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_MM | No | Sample Overflow Enable Limit Tracking | 0 | 0
BXX_OVF1_FI1_PB_RS | BXX_OVF1_FI1 | Sample Overflow Totalizer Reset | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_RS | No | Sample Overflow Totalizer Reset | 0 | 0
BXX_OVF1_FI1_PB_HI_DE | BXX_OVF1_FI1 | Sample Overflow High Alarm Dialer Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HI.DE | No | Sample Overflow High Alarm Dialer Enable | 0 | 0
BXX_OVF1_FI1_PB_LO_DE | BXX_OVF1_FI1 | Sample Overflow Low Alarm Dialer Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_LO.DE | No | Sample Overflow Low Alarm Dialer Enable | 0 | 0
BXX_OVF1_FI1_PB_LL_DE | BXX_OVF1_FI1 | Sample Overflow LOLO Alarm Dialer Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_LL.DE | No | Sample Overflow LOLO Alarm Dialer Enable | 0 | 0
BXX_OVF1_FI1_PB_ER_DE | BXX_OVF1_FI1 | Sample Overflow Signal Error Alarm Dialer En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_ER.DE | No | Sample Overflow Signal Error Alarm Dialer En | 0 | 0
BXX_OVF1_FI1_PB_HH_DE | BXX_OVF1_FI1 | Sample Overflow HIHI Alarm Dialer Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HH.DE | No | Sample Overflow HIHI Alarm Dialer Enable | 0 | 0
BXX_OVF1_FI1_PB_AE_DE | BXX_OVF1_FI1 | Sample Overflow Alarms Dialer Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_AE.DE | No | Sample Overflow Alarms Dialer Enable | 0 | 0
BXX_OVF1_FI1_PB_HI_SR | BXX_OVF1_FI1 | Sample Overflow High Alarm Sup Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HI.SR | No | Sample Overflow High Alarm Sup Enable | 0 | 0
BXX_OVF1_FI1_PB_LO_SR | BXX_OVF1_FI1 | Sample Overflow Low Alarm Sup Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_LO.SR | No | Sample Overflow Low Alarm Sup Enable | 0 | 0
BXX_OVF1_FI1_PB_LL_SR | BXX_OVF1_FI1 | Sample Overflow LOLO Alarm Sup Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_LL.SR | No | Sample Overflow LOLO Alarm Sup Enable | 0 | 0
BXX_OVF1_FI1_PB_ER_SR | BXX_OVF1_FI1 | Sample Overflow Signal Error Alarm Sup En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_ER.SR | No | Sample Overflow Signal Error Alarm Sup En | 0 | 0
BXX_OVF1_FI1_PB_HH_SR | BXX_OVF1_FI1 | Sample Overflow HIHI Alarm Sup Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HH.SR | No | Sample Overflow HIHI Alarm Sup Enable | 0 | 0
BXX_OVF1_FI1_PB_AE_SR | BXX_OVF1_FI1 | Sample Overflow Alarms Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_AE.SR | No | Sample Overflow Alarms Sup Enable | 0 | 0
BXX_OVF1_FI1_DI_SS | BXX_OVF1_FI1 | Sample Overflow Event | 21 | No | Yes | 700 | Yes | Off | Normal | Overflow | None | 1 | Direct | BXX | No | BXX_OVFTL1.DI_SS | No | Sample Overflow Event | 0 | 0
BXX_OVF1_FI1_DA_SS | BXX_OVF1_FI1 | Sample Overflow Alarm | 21 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_OVFTL1.DA_SS | No | Sample Overflow Alarm | 0 | 0
BXX_OVF1_FI1_PB_RS | BXX_OVF1_FI1 | Sample Overflow Manual Reset | 28 | No | Yes | 600 | Yes | Off | Off | Reset | None | 1 | Direct | BXX | No | BXX_OVFTL1.PB_RS | No | Sample Overflow Manual Reset | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_OVF1_FI1_AI_VI | BXX_OVF1_FI1 | Sample Overflow Number of Visible Eng Values | 44 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_OVF1_FI1.AI_VI | No | Sample Overflow Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_DC | BXX_OVF1_FI1 | Sample Overflow Precision | 25 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_OVF1_FI1.AI_DC | No | Sample Overflow Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_E2_DC | BXX_OVF1_FI1 | Sample Overflow Eng Value 2 Precision | 37 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_OVF1_FI1.E2_DC | No | Sample Overflow Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_E3_DC | BXX_OVF1_FI1 | Sample Overflow Eng Value 3 Precision | 37 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_OVF1_FI1.E3_DC | No | Sample Overflow Eng Value 3 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_HS | BXX_OVF1_FI1 | Sample Overflow Event Start Hour | 32 | No | Yes | 900 | Yes | No | 0 | 0 | Hour | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_HS | No | Sample Overflow Event Start Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_HS | BXX_OVF1_FI1 | Sample Overflow Event Stop Hour | 31 | No | Yes | 900 | Yes | No | 0 | 0 | Hour | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_HS | No | Sample Overflow Event Stop Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_MM | BXX_OVF1_FI1 | Sample Overflow Event Stop Month | 32 | No | Yes | 900 | Yes | No | 0 | 0 | Month | 0 | 0 | 12 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 12 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_MM | No | Sample Overflow Event Stop Month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_DY | BXX_OVF1_FI1 | Sample Overflow Event Stop Day | 30 | No | Yes | 900 | Yes | No | 0 | 0 | Day | 0 | 0 | 31 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 31 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_DY | No | Sample Overflow Event Stop Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_MS | BXX_OVF1_FI1 | Sample Overflow Event Stop Minute | 33 | No | Yes | 900 | Yes | No | 0 | 0 | Minutes | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_MS | No | Sample Overflow Event Stop Minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_YY | BXX_OVF1_FI1 | Sample Overflow Event Stop Year | 31 | No | Yes | 900 | Yes | No | 0 | 0 | Year | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 9999 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_YY | No | Sample Overflow Event Stop Year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_YY | BXX_OVF1_FI1 | Sample Overflow Event Start Year | 32 | No | Yes | 900 | Yes | No | 0 | 0 | Year | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 9999 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_YY | No | Sample Overflow Event Start Year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_SN | BXX_OVF1_FI1 | Sample Overflow Event Start Second | 34 | No | Yes | 900 | Yes | No | 0 | 0 | Seconds | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_SN | No | Sample Overflow Event Start Second | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_MS | BXX_OVF1_FI1 | Sample Overflow Event Start Minute | 34 | No | Yes | 900 | Yes | No | 0 | 0 | Minutes | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_MS | No | Sample Overflow Event Start Minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_MM | BXX_OVF1_FI1 | Sample Overflow Event Start Month | 33 | No | Yes | 900 | Yes | No | 0 | 0 | Month | 0 | 0 | 12 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 12 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_MM | No | Sample Overflow Event Start Month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_SN | BXX_OVF1_FI1 | Sample Overflow Event Stop Second | 33 | No | Yes | 900 | Yes | No | 0 | 0 | Seconds | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_SN | No | Sample Overflow Event Stop Second | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_TL1_AI_BE | BXX_OVF1_FI1 | Sample Overflow Total Number of Events | 38 | No | Yes | 700 | Yes | No | 0 | 0 | # | 0 | 0 | 32767 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 32767 | Linear | BXX | No | BXX_OVF1_TL1.AI_BE | No | Sample Overflow Total Number of Events | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_DY | BXX_OVF1_FI1 | Sample Overflow Event Start Day | 31 | No | Yes | 900 | Yes | No | 0 | 0 | Day | 0 | 0 | 31 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 31 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_DY | No | Sample Overflow Event Start Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_TL1_AI_TM | BXX_OVF1_FI1 | Sample Overflow Event Duration | 30 | No | No | 0 | Yes | No | 0 | 0 | Minutes | 0 | 0 | 32767 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 32767 | Linear | BXX | No | BXX_OVF1_TL1.AI_TM | No | Sample Overflow Event Duration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_OVF1_FI1_SN_LL | BXX_OVF1_FI1 | Sample Overflow LOLO Alarm Delay | 32 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_OVF1_FI1.SN_LL | No | Sample Overflow LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_SN_HI | BXX_OVF1_FI1 | Sample Overflow High Alarm Delay | 32 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_OVF1_FI1.SN_HI | No | Sample Overflow High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_CV | BXX_OVF1_FI1 | Sample Overflow Current Value | 29 | Yes | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AI_CV | No | Sample Overflow Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_ND | BXX_OVF1_FI1 | Sample Overflow Min Value Today | 31 | Yes | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AI_ND | No | Sample Overflow Min Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_NP | BXX_OVF1_FI1 | Sample Overflow Max Value Today | 31 | Yes | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AI_NP | No | Sample Overflow Max Value Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_XD | BXX_OVF1_FI1 | Sample Overflow Min Value Yesterday | 35 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AI_XD | No | Sample Overflow Min Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_XP | BXX_OVF1_FI1 | Sample Overflow Max Value Yesterday | 35 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AI_XP | No | Sample Overflow Max Value Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_TD | BXX_OVF1_FI1 | Sample Overflow Total Today | 27 | Yes | No | 0 | Yes | No | 0 | 0 | m3 | 0 | 0 | 20000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 20000 | Linear | BXX | No | BXX_OVF1_FI1.AI_TD | No | Sample Overflow Total Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_YT | BXX_OVF1_FI1 | Sample Overflow Total Yesterday | 31 | Yes | No | 0 | Yes | No | 0 | 0 | m3 | 0 | 0 | 20000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 20000 | Linear | BXX | No | BXX_OVF1_FI1.AI_YT | No | Sample Overflow Total Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_AT | BXX_OVF1_FI1 | Sample Overflow Average | 23 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AI_AT | No | Sample Overflow Average | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_XM | BXX_OVF1_FI1 | Sample Overflow Span Setpoint | 29 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_XM | No | Sample Overflow Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_LO | BXX_OVF1_FI1 | Sample Overflow Low Setpoint | 28 | No | Yes | 600 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_LO | No | Sample Overflow Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_HH | BXX_OVF1_FI1 | Sample Overflow HIHI Setpoint | 29 | No | Yes | 600 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_HH | No | Sample Overflow HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_E2_CV | BXX_OVF1_FI1 | Sample Overflow Units 2 | 23 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_OVF1_FI1.E2_CV | No | Sample Overflow Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_HI | BXX_OVF1_FI1 | Sample Overflow High Setpoint | 29 | No | Yes | 600 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_HI | No | Sample Overflow High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_SV | BXX_OVF1_FI1 | Sample Overflow Override Value | 30 | No | Yes | 700 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_SV | No | Sample Overflow Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_EM | BXX_OVF1_FI1 | Sample Overflow Zero Setpoint | 29 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_EM | No | Sample Overflow Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_E3_CV | BXX_OVF1_FI1 | Sample Overflow Units 3 | 23 | No | No | 0 | Yes | No | 0 | 0 | mA | 4 | 4 | 20 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 4 | 20 | Linear | BXX | No | BXX_OVF1_FI1.E3_CV | No | Sample Overflow Units 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_SN_HH | BXX_OVF1_FI1 | Sample Overflow HIHI Alarm Delay | 32 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_OVF1_FI1.SN_HH | No | Sample Overflow HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_SN_LO | BXX_OVF1_FI1 | Sample Overflow Low Alarm Delay | 31 | No | Yes | 600 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_OVF1_FI1.SN_LO | No | Sample Overflow Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_LL | BXX_OVF1_FI1 | Sample Overflow LOLO Setpoint | 29 | No | Yes | 600 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_LL | No | Sample Overflow LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_TL1_AI_CV | BXX_OVF1_FI1 | Sample Overflow Event Volume | 28 | Yes | No | 0 | Yes | No | 0 | 0 | m3 | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_OVF1_TL1.AI_CV | Yes | Sample Overflow Event Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_OVF1_FI1_DI_NM | BXX_OVF1_FI1 | BXX_OVF1_FI1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_OVF1_FI1_PB_HH_RN | BXX_OVF1_FI1 | Sample Overflow HIHI Alarm Disabled Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_HH_RN | No | Sample Overflow HIHI Alarm Disabled Reason
BXX_OVF1_FI1_PB_HI_RN | BXX_OVF1_FI1 | Sample Overflow High Alarm Disabled Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_HI_RN | No | Sample Overflow High Alarm Disabled Reason
BXX_OVF1_FI1_PB_LO_RN | BXX_OVF1_FI1 | Sample Overflow Low Alarm Disabled Reason | 41 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_LO_RN | No | Sample Overflow Low Alarm Disabled Reason
BXX_OVF1_FI1_PB_LL_RN | BXX_OVF1_FI1 | Sample Overflow LOLO Alarm Disabled Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_LL_RN | No | Sample Overflow LOLO Alarm Disabled Reason
BXX_OVF1_FI1_PB_ER_RN | BXX_OVF1_FI1 | Sample Overflow Sig Error Alarm Dis Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_ER_RN | No | Sample Overflow Sig Error Alarm Dis Reason
BXX_OVF1_FI1_PB_AE_RN | BXX_OVF1_FI1 | Sample Overflow Alarms Disabled Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_AE_RN | No | Sample Overflow Alarms Disabled Reason
:IndirectDisc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
OVF1_DA_SS | $System | Overflow Alarm Indirect Tag | 27 | No | 0 | No
OVF1_DI_SS | $System | Overflow Event Present Indirect Tag | 35 | No | 0 | No
OVF1_PB_RS | $System | Overflow Report Reset Indirect Tag | 34 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_DEC | $System | Analog Input Signal Deimal Points - Indirect | 44 | No | 0 | No
ANIN_DC2 | $System | Analog Input Units 2 Decimal Points - Indirect | 46 | No | 0 | No
ANIN_DC3 | $System | Analog Input Units 3 Decimal Points - Indirect | 46 | No | 0 | No
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
OVF1_AI_BE | $System | Overflow Event Count Indirect Tag | 33 | No | 0 | No
OVF1_AI_CV | $System | Overflow Quantity Indirect Tag | 30 | No | 0 | No
OVF1_AI_TM | $System | Overflow Duration Indirect Tag | 30 | No | 0 | No
OVF1_SPAI_DY | $System | Overflow End Day Indirect Tag | 29 | No | 0 | No
OVF1_SPAI_HS | $System | Overflow End Hour Indirect Tag | 30 | No | 0 | No
OVF1_SPAI_MM | $System | Overflow End Month Indirect Tag | 31 | No | 0 | No
OVF1_SPAI_MS | $System | Overflow End Minute Indirect Tag | 32 | No | 0 | No
OVF1_SPAI_SN | $System | Overflow End Second Indirect Tag | 32 | No | 0 | No
OVF1_SPAI_YY | $System | Overflow End Year Indirect Tag | 30 | No | 0 | No
OVF1_STAI_DY | $System | Overflow Start Day Indirect Tag | 31 | No | 0 | No
OVF1_STAI_HS | $System | Overflow Start Hour Indirect Tag | 32 | No | 0 | No
OVF1_STAI_MM | $System | Overflow Start Month Indirect Tag | 33 | No | 0 | No
OVF1_STAI_MS | $System | Overflow Start Minute Indirect Tag | 34 | No | 0 | No
OVF1_STAI_SN | $System | Overflow Start Second Indirect Tag | 34 | No | 0 | No
OVF1_STAI_YY | $System | Overflow Start Year Indirect Tag | 32 | No | 0 | No
:IndirectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0