## Guide
Colour Guide
These Values Should not Changed unless Directed by Halton Region
Optional Tags. Only include if Functionality is Needed
These values must be manually configured by the Programmer
This Column is provided as a development aid and should be deleted before attempting an InTouch Import
51 | String length is too long. Either the Device Description must be shortened or the string concatenation edited within the cell to meet the character limit
Value is Partially or Fully Derived from another entry in worksheet
Instructions
1 | These templates are specifically provided for the design of Wastewater Pump Station Applications
2 | Theses templates compliment the 2 Pump and 4 Pump Baseload Programs and accomanying screens in the InTouch Baseload
3 | These templates may not be comprehensive of all tags required for a Wastewater Pump Station SCADA deployment
4 | Programmers are responsible for ensuring the tags created for their application are complete and correct, irrespective of any errors or ommissions in these templates
5 | Programmers should be aware that deviations from the standard design may require modifications to rows and cells not explicitly highlighted as requiring configuration
6 | These templates rely on values linked across worksheets. It is not recommended to copy worksheets from this workbook to another workbook
7 | In order to create tags for a device, Programmers shall change any cell highlighted orange to an appropriate value
8 | Programmer may be required to remove tags not highlighted as optional due to deviations from the standard design
9 | Any cell highlighted brown should not typically require modification as it will automatically configure itself based on the values in orange cells
10 | If tag descriptions in Column 3 are too long, and the device description cannot be shorted, then the existing standard descriptors may be modified
11 | Column D must be deleted before saving the templates as CSV files for DBLoad into InTouch

## BXXPLC1
:mode=ask |  |  | Description Lengths
:IOAccess | Application | Topic | 5 | AdviseActive | DDEProtocol | SecApplication | SecTopic | SecAdviseActive | SecDDEProtocol | F.AIloverExpression | F.AIloverDeadband | DFOFlag | FBDFlag | F.AIlbackDeadband
BXX | \WCYCPU01\ABCIP | BXX | 3 | Yes | No | \\WCYCPU02\ABCIP | BXX | Yes | No |  | 0 | Yes | Yes | 5
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX | Plant | Station BXX | 11 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1 | BXX | BXX Controller Status | 21 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_PLC1_KS1_DI_PM | BXX_PLC1 | BXX Key Program Mode Status | 27 | No | Yes | 700 | Yes | Off | Off | Program | None | 1 | Direct | BXXCPU01_1 | No | BXX_PLC1.KEY_PROGRAM | No | BXX Key Program Mode Status | 0 | 0
BXX_PLC1_KS1_DI_RM | BXX_PLC1 | BXX Key Run Mode Status | 23 | No | Yes | 700 | Yes | Off | Off | Run | None | 1 | Direct | BXXCPU01_1 | No | BXX_PLC1.KEY_RUN | No | BXX Key Run Mode Status | 0 | 0
BXX_PLC1_F91_DA_EN | BXX_PLC1 | BXX Forces Enabled | 18 | No | Yes | 700 | Yes | Off | Disabled | Enabled | On | 10 | Direct | BXXCPU01_1 | No | BXX_PLC1.FORCES_ENABLED | No | BXX Forces Enabled | 0 | 0
BXX_PLC1_F61_DA_SS | BXX_PLC1 | BXX Minor Fault IO Alarm | 24 | No | No | 0 | Yes | Off | Normal | Fault | On | 10 | Direct | BXXCPU01_1 | No | BXX_PLC1.MINORFAULT_IO | No | BXX Minor Fault IO Alarm | 2 | 0
BXX_PLC1_F71_DA_SS | BXX_PLC1 | BXX Forces Present | 18 | No | No | 0 | Yes | Off | Disabled | Present | On | 275 | Direct | BXXCPU01_1 | No | BXX_PLC1.FORCES_PRESENT | No | BXX Forces Present | 0 | 0
BXX_PLC1_F31_DA_SS | BXX_PLC1 | BXX Major Fault Watchdog Alarm | 30 | No | No | 0 | Yes | Off | Normal | Fault | On | 10 | Direct | BXXCPU01_1 | No | BXX_PLC1.MAJORFAULT_WATCHDOG | No | BXX Major Fault Watchdog Alarm | 2 | 0
BXX_PLC1_JI1_DA_BT | BXX_PLC1 | BXX Minor Fault Battery Alarm | 29 | No | No | 0 | Yes | Off | Normal | Fault | On | 10 | Direct | BXXCPU01_1 | No | BXX_PLC1.MINORFAULT_BATTERY_LOW | No | BXX Minor Fault Battery Alarm | 2 | 0
BXX_PLC1_F21_DA_SS | BXX_PLC1 | BXX Major Fault Startup Alarm | 29 | No | No | 0 | Yes | Off | Normal | Fault | On | 10 | Direct | BXXCPU01_1 | No | BXX_PLC1.MAJORFAULT_STARTUP | No | BXX Major Fault Startup Alarm | 2 | 0
BXX_PLC1_F81_DI_SS | BXX_PLC1 | BXX Minor Faults | 16 | No | Yes | 700 | Yes | Off | Normal | Fault | None | 1 | Direct | BXXCPU01_1 | No | BXX_PLC1.MINORFAULT_PROGRAM | No | BXX Minor Faults | 0 | 0
BXX_PLC1_CK1_PB_SU | BXX_PLC1 | BXX Set PLC Date/Time | 21 | No | Yes | 700 | Yes | Off | Off | On | None | 1 | Direct | BXXCPU01_1 | No | BXX_PLC1.DO_SU | No | BXX Set PLC Date/Time | 0 | 0
BXX_PLC1_001_DI_TM | BXX_PLC1 | BXX Controller Test Mode Status | 31 | No | Yes | 700 | Yes | Off | Off | Test | None | 1 | Direct | BXXCPU01_1 | No | BXX_PLC1.CONTROLLER_TEST | No | BXX Controller Test Mode Status | 0 | 0
BXX_PLC1_001_DI_RE | BXX_PLC1 | BXX Run mode status | 19 | No | Yes | 700 | Yes | Off | Off | Run | None | 1 | Direct | BXXCPU01_1 | No | BXX_PLC1.CONTROLLER_RUN | No | BXX Run mode status | 0 | 0
BXX_PLC1_KS1_DI_RE | BXX_PLC1 | BXX Key Remote Mode Status | 26 | No | Yes | 700 | Yes | Off | Off | Remote | None | 1 | Direct | BXXCPU01_1 | No | BXX_PLC1.KEY_REMOTE | No | BXX Key Remote Mode Status | 0 | 0
BXX_PLC1_001_DI_CN | BXX_PLC1 | BXX-HMI Communication Status | 28 | No | No | 0 | Yes | On | Down | Ok | None | 1 | Direct | BXXCPU01_1 | No | $SYS$Status | No | BXX-HMI Communication Status | 0 | 0
BXX_PLC1_001_DA_CN | BXX_PLC1 | BXX Polling Status Down | 23 | No | No | 0 | Yes | On | Down | Ok | Off | 90 | Direct | BXXCPU01_1 | Yes | BXX_PLC1_001_DA_CN | No | BXX Polling Status Down | 0 | 0
BXX_PLC1_001_DA_FL | BXX_PLC1 | BXX Controller Faulted Status | 29 | No | No | 0 | Yes | Off | Normal | Fault | On | 1 | Direct | BXXCPU01_1 | No | BXX_PLC1.CONTROLLER_FAULTED | No | BXX Controller Faulted Status | 0 | 0
BXX_PLC1_001_DI_PM | BXX_PLC1 | BXX Controller Program Mode Status | 34 | No | No | 0 | Yes | Off | Off | Program | On | 1 | Direct | BXXCPU01_1 | No | BXX_PLC1.CONTROLLER_PROGRAM | No | BXX Controller Program Mode Status | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_PLC1_CK1_AI_YY | BXX_PLC1 | BXX Date - Year | 15 | No | No | 0 | Yes | No | 0 | 0 | Year | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 9999 | Linear | BXX | No | BXX_PLC1.CK.AI_YY | No | BXX Date - Year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_SN | BXX_PLC1 | BXX Date - Second Setting | 25 | No | No | 0 | Yes | No | 0 | 0 | s | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_PLC1.AO_SN | No | BXX Date - Second Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_F31_AI_CV | BXX_PLC1 | BXX Major Fault Code | 21 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 1000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000 | Linear | BXX | No | BXX_PLC1.MAJOR_FAULT_CODE | No | BXX Major Fault Code | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_F21_AI_CV | BXX_PLC1 | BXX Major Fault Information | 27 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 1000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000 | Linear | BXX | No | BXX_PLC1.MAJOR_FAULT_INFO | No | BXX Major Fault Information | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_SN | BXX_PLC1 | BXX Date - Second | 17 | No | No | 0 | Yes | No | 0 | 0 | s | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_PLC1.CK.AI_SN | No | BXX Date - Second | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_MM | BXX_PLC1 | BXX Date - Month | 16 | No | No | 0 | Yes | No | 0 | 0 | Month | 0 | 0 | 12 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 12 | Linear | BXX | No | BXX_PLC1.CK.AI_MM | No | BXX Date - Month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_MS | BXX_PLC1 | BXX Date - Minutes | 18 | No | No | 0 | Yes | No | 0 | 0 | Min | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_PLC1.CK.AI_MS | No | BXX Date - Minutes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_HS | BXX_PLC1 | BXX Date - Hour | 15 | No | No | 0 | Yes | No | 0 | 0 | Hr | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_PLC1.CK.AI_HS | No | BXX Date - Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AI_DY | BXX_PLC1 | BXX Date - Day | 14 | No | No | 0 | Yes | No | 0 | 0 | Day | 0 | 0 | 31 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 31 | Linear | BXX | No | BXX_PLC1.CK.AI_DY | No | BXX Date - Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_MS | BXX_PLC1 | BXX Date - Minutes Setting | 26 | No | No | 0 | Yes | No | 0 | 0 | Min | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_PLC1.AO_MS | No | BXX Date - Minutes Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_DY | BXX_PLC1 | BXX Date - Day Setting | 22 | No | No | 0 | Yes | No | 0 | 0 | Day | 0 | 0 | 31 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 31 | Linear | BXX | No | BXX_PLC1.CK.AO_DY | No | BXX Date - Day Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_MM | BXX_PLC1 | BXX Date - Month Setting | 24 | No | No | 0 | Yes | No | 0 | 0 | Month | 0 | 0 | 12 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 12 | Linear | BXX | No | BXX_PLC1.AO_MM | No | BXX Date - Month Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_HS | BXX_PLC1 | BXX Date - Hour Setting | 23 | No | No | 0 | Yes | No | 0 | 0 | Hr | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_PLC1.AO_HS | No | BXX Date - Hour Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_CK1_AO_YY | BXX_PLC1 | BXX Date - Year Setting | 23 | No | No | 0 | Yes | No | 0 | 0 | Year | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 9999 | Linear | BXX | No | BXX_PLC1.AO_YY | No | BXX Date - Year Setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_PLC1_F11_AI_CV | BXX_PLC1 | BXX Major Fault Type | 20 | No | No | 0 | Yes | No | 0 | 0 |  | 0 | 0 | 1000 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000 | Linear | BXX | No | BXX_PLC1.MAJOR_FAULT_TYPE | No | BXX Major Fault Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## BXX Alarms
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX | Plant | Station BXX | 11 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_OVF1_FI1_DA_EL | BXX | Station BXX Overflow Loss of Echo | 33 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_OVF1_FI1_DA_EL.eng | No | Station BXX Overflow Loss of Echo | 0 | 0
BXX_OVF1_FI1_PB_EL_RE | BXX | Station BXX Overflow Loss of Echo Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1_DA_EL.RE | No | Station BXX Overflow Loss of Echo Enable | 0 | 0
BXX_OVF1_FI1_PB_EL_DE | BXX | Station BXX Overflow Loss of Echo Dialer En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1_DA_EL.DE | No | Station BXX Overflow Loss of Echo Dialer En | 0 | 0
BXX_OVF1_FI1_PB_EL_SR | BXX | Station BXX Overflow Loss of Echo Super En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1_DA_EL.SR | No | Station BXX Overflow Loss of Echo Super En | 0 | 0
BXX_WW01_LI1_DA_EL | BXX | Station BXX Wet Well 1 Loss of Echo | 35 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_WW01_LI1_DA_EL.eng | No | Station BXX Wet Well 1 Loss of Echo | 0 | 0
BXX_WW01_LI1_PB_EL_RE | BXX | Station BXX Wet Well 1 Loss of Echo Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1_DA_EL.RE | No | Station BXX Wet Well 1 Loss of Echo Enable | 0 | 0
BXX_WW01_LI1_PB_EL_DE | BXX | Station BXX Wet Well 1 Loss of Echo Dialer En | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1_DA_EL.DE | No | Station BXX Wet Well 1 Loss of Echo Dialer En | 0 | 0
BXX_WW01_LI1_PB_EL_SR | BXX | Station BXX Wet Well 1 Loss of Echo Super En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1_DA_EL.SR | No | Station BXX Wet Well 1 Loss of Echo Super En | 0 | 0
BXX_WW01_LE1_DA_HH | BXX | Station BXX Wet Well 1 High Level Float | 39 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_WW01_LE1_DA_HH.eng | No | Station BXX Wet Well 1 High Level Float | 0 | 0
BXX_WW01_LE1_PB_HH_RE | BXX | Station BXX Wet Well 1 High Level Float Enable | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LE1_DA_HH.RE | No | Station BXX Wet Well 1 High Level Float Enable | 0 | 0
BXX_WW01_LE1_PB_HH_DE | BXX | Station BXX Wet Well 1 High Level Float Dialer En | 49 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LE1_DA_HH.DE | No | Station BXX Wet Well 1 High Level Float Dialer En | 0 | 0
BXX_WW01_LE1_PB_HH_SR | BXX | Station BXX Wet Well 1 High Level Float Super En | 48 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LE1_DA_HH.SR | No | Station BXX Wet Well 1 High Level Float Super En | 0 | 0
BXX_WW02_LI1_DA_EL | BXX | Station BXX Wet Well 2 Loss of Echo | 35 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_WW02_LI1_DA_EL.eng | No | Station BXX Wet Well 2 Loss of Echo | 0 | 0
BXX_WW02_LI1_PB_EL_RE | BXX | Station BXX Wet Well 2 Loss of Echo Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1_DA_EL.RE | No | Station BXX Wet Well 2 Loss of Echo Enable | 0 | 0
BXX_WW02_LI1_PB_EL_DE | BXX | Station BXX Wet Well 2 Loss of Echo Dialer En | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1_DA_EL.DE | No | Station BXX Wet Well 2 Loss of Echo Dialer En | 0 | 0
BXX_WW02_LI1_PB_EL_SR | BXX | Station BXX Wet Well 2 Loss of Echo Super En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1_DA_EL.SR | No | Station BXX Wet Well 2 Loss of Echo Super En | 0 | 0
BXX_WW02_LE1_DA_HH | BXX | Station BXX Wet Well 2 High Level Float | 39 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_WW02_LE1_DA_HH.eng | No | Station BXX Wet Well 2 High Level Float | 0 | 0
BXX_WW02_LE1_PB_HH_RE | BXX | Station BXX Wet Well 2 High Level Float Enable | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LE1_DA_HH.RE | No | Station BXX Wet Well 2 High Level Float Enable | 0 | 0
BXX_WW02_LE1_PB_HH_DE | BXX | Station BXX Wet Well 2 High Level Float Dialer En | 49 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LE1_DA_HH.DE | No | Station BXX Wet Well 2 High Level Float Dialer En | 0 | 0
BXX_WW02_LE1_PB_HH_SR | BXX | Station BXX Wet Well 2 High Level Float Super En | 48 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LE1_DA_HH.SR | No | Station BXX Wet Well 2 High Level Float Super En | 0 | 0
BXX_PSB1_CP1_DA_JR | BXX | Station BXX Control Power Failure | 33 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_PSB1_CP1_DA_JR.eng | No | Station BXX Control Power Failure | 0 | 0
BXX_PSB1_CP1_PB_JR_RE | BXX | Station BXX Control Power Failure Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_CP1_DA_JR.RE | No | Station BXX Control Power Failure Enable | 0 | 0
BXX_PSB1_CP1_PB_JR_DE | BXX | Station BXX Control Power Failure Dialer En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_CP1_DA_JR.DE | No | Station BXX Control Power Failure Dialer En | 0 | 0
BXX_PSB1_CP1_PB_JR_SR | BXX | Station BXX Control Power Failure Super En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_CP1_DA_JR.SR | No | Station BXX Control Power Failure Super En | 0 | 0
BXX_UPS1_001_DA_GA | BXX | Station BXX Main UPS Fault | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_UPS1_001_DA_GA.eng | No | Station BXX Main UPS Fault | 0 | 0
BXX_UPS1_001_PB_GA_RE | BXX | Station BXX Main UPS Fault Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_001_DA_GA.RE | No | Station BXX Main UPS Fault Enable | 0 | 0
BXX_UPS1_001_PB_GA_DE | BXX | Station BXX Main UPS Fault Dialer En | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_001_DA_GA.DE | No | Station BXX Main UPS Fault Dialer En | 0 | 0
BXX_UPS1_001_PB_GA_SR | BXX | Station BXX Main UPS Fault Super En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_001_DA_GA.SR | No | Station BXX Main UPS Fault Super En | 0 | 0
BXX_UPS1_BT1_DA_JL | BXX | Station BXX Main UPS Low Battery | 32 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_UPS1_BT1_DA_JL.eng | No | Station BXX Main UPS Low Battery | 0 | 0
BXX_UPS1_BT1_PB_JL_RE | BXX | Station BXX Main UPS Low Battery Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_BT1_DA_JL.RE | No | Station BXX Main UPS Low Battery Enable | 0 | 0
BXX_UPS1_BT1_PB_JL_DE | BXX | Station BXX Main UPS Low Battery Dialer En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_BT1_DA_JL.DE | No | Station BXX Main UPS Low Battery Dialer En | 0 | 0
BXX_UPS1_BT1_PB_JL_SR | BXX | Station BXX Main UPS Low Battery Super En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS1_BT1_DA_JL.SR | No | Station BXX Main UPS Low Battery Super En | 0 | 0
BXX_PSB1_JI1_DA_GA | BXX | Station BXX Phase Failure | 25 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_PSB1_JI1_DA_GA.eng | No | Station BXX Phase Failure | 0 | 0
BXX_PSB1_JI1_PB_GA_RE | BXX | Station BXX Phase Failure Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_GA.RE | No | Station BXX Phase Failure Enable | 0 | 0
BXX_PSB1_JI1_PB_GA_DE | BXX | Station BXX Phase Failure Dialer En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_GA.DE | No | Station BXX Phase Failure Dialer En | 0 | 0
BXX_PSB1_JI1_PB_GA_SR | BXX | Station BXX Phase Failure Super En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_GA.SR | No | Station BXX Phase Failure Super En | 0 | 0
BXX_DDT1_LS1_DA_KA | BXX | Station BXX Diesel Flood | 24 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_DDT1_LS1_DA_KA.eng | No | Station BXX Diesel Flood | 0 | 0
BXX_DDT1_LS1_PB_KA_RE | BXX | Station BXX Diesel Flood Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDT1_LS1_DA_KA.RE | No | Station BXX Diesel Flood Enable | 0 | 0
BXX_DDT1_LS1_PB_KA_DE | BXX | Station BXX Diesel Flood Dialer En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDT1_LS1_DA_KA.DE | No | Station BXX Diesel Flood Dialer En | 0 | 0
BXX_DDT1_LS1_PB_KA_SR | BXX | Station BXX Diesel Flood Super En | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDT1_LS1_DA_KA.SR | No | Station BXX Diesel Flood Super En | 0 | 0
BXX_DDV1_LS1_DA_KA | BXX | Station BXX Diesel Tank Loss Vac Alarm | 38 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_DDV1_LS1_DA_KA.eng | No | Station BXX Diesel Tank Loss Vac Alarm | 0 | 0
BXX_DDV1_LS1_PB_KA_RE | BXX | Station BXX Diesel Tank Loss Vac Alarm Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDV1_LS1_DA_KA.RE | No | Station BXX Diesel Tank Loss Vac Alarm Enable | 0 | 0
BXX_DDV1_LS1_PB_KA_DE | BXX | Station BXX Diesel Tank Loss Vac Alarm Dialer En | 48 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDV1_LS1_DA_KA.DE | No | Station BXX Diesel Tank Loss Vac Alarm Dialer En | 0 | 0
BXX_DDV1_LS1_PB_KA_SR | BXX | Station BXX Diesel Tank Loss Vac Alarm Super En | 47 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DDV1_LS1_DA_KA.SR | No | Station BXX Diesel Tank Loss Vac Alarm Super En | 0 | 0
BXX_PSB1_JI1_DA_NF | BXX | Station BXX Ground Fault | 24 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_PSB1_JI1_DA_NF.eng | No | Station BXX Ground Fault | 0 | 0
BXX_PSB1_JI1_PB_NF_RE | BXX | Station BXX Ground Fault Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_NF.RE | No | Station BXX Ground Fault Enable | 0 | 0
BXX_PSB1_JI1_PB_NF_DE | BXX | Station BXX Ground Fault Dialer En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_NF.DE | No | Station BXX Ground Fault Dialer En | 0 | 0
BXX_PSB1_JI1_PB_NF_SR | BXX | Station BXX Ground Fault Super En | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_JI1_DA_NF.SR | No | Station BXX Ground Fault Super En | 0 | 0
BXX_GEN1_VV1_DA_SF | BXX | Station BXX Louver Failed to Open | 33 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_GEN1_VV1_DA_SF.eng | No | Station BXX Louver Failed to Open | 0 | 0
BXX_GEN1_VV1_PB_SF_RE | BXX | Station BXX Louver Failed to Open Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_VV1_DA_SF.RE | No | Station BXX Louver Failed to Open Enable | 0 | 0
BXX_GEN1_VV1_PB_SF_DE | BXX | Station BXX Louver Failed to Open Dialer En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_VV1_DA_SF.DE | No | Station BXX Louver Failed to Open Dialer En | 0 | 0
BXX_GEN1_VV1_PB_SF_SR | BXX | Station BXX Louver Failed to Open Super En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_VV1_DA_SF.SR | No | Station BXX Louver Failed to Open Super En | 0 | 0
BXX_PSB1_TI1_DA_TL | BXX | Station BXX Low Temperature | 27 | No | No | 0 | Yes | Off | Normal | Alarm | On | 57 | Direct | BXX | No | BXX_PSB1_TI1_DA_TL.eng | No | Station BXX Low Temperature | 0 | 0
BXX_PSB1_TI1_PB_TL_RE | BXX | Station BXX Low Temperature Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TL.RE | No | Station BXX Low Temperature Enable | 0 | 0
BXX_PSB1_TI1_PB_TL_DE | BXX | Station BXX Low Temperature Dialer En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TL.DE | No | Station BXX Low Temperature Dialer En | 0 | 0
BXX_PSB1_TI1_PB_TL_SR | BXX | Station BXX Low Temperature Super En | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TL.SR | No | Station BXX Low Temperature Super En | 0 | 0
BXX_PSB1_TI1_DA_TH | BXX | Station BXX High Temperature | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 56 | Direct | BXX | No | BXX_PSB1_TI1_DA_TH.eng | No | Station BXX High Temperature | 0 | 0
BXX_PSB1_TI1_PB_TH_RE | BXX | Station BXX High Temperature Enable | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TH.RE | No | Station BXX High Temperature Enable | 0 | 0
BXX_PSB1_TI1_PB_TH_DE | BXX | Station BXX High Temperature Dialer En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TH.DE | No | Station BXX High Temperature Dialer En | 0 | 0
BXX_PSB1_TI1_PB_TH_SR | BXX | Station BXX High Temperature Super En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_TI1_DA_TH.SR | No | Station BXX High Temperature Super En | 0 | 0
BXX_DW01_LE1_DA_KA | BXX | Station BXX Dry Well Flood | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_DW01_LE1_DA_KA.eng | No | Station BXX Dry Well Flood | 0 | 0
BXX_DW01_LE1_PB_KA_RE | BXX | Station BXX Dry Well Flood Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DW01_LE1_DA_KA.RE | No | Station BXX Dry Well Flood Enable | 0 | 0
BXX_DW01_LE1_PB_KA_DE | BXX | Station BXX Dry Well Flood Dialer En | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DW01_LE1_DA_KA.DE | No | Station BXX Dry Well Flood Dialer En | 0 | 0
BXX_DW01_LE1_PB_KA_SR | BXX | Station BXX Dry Well Flood Super En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DW01_LE1_DA_KA.SR | No | Station BXX Dry Well Flood Super En | 0 | 0
BXX_PSB1_001_DA_YA | BXX | Station BXX Fire Alarm | 22 | No | No | 0 | Yes | Off | Normal | Alarm | On | 1 | Direct | BXX | No | BXX_PSB1_001_DA_YA.eng | No | Station BXX Fire Alarm | 0 | 0
BXX_PSB1_001_PB_YA_RE | BXX | Station BXX Fire Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_001_DA_YA.RE | No | Station BXX Fire Alarm Enable | 0 | 0
BXX_PSB1_001_PB_YA_DE | BXX | Station BXX Fire Alarm Dialer En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_001_DA_YA.DE | No | Station BXX Fire Alarm Dialer En | 0 | 0
BXX_PSB1_001_PB_YA_SR | BXX | Station BXX Fire Alarm Super En | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSB1_001_DA_YA.SR | No | Station BXX Fire Alarm Super En | 0 | 0
BXX_GDS1_GI1_DA_AR | BXX | Station BXX Gas Detector Failure | 32 | No | No | 0 | Yes | Off | Normal | Alarm | On | 12 | Direct | BXX | No | BXX_GDS1_GI1_DA_AR.eng | No | Station BXX Gas Detector Failure | 0 | 0
BXX_GDS1_GI1_PB_AR_RE | BXX | Station BXX Gas Detector Failure Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AR.RE | No | Station BXX Gas Detector Failure Enable | 0 | 0
BXX_GDS1_GI1_PB_AR_DE | BXX | Station BXX Gas Detector Failure Dialer En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AR.DE | No | Station BXX Gas Detector Failure Dialer En | 0 | 0
BXX_GDS1_GI1_PB_AR_SR | BXX | Station BXX Gas Detector Failure Super En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AR.SR | No | Station BXX Gas Detector Failure Super En | 0 | 0
BXX_GDS1_GI1_DA_AG | BXX | Station BXX Gas Detector Alarm | 30 | No | No | 0 | Yes | Off | Normal | Alarm | On | 10 | Direct | BXX | No | BXX_GDS1_GI1_DA_AG.eng | No | Station BXX Gas Detector Alarm | 0 | 0
BXX_GDS1_GI1_PB_AG_RE | BXX | Station BXX Gas Detector Alarm Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AG.RE | No | Station BXX Gas Detector Alarm Enable | 0 | 0
BXX_GDS1_GI1_PB_AG_DE | BXX | Station BXX Gas Detector Alarm Dialer En | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AG.DE | No | Station BXX Gas Detector Alarm Dialer En | 0 | 0
BXX_GDS1_GI1_PB_AG_SR | BXX | Station BXX Gas Detector Alarm Super En | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AG.SR | No | Station BXX Gas Detector Alarm Super En | 0 | 0
BXX_GDS1_GI1_DA_AW | BXX | Station BXX Gas Detector Warning | 32 | No | No | 0 | Yes | Off | Normal | Alarm | On | 310 | Direct | BXX | No | BXX_GDS1_GI1_DA_AW.eng | No | Station BXX Gas Detector Warning | 0 | 0
BXX_GDS1_GI1_PB_AW_RE | BXX | Station BXX Gas Detector Warning Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AW.RE | No | Station BXX Gas Detector Warning Enable | 0 | 0
BXX_GDS1_GI1_PB_AW_DE | BXX | Station BXX Gas Detector Warning Dialer En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AW.DE | No | Station BXX Gas Detector Warning Dialer En | 0 | 0
BXX_GDS1_GI1_PB_AW_SR | BXX | Station BXX Gas Detector Warning Super En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GDS1_GI1_DA_AW.SR | No | Station BXX Gas Detector Warning Super En | 0 | 0
BXX_PSU1_001_DA_GA | BXX | Station BXX Main 24VDC Power Fault | 34 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_PSU1_001_DA_GA.eng | No | Station BXX Main 24VDC Power Fault | 0 | 0
BXX_PSU1_001_PB_GA_RE | BXX | Station BXX Main 24VDC Power Fault Enable | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSU1_001_DA_GA.RE | No | Station BXX Main 24VDC Power Fault Enable | 0 | 0
BXX_PSU1_001_PB_GA_DE | BXX | Station BXX Main 24VDC Power Fault Dialer En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSU1_001_DA_GA.DE | No | Station BXX Main 24VDC Power Fault Dialer En | 0 | 0
BXX_PSU1_001_PB_GA_SR | BXX | Station BXX Main 24VDC Power Fault Super En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_PSU1_001_DA_GA.SR | No | Station BXX Main 24VDC Power Fault Super En | 0 | 0
BXX_BLS1_CP1_DA_GA | BXX | Station BXX Backup 24VDC Power Fault | 36 | No | No | 0 | Yes | Off | Normal | Alarm | On | 48 | Direct | BXX | No | BXX_BLS1_CP1_DA_GA.eng | No | Station BXX Backup 24VDC Power Fault | 0 | 0
BXX_BLS1_CP1_PB_GA_RE | BXX | Station BXX Backup 24VDC Power Fault Enable | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_CP1_DA_GA.RE | No | Station BXX Backup 24VDC Power Fault Enable | 0 | 0
BXX_BLS1_CP1_PB_GA_DE | BXX | Station BXX Backup 24VDC Power Fault Dialer En | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_CP1_DA_GA.DE | No | Station BXX Backup 24VDC Power Fault Dialer En | 0 | 0
BXX_BLS1_CP1_PB_GA_SR | BXX | Station BXX Backup 24VDC Power Fault Super En | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_CP1_DA_GA.SR | No | Station BXX Backup 24VDC Power Fault Super En | 0 | 0
BXX_STN1_EY1_DA_SS | BXX | Station BXX Eyewash Station Active | 34 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_STN1_EY1_DA_SS.eng | No | Station BXX Eyewash Station Active | 0 | 0
BXX_STN1_EY1_PB_SS_RE | BXX | Station BXX Eyewash Station Active Enable | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_EY1_DA_SS.RE | No | Station BXX Eyewash Station Active Enable | 0 | 0
BXX_STN1_EY1_PB_SS_DE | BXX | Station BXX Eyewash Station Active Dialer En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_EY1_DA_SS.DE | No | Station BXX Eyewash Station Active Dialer En | 0 | 0
BXX_STN1_EY1_PB_SS_SR | BXX | Station BXX Eyewash Station Active Super En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_EY1_DA_SS.SR | No | Station BXX Eyewash Station Active Super En | 0 | 0
BXX_UPS2_001_DA_GA | BXX | Station BXX Backup UPS Fault | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_UPS2_001_DA_GA.eng | No | Station BXX Backup UPS Fault | 0 | 0
BXX_UPS2_001_PB_GA_RE | BXX | Station BXX Backup UPS Fault Enable | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS2_001_DA_GA.RE | No | Station BXX Backup UPS Fault Enable | 0 | 0
BXX_UPS2_001_PB_GA_DE | BXX | Station BXX Backup UPS Fault Dialer En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS2_001_DA_GA.DE | No | Station BXX Backup UPS Fault Dialer En | 0 | 0
BXX_UPS2_001_PB_GA_SR | BXX | Station BXX Backup UPS Fault Super En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS2_001_DA_GA.SR | No | Station BXX Backup UPS Fault Super En | 0 | 0
BXX_UPS2_BT1_DA_JL | BXX | Station BXX Backup UPS Low Battery | 34 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_UPS2_BT1_DA_JL.eng | No | Station BXX Backup UPS Low Battery | 0 | 0
BXX_UPS2_BT1_PB_JL_RE | BXX | Station BXX Backup UPS Low Battery Enable | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS2_BT1_DA_JL.RE | No | Station BXX Backup UPS Low Battery Enable | 0 | 0
BXX_UPS2_BT1_PB_JL_DE | BXX | Station BXX Backup UPS Low Battery Dialer En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS2_BT1_DA_JL.DE | No | Station BXX Backup UPS Low Battery Dialer En | 0 | 0
BXX_UPS2_BT1_PB_JL_SR | BXX | Station BXX Backup UPS Low Battery Super En | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_UPS2_BT1_DA_JL.SR | No | Station BXX Backup UPS Low Battery Super En | 0 | 0
BXX_GEN1_JI1_DA_CD | BXX | Station BXX Generator Breaker Not Closed | 40 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_GEN1_JI1_DA_CD.eng | No | Station BXX Generator Breaker Not Closed | 0 | 0
BXX_GEN1_JI1_PB_CD_RE | BXX | Station BXX Generator Breaker Not Closed Enable | 47 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_JI1_DA_CD.RE | No | Station BXX Generator Breaker Not Closed Enable | 0 | 0
BXX_GEN1_JI1_PB_CD_DE | BXX | Station BXX Generator Breaker Not Closed Dialer En | 50 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_JI1_DA_CD.DE | No | Station BXX Generator Breaker Not Closed Dialer En | 0 | 0
BXX_GEN1_JI1_PB_CD_SR | BXX | Station BXX Generator Breaker Not Closed Super En | 49 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_JI1_DA_CD.SR | No | Station BXX Generator Breaker Not Closed Super En | 0 | 0
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_OVF1_FI1_PB_EL_RN | BXX | Station BXX Overflow Loss of Echo Dis Reason | 44 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_EL_RN | No | Station BXX Overflow Loss of Echo Dis Reason |  |  |  |  | 0 | 0
BXX_WW01_LI1_PB_EL_RN | BXX | Station BXX Wet Well 1 Loss of Echo Dis Reason | 46 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW01_LI1_PB_EL_RN | No | Station BXX Wet Well 1 Loss of Echo Dis Reason
BXX_WW01_LE1_PB_HH_RN | BXX | Station BXX Wet Well 1 High Level Float Dis Reason | 50 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW01_LE1_PB_HH_RN | No | Station BXX Wet Well 1 High Level Float Dis Reason
BXX_WW02_LI1_PB_EL_RN | BXX | Station BXX Wet Well 2 Loss of Echo Dis Reason | 46 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW02_LI1_PB_EL_RN | No | Station BXX Wet Well 2 Loss of Echo Dis Reason
BXX_WW02_LE1_PB_HH_RN | BXX | Station BXX Wet Well 2 High Level Float Dis Reason | 50 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW02_LE1_PB_HH_RN | No | Station BXX Wet Well 2 High Level Float Dis Reason
BXX_PSB1_CP1_PB_JR_RN | BXX | Station BXX Control Power Failure Dis Reason | 44 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_CP1_PB_JR_RN | No | Station BXX Control Power Failure Dis Reason
BXX_UPS1_001_PB_GA_RN | BXX | Station BXX Main UPS Fault Dis Reason | 37 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_UPS1_001_PB_GA_RN | No | Station BXX Main UPS Fault Dis Reason
BXX_UPS1_BT1_PB_JL_RN | BXX | Station BXX Main UPS Low Battery Dis Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_UPS1_BT1_PB_JL_RN | No | Station BXX Main UPS Low Battery Dis Reason
BXX_PSB1_JI1_PB_GA_RN | BXX | Station BXX Phase Failure Dis Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_JI1_PB_GA_RN | No | Station BXX Phase Failure Dis Reason
BXX_DDT1_LS1_PB_KA_RN | BXX | Station BXX Diesel Flood Dis Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DDT1_LS1_PB_KA_RN | No | Station BXX Diesel Flood Dis Reason
BXX_DDV1_LS1_PB_KA_RN | BXX | Station BXX Diesel Tank Loss Vac Alarm Dis Reason | 49 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DDV1_LS1_PB_KA_RN | No | Station BXX Diesel Tank Loss Vac Alarm Dis Reason
BXX_PSB1_JI1_PB_NF_RN | BXX | Station BXX Ground Fault Dis Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_JI1_PB_NF_RN | No | Station BXX Ground Fault Dis Reason
BXX_GEN1_VV1_PB_SF_RN | BXX | Station BXX Louver Failed to Open Dis Reason | 44 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_VV1_PB_SF_RN | No | Station BXX Louver Failed to Open Dis Reason
BXX_PSB1_TI1_PB_TL_RN | BXX | Station BXX Low Temperature Dis Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_TI1_PB_TL_RN | No | Station BXX Low Temperature Dis Reason
BXX_PSB1_TI1_PB_TH_RN | BXX | Station BXX High Temperature Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_TI1_PB_TH_RN | No | Station BXX High Temperature Dis Reason
BXX_DW01_LE1_PB_KA_RN | BXX | Station BXX High Temperature Enable Dis Reason | 46 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DW01_LE1_PB_KA_RN | No | Station BXX High Temperature Enable Dis Reason
BXX_PSB1_001_PB_YA_RN | BXX | Station BXX High Temperature Dialer En Dis Reason | 49 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSB1_001_PB_YA_RN | No | Station BXX High Temperature Dialer En Dis Reason
BXX_GDS1_GI1_PB_AR_RN | BXX | Station BXX Gas Detector Failure Dis Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GDS1_GI1_PB_AR_RN | No | Station BXX Gas Detector Failure Dis Reason
BXX_GDS1_GI1_PB_AG_RN | BXX | Station BXX Gas Detector Alarm Dis Reason | 41 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GDS1_GI1_PB_AG_RN | No | Station BXX Gas Detector Alarm Dis Reason
BXX_GDS1_GI1_PB_AW_RN | BXX | Station BXX Gas Detector Warning Dis Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GDS1_GI1_PB_AW_RN | No | Station BXX Gas Detector Warning Dis Reason
BXX_PSU1_001_PB_GA_RN | BXX | Station BXX Main 24VDC Power Fault Dis Reason | 45 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_PSU1_001_PB_GA_RN | No | Station BXX Main 24VDC Power Fault Dis Reason
BXX_BLS1_CP1_PB_GA_RN | BXX | Station BXX Backup 24VDC Power Fault Dis Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_BLS1_CP1_PB_GA_RN | No | Station BXX Backup 24VDC Power Fault Dis Reason
BXX_STN1_EY1_PB_SS_RN | BXX | Station BXX Eyewash Station Active Dis Reason | 45 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_STN1_EY1_PB_SS_RN | No | Station BXX Eyewash Station Active Dis Reason
BXX_UPS2_001_PB_GA_RN | BXX | Station BXX Backup UPS Fault Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_UPS2_001_PB_GA_RN | No | Station BXX Backup UPS Fault Dis Reason
BXX_UPS2_BT1_PB_JL_RN | BXX | Station BXX Backup UPS Low Battery Dis Reason | 45 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_UPS2_BT1_PB_JL_RN | No | Station BXX Backup UPS Low Battery Dis Reason
BXX_GEN1_JI1_PB_CD_RN | BXX | Station BXX Generator Breaker Not Closed Dis Rsn | 48 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_JI1_PB_CD_RN | No | Station BXX Generator Breaker Not Closed Dis Rsn

## BXX Security
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX | Plant | Station BXX | 11 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_STN1_KS1 | BXX | Station BXX Security | 20 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_PSB1_KS1_DI_DE | BXX_STN1_KS1 | Station BXX Security Keyswitch | 30 | Yes | No | 700 | Yes | Off | Armed | Disarmed | None | 1 | Direct | BXX | No | BXX_PSB1_KS1_DI_DE.eng | No | Station BXX Security Keyswitch | 0 | 0
BXX_DR01_TO1_DI_SI | BXX_STN1_KS1 | Station BXX Door Contact | 24 | Yes | No | 700 | Yes | Off | Open | Closed | None | 1 | Direct | BXX | No | BXX_DR01_TO1_DI_SI.eng | No | Station BXX Door Contact | 0 | 0
BXX_STN1_TO1_DI_SI | BXX_STN1_KS1 | Station BXX Security Monitor | 28 | Yes | No | 700 | Yes | Off | Disarmed | Armed | None | 1 | Direct | BXX | No | BXX_STN1_TO1_DI_SI.eng | No | Station BXX Security Monitor | 0 | 0
BXX_STN1_TO1_DA_EA | BXX_STN1_KS1 | Station BXX Legal Entry | 23 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_STN1_TO1_DA_EA.eng | No | Station BXX Legal Entry | 0 | 0
BXX_STN1_TO1_PB_EA_RE | BXX_STN1_KS1 | Station BXX Legal Entry Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_TO1_DA_EA.RE | No | Station BXX Legal Entry Enable | 0 | 0
BXX_STN1_TO1_PB_EA_DE | BXX_STN1_KS1 | Station BXX Legal Entry Dialer En | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_TO1_DA_EA.DE | No | Station BXX Legal Entry Dialer En | 0 | 0
BXX_STN1_TO1_PB_EA_SR | BXX_STN1_KS1 | Station BXX Legal Entry Super En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_TO1_DA_EA.SR | No | Station BXX Legal Entry Super En | 0 | 0
BXX_STN1_TO1_DA_SI | BXX_STN1_KS1 | Station BXX Illegal Entry | 25 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_STN1_TO1_DA_SI.eng | No | Station BXX Illegal Entry | 0 | 0
BXX_STN1_TO1_PB_SI_RE | BXX_STN1_KS1 | Station BXX Illegal Entry Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_TO1_DA_SI.RE | No | Station BXX Illegal Entry Enable | 0 | 0
BXX_STN1_TO1_PB_SI_DE | BXX_STN1_KS1 | Station BXX Illegal Entry Dialer En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_TO1_DA_SI.DE | No | Station BXX Illegal Entry Dialer En | 0 | 0
BXX_STN1_TO1_PB_SI_SR | BXX_STN1_KS1 | Station BXX Illegal Entry Super En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_STN1_TO1_DA_SI.SR | No | Station BXX Illegal Entry Super En | 0 | 0
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_STN1_TO1_PB_EA_RN | BXX | Station BXX Legal Entry Dis Reason | 34 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_STN1_TO1_PB_EA_RN | No | Station BXX Legal Entry Dis Reason
BXX_STN1_TO1_PB_SI_RN | BXX | Station BXX Illegal Entry Dis Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_STN1_TO1_PB_SI_RN | No | Station BXX Illegal Entry Dis Reason

## BXX Other Discretes
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX | Plant | Station BXX | 11 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_BPC1_LM1_DA_RS | BXX | Station BXX on Backup Control | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_BPC1_LM1_DA_RS.eng | No | Station BXX on Backup Control | 0 | 0

## BXXDIH1PI1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DIH1_PI1 | BXX | BXX Disch. Pressure | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DIH1_PI1_DI_AD | BXX_DSAB | BXX Disch. Pressure Disabled Analog Alarm | 41 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_DIH1_PI1.DI_AD | No | BXX Disch. Pressure Disabled Analog Alarm | 0 | 0
BXX_DIH1_PI1_DI_SC | BXX_DIH1_PI1 | BXX Disch. Pressure Scan Status | 31 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.DI_SC | No | BXX Disch. Pressure Scan Status | 0 | 0
BXX_DIH1_PI1_DA_LL | BXX_DIH1_PI1 | BXX Disch. Pressure LOLO Alarm | 30 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DIH1_PI1DA_LL | No | BXX Disch. Pressure LOLO Alarm | 0 | 0
BXX_DIH1_PI1_DA_ER | BXX_DIH1_PI1 | BXX Disch. Pressure Signal Error Alarm | 38 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DIH1_PI1DA_ER | No | BXX Disch. Pressure Signal Error Alarm | 0 | 0
BXX_DIH1_PI1_PB_SM | BXX_DIH1_PI1 | BXX Disch. Pressure Alarm Test | 30 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_SM | No | BXX Disch. Pressure Alarm Test | 0 | 0
BXX_DIH1_PI1_PB_SV | BXX_DIH1_PI1 | BXX Disch. Pressure Override Enable | 35 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_SV | No | BXX Disch. Pressure Override Enable | 0 | 0
BXX_DIH1_PI1_PB_AE | BXX_DIH1_PI1 | BXX Disch. Pressure Alarm Enable | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_AE.RE | No | BXX Disch. Pressure Alarm Enable | 0 | 0
BXX_DIH1_PI1_PB_HI | BXX_DIH1_PI1 | BXX Disch. Pressure High Alarm Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_HI.RE | No | BXX Disch. Pressure High Alarm Enable | 0 | 0
BXX_DIH1_PI1_PB_LO | BXX_DIH1_PI1 | BXX Disch. Pressure Low Alarm Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_LO.RE | No | BXX Disch. Pressure Low Alarm Enable | 0 | 0
BXX_DIH1_PI1_PB_LL | BXX_DIH1_PI1 | BXX Disch. Pressure LOLO Alarm Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_LL.RE | No | BXX Disch. Pressure LOLO Alarm Enable | 0 | 0
BXX_DIH1_PI1_PB_ER | BXX_DIH1_PI1 | BXX Disch. Pressure Signal Error Alarm En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_ER.RE | No | BXX Disch. Pressure Signal Error Alarm En | 0 | 0
BXX_DIH1_PI1_PB_SC | BXX_DIH1_PI1 | BXX Disch. Pressure Scan Enable | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_SC | No | BXX Disch. Pressure Scan Enable | 0 | 0
BXX_DIH1_PI1_DA_HH | BXX_DIH1_PI1 | BXX Disch. Pressure HIHI Alarm | 30 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DIH1_PI1DA_HH | No | BXX Disch. Pressure HIHI Alarm | 0 | 0
BXX_DIH1_PI1_DA_HI | BXX_DIH1_PI1 | BXX Disch. Pressure HI Alarm | 28 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DIH1_PI1DA_HI | No | BXX Disch. Pressure HI Alarm | 0 | 0
BXX_DIH1_PI1_PB_HH | BXX_DIH1_PI1 | BXX Disch. Pressure HIHI Alarm Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_HH.RE | No | BXX Disch. Pressure HIHI Alarm Enable | 0 | 0
BXX_DIH1_PI1_PB_AR | BXX_DIH1_PI1 | BXX Disch. Pressure Alarm Reset | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_AR | No | BXX Disch. Pressure Alarm Reset | 0 | 0
BXX_DIH1_PI1_DA_LO | BXX_DIH1_PI1 | BXX Disch. Pressure LO Alarm | 28 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DIH1_PI1DA_LO | No | BXX Disch. Pressure LO Alarm | 0 | 0
BXX_DIH1_PI1_PB_LL_DE | BXX_DIH1_PI1 | BXX Disch. Pressure LOLO Alarm Dialer Enable | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_LL.DE | No | BXX Disch. Pressure LOLO Alarm Dialer Enable | 0 | 0
BXX_DIH1_PI1_PB_ER_DE | BXX_DIH1_PI1 | BXX Disch. Pressure Sig Error Alarm Dialer En | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_ER.DE | No | BXX Disch. Pressure Sig Error Alarm Dialer En | 0 | 0
BXX_DIH1_PI1_PB_HH_DE | BXX_DIH1_PI1 | BXX Disch. Pressure HIHI Alarm Dialer Enable | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_HH.DE | No | BXX Disch. Pressure HIHI Alarm Dialer Enable | 0 | 0
BXX_DIH1_PI1_PB_LL_SR | BXX_DIH1_PI1 | BXX Disch. Pressure LOLO Alarm Sup Enable | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_LL.SR | No | BXX Disch. Pressure LOLO Alarm Sup Enable | 0 | 0
BXX_DIH1_PI1_PB_ER_SR | BXX_DIH1_PI1 | BXX Disch. Pressure Signal Error Alarm Sup En | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_ER.SR | No | BXX Disch. Pressure Signal Error Alarm Sup En | 0 | 0
BXX_DIH1_PI1_PB_HH_SR | BXX_DIH1_PI1 | BXX Disch. Pressure HIHI Alarm Sup Enable | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_PI1.PB_HH.SR | No | BXX Disch. Pressure HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DIH1_PI1_AI_VI | BXX_DIH1_PI1 | BXX Disch. Pressure Number of Vis Eng Values | 44 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_DIH1_PI1.AI_VI | No | BXX Disch. Pressure Number of Vis Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_AI_DC | BXX_DIH1_PI1 | BXX Disch. Pressure Precision | 29 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DIH1_PI1.AI_DC | No | BXX Disch. Pressure Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DIH1_PI1_SN_LL | BXX_DIH1_PI1 | BXX Disch. Pressure LOLO Alarm Delay | 36 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DIH1_PI1SN_LL | No | BXX Disch. Pressure LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_SN_HI | BXX_DIH1_PI1 | BXX Disch. Pressure High Alarm Delay | 36 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DIH1_PI1SN_HI | No | BXX Disch. Pressure High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_AI_CV | BXX_DIH1_PI1 | BXX Disch. Pressure Current Value | 33 | Yes | No | 0 | Yes | No | 0 | 0 | kPa | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_PI1.AI_CV | No | BXX Disch. Pressure Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_AO_XM | BXX_DIH1_PI1 | BXX Disch. Pressure Span Setpoint | 33 | No | Yes | 900 | Yes | No | 0 | 0 | kPa | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_PI1.AO_XM | No | BXX Disch. Pressure Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_AO_LO | BXX_DIH1_PI1 | BXX Disch. Pressure Low Setpoint | 32 | No | Yes | 900 | Yes | No | 0 | 0 | kPa | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_PI1.AO_LO | No | BXX Disch. Pressure Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_AO_HH | BXX_DIH1_PI1 | BXX Disch. Pressure HIHI Setpoint | 33 | No | Yes | 900 | Yes | No | 0 | 0 | kPa | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_PI1.AO_HH | No | BXX Disch. Pressure HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_AO_HI | BXX_DIH1_PI1 | BXX Disch. Pressure High Setpoint | 33 | No | Yes | 900 | Yes | No | 0 | 0 | kPa | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_PI1.AO_HI | No | BXX Disch. Pressure High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_AO_SV | BXX_DIH1_PI1 | BXX Disch. Pressure Override Value | 34 | No | Yes | 900 | Yes | No | 0 | 0 | kPa | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_PI1.AO_SV | No | BXX Disch. Pressure Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_AO_EM | BXX_DIH1_PI1 | BXX Disch. Pressure Zero Setpoint | 33 | No | Yes | 900 | Yes | No | 0 | 0 | kPa | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_PI1.AO_EM | No | BXX Disch. Pressure Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_SN_HH | BXX_DIH1_PI1 | BXX Disch. Pressure HIHI Alarm Delay | 36 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DIH1_PI1SN_HH | No | BXX Disch. Pressure HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_SN_LO | BXX_DIH1_PI1 | BXX Disch. Pressure Low Alarm Delay | 35 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DIH1_PI1SN_LO | No | BXX Disch. Pressure Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_PI1_AO_LL | BXX_DIH1_PI1 | BXX Disch. Pressure LOLO Setpoint | 33 | No | Yes | 900 | Yes | No | 0 | 0 | kPa | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_PI1.AO_LL | No | BXX Disch. Pressure LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_DIH1_PI1_DI_NM | BXX_DIH1_PI1 | BXX_DIH1_PI1 | 12 | No | No | 0 | Yes | 24 | BXX_DIH1_PI1 | BXX_DIH1_PI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_DIH1_PI1_PB_HH_RN | BXX_DIH1_PI1 | BXX Disch. Pressure HIHI Alarm Disabled Reason | 46 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DIH1_PI1_PB_HH_RN | No | BXX Disch. Pressure HIHI Alarm Disabled Reason
BXX_DIH1_PI1_PB_LL_RN | BXX_DIH1_PI1 | BXX Disch. Pressure LOLO Alarm Disabled Reason | 46 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DIH1_PI1_PB_LL_RN | No | BXX Disch. Pressure LOLO Alarm Disabled Reason
BXX_DIH1_PI1_PB_ER_RN | BXX_DIH1_PI1 | BXX Disch. Pressure Sig Error Alarm Dis Reason | 46 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DIH1_PI1_PB_ER_RN | No | BXX Disch. Pressure Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:IndirectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXDIH1FI1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DIH1_FI1 | BXX | BXX Disch. Flow | 15 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DIH1_FI1_DI_AD | BXX_DSAB | BXX Disch. Flow Disabled Analog Alarm | 37 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_DIH1_FI1.DI_AD | No | BXX Disch. Flow Disabled Analog Alarm | 0 | 0
BXX_DIH1_FI1_DI_SC | BXX_DIH1_FI1 | BXX Disch. Flow Scan Status | 27 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.DI_SC | No | BXX Disch. Flow Scan Status | 0 | 0
BXX_DIH1_FI1_DA_LL | BXX_DIH1_FI1 | BXX Disch. Flow LOLO Alarm | 26 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DIH1_FI1.DA_LL | No | BXX Disch. Flow LOLO Alarm | 0 | 0
BXX_DIH1_FI1_DA_ER | BXX_DIH1_FI1 | BXX Disch. Flow Signal Error Alarm | 34 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DIH1_FI1.DA_ER | No | BXX Disch. Flow Signal Error Alarm | 0 | 0
BXX_DIH1_FI1_PB_SM | BXX_DIH1_FI1 | BXX Disch. Flow Alarm Test | 26 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_SM | No | BXX Disch. Flow Alarm Test | 0 | 0
BXX_DIH1_FI1_PB_SV | BXX_DIH1_FI1 | BXX Disch. Flow Override Enable | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_SV | No | BXX Disch. Flow Override Enable | 0 | 0
BXX_DIH1_FI1_PB_AE | BXX_DIH1_FI1 | BXX Disch. Flow Alarm Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_AE.RE | No | BXX Disch. Flow Alarm Enable | 0 | 0
BXX_DIH1_FI1_PB_HI | BXX_DIH1_FI1 | BXX Disch. Flow High Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_HI.RE | No | BXX Disch. Flow High Alarm Enable | 0 | 0
BXX_DIH1_FI1_PB_LO | BXX_DIH1_FI1 | BXX Disch. Flow Low Alarm Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_LO.RE | No | BXX Disch. Flow Low Alarm Enable | 0 | 0
BXX_DIH1_FI1_PB_LL | BXX_DIH1_FI1 | BXX Disch. Flow LOLO Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_LL.RE | No | BXX Disch. Flow LOLO Alarm Enable | 0 | 0
BXX_DIH1_FI1_PB_ER | BXX_DIH1_FI1 | BXX Disch. Flow Signal Error Alarm En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_ER.RE | No | BXX Disch. Flow Signal Error Alarm En | 0 | 0
BXX_DIH1_FI1_PB_SC | BXX_DIH1_FI1 | BXX Disch. Flow Scan Enable | 27 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_SC | No | BXX Disch. Flow Scan Enable | 0 | 0
BXX_DIH1_FI1_DA_HH | BXX_DIH1_FI1 | BXX Disch. Flow HIHI Alarm | 26 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DIH1_FI1.DA_HH | No | BXX Disch. Flow HIHI Alarm | 0 | 0
BXX_DIH1_FI1_DA_HI | BXX_DIH1_FI1 | BXX Disch. Flow HI Alarm | 24 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DIH1_FI1.DA_HI | No | BXX Disch. Flow HI Alarm | 0 | 0
BXX_DIH1_FI1_PB_HH | BXX_DIH1_FI1 | BXX Disch. Flow HIHI Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_HH.RE | No | BXX Disch. Flow HIHI Alarm Enable | 0 | 0
BXX_DIH1_FI1_PB_AR | BXX_DIH1_FI1 | BXX Disch. Flow Alarm Reset | 27 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_AR | No | BXX Disch. Flow Alarm Reset | 0 | 0
BXX_DIH1_FI1_DA_LO | BXX_DIH1_FI1 | BXX Disch. Flow LO Alarm | 24 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DIH1_FI1.DA_LO | No | BXX Disch. Flow LO Alarm | 0 | 0
BXX_DIH1_FI1_PB_LL_DE | BXX_DIH1_FI1 | BXX Disch. Flow LOLO Alarm Dialer Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_LL.DE | No | BXX Disch. Flow LOLO Alarm Dialer Enable | 0 | 0
BXX_DIH1_FI1_PB_ER_DE | BXX_DIH1_FI1 | BXX Disch. Flow Signal Error Alarm Dialer En | 44 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_ER.DE | No | BXX Disch. Flow Signal Error Alarm Dialer En | 0 | 0
BXX_DIH1_FI1_PB_HH_DE | BXX_DIH1_FI1 | BXX Disch. Flow HIHI Alarm Dialer Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_HH.DE | No | BXX Disch. Flow HIHI Alarm Dialer Enable | 0 | 0
BXX_DIH1_FI1_PB_LL_SR | BXX_DIH1_FI1 | BXX Disch. Flow LOLO Alarm Sup Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_LL.SR | No | BXX Disch. Flow LOLO Alarm Sup Enable | 0 | 0
BXX_DIH1_FI1_PB_ER_SR | BXX_DIH1_FI1 | BXX Disch. Flow Signal Error Alarm Sup En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_ER.SR | No | BXX Disch. Flow Signal Error Alarm Sup En | 0 | 0
BXX_DIH1_FI1_PB_HH_SR | BXX_DIH1_FI1 | BXX Disch. Flow HIHI Alarm Sup Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DIH1_FI1.PB_HH.SR | No | BXX Disch. Flow HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DIH1_FI1_AI_VI | BXX_DIH1_FI1 | BXX Disch. Flow Number of Visible Eng Values | 44 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_DIH1_FI1.AI_VI | No | BXX Disch. Flow Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AI_DC | BXX_DIH1_FI1 | BXX Disch. Flow Precision | 25 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DIH1_FI1.AI_DC | No | BXX Disch. Flow Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DIH1_FI1_SN_LL | BXX_DIH1_FI1 | BXX Disch. Flow LOLO Alarm Delay | 32 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DIH1_FI1.SN_LL | No | BXX Disch. Flow LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_SN_HI | BXX_DIH1_FI1 | BXX Disch. Flow High Alarm Delay | 32 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DIH1_FI1.SN_HI | No | BXX Disch. Flow High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AI_CV | BXX_DIH1_FI1 | BXX Disch. Flow Current Value | 29 | Yes | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_FI1.AI_CV | No | BXX Disch. Flow Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AI_TD | BXX_DIH1_FI1 | BXX Disch. Flow Total Today | 27 | Yes | No | 0 | Yes | No | 0 | 0 | m3 | 0 | 0 | 20000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 20000 | Linear | BXX | No | BXX_DIH1_FI1.AI_TD | No | BXX Disch. Flow Total Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AI_YT | BXX_DIH1_FI1 | BXX Disch. Flow Total Yesterday | 31 | Yes | No | 0 | Yes | No | 0 | 0 | m3 | 0 | 0 | 20000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 20000 | Linear | BXX | No | BXX_DIH1_FI1.AI_YT | No | BXX Disch. Flow Total Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AO_XM | BXX_DIH1_FI1 | BXX Disch. Flow Span Setpoint | 29 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_FI1.AO_XM | No | BXX Disch. Flow Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AO_LO | BXX_DIH1_FI1 | BXX Disch. Flow Low Setpoint | 28 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_FI1.AO_LO | No | BXX Disch. Flow Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AO_HH | BXX_DIH1_FI1 | BXX Disch. Flow HIHI Setpoint | 29 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_FI1.AO_HH | No | BXX Disch. Flow HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AO_HI | BXX_DIH1_FI1 | BXX Disch. Flow High Setpoint | 29 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_FI1.AO_HI | No | BXX Disch. Flow High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AO_SV | BXX_DIH1_FI1 | BXX Disch. Flow Override Value | 30 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_FI1.AO_SV | No | BXX Disch. Flow Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AO_EM | BXX_DIH1_FI1 | BXX Disch. Flow Zero Setpoint | 29 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_FI1.AO_EM | No | BXX Disch. Flow Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_SN_HH | BXX_DIH1_FI1 | BXX Disch. Flow HIHI Alarm Delay | 32 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DIH1_FI1.SN_HH | No | BXX Disch. Flow HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_SN_LO | BXX_DIH1_FI1 | BXX Disch. Flow Low Alarm Delay | 31 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DIH1_FI1.SN_LO | No | BXX Disch. Flow Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DIH1_FI1_AO_LL | BXX_DIH1_FI1 | BXX Disch. Flow LOLO Setpoint | 29 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_DIH1_FI1.AO_LL | No | BXX Disch. Flow LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_DIH1_FI1_DI_NM | BXX_DIH1_FI1 | BXX_DIH1_FI1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_DIH1_FI1_PB_HH_RN | BXX_DIH1_FI1 | BXX Disch. Flow HIHI Alarm Disabled Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DIH1_FI1_PB_HH_RN | No | BXX Disch. Flow HIHI Alarm Disabled Reason
BXX_DIH1_FI1_PB_LL_RN | BXX_DIH1_FI1 | BXX Disch. Flow LOLO Alarm Disabled Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DIH1_FI1_PB_LL_RN | No | BXX Disch. Flow LOLO Alarm Disabled Reason
BXX_DIH1_FI1_PB_ER_RN | BXX_DIH1_FI1 | BXX Disch. Flow Sig Error Alarm Dis Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DIH1_FI1_PB_ER_RN | No | BXX Disch. Flow Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:IndirectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXDF1LI1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DFT1_LI1 | BXX | BXX Diesel Level | 16 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DFT1_LI1_DI_AD | BXX_DSAB | BXX Diesel Level Disabled Analog Alarm | 38 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_DFT1_LI1.DI_AD | No | BXX Diesel Level Disabled Analog Alarm | 0 | 0
BXX_DFT1_LI1_DI_SC | BXX_DFT1_LI1 | BXX Diesel Level Scan Status | 28 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.DI_SC | No | BXX Diesel Level Scan Status | 0 | 0
BXX_DFT1_LI1_DA_LL | BXX_DFT1_LI1 | BXX Diesel Level LOLO Alarm | 27 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DFT1_LI1.DA_LL | No | BXX Diesel Level LOLO Alarm | 0 | 0
BXX_DFT1_LI1_DA_ER | BXX_DFT1_LI1 | BXX Diesel Level Signal Error Alarm | 35 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DFT1_LI1.DA_ER | No | BXX Diesel Level Signal Error Alarm | 0 | 0
BXX_DFT1_LI1_PB_SM | BXX_DFT1_LI1 | BXX Diesel Level Alarm Test | 27 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_SM | No | BXX Diesel Level Alarm Test | 0 | 0
BXX_DFT1_LI1_PB_SV | BXX_DFT1_LI1 | BXX Diesel Level Override Enable | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_SV | No | BXX Diesel Level Override Enable | 0 | 0
BXX_DFT1_LI1_PB_AE | BXX_DFT1_LI1 | BXX Diesel Level Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_AE.RE | No | BXX Diesel Level Alarm Enable | 0 | 0
BXX_DFT1_LI1_PB_HI | BXX_DFT1_LI1 | BXX Diesel Level High Alarm Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_HI.RE | No | BXX Diesel Level High Alarm Enable | 0 | 0
BXX_DFT1_LI1_PB_LO | BXX_DFT1_LI1 | BXX Diesel Level Low Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_LO.RE | No | BXX Diesel Level Low Alarm Enable | 0 | 0
BXX_DFT1_LI1_PB_LL | BXX_DFT1_LI1 | BXX Diesel Level LOLO Alarm Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_LL.RE | No | BXX Diesel Level LOLO Alarm Enable | 0 | 0
BXX_DFT1_LI1_PB_ER | BXX_DFT1_LI1 | BXX Diesel Level Signal Error Alarm En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_ER.RE | No | BXX Diesel Level Signal Error Alarm En | 0 | 0
BXX_DFT1_LI1_PB_SC | BXX_DFT1_LI1 | BXX Diesel Level Scan Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_SC | No | BXX Diesel Level Scan Enable | 0 | 0
BXX_DFT1_LI1_DA_HH | BXX_DFT1_LI1 | BXX Diesel Level HIHI Alarm | 27 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DFT1_LI1.DA_HH | No | BXX Diesel Level HIHI Alarm | 0 | 0
BXX_DFT1_LI1_DA_HI | BXX_DFT1_LI1 | BXX Diesel Level HI Alarm | 25 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DFT1_LI1.DA_HI | No | BXX Diesel Level HI Alarm | 0 | 0
BXX_DFT1_LI1_PB_HH | BXX_DFT1_LI1 | BXX Diesel Level HIHI Alarm Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_HH.RE | No | BXX Diesel Level HIHI Alarm Enable | 0 | 0
BXX_DFT1_LI1_PB_AR | BXX_DFT1_LI1 | BXX Diesel Level Alarm Reset | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_AR | No | BXX Diesel Level Alarm Reset | 0 | 0
BXX_DFT1_LI1_DA_LO | BXX_DFT1_LI1 | BXX Diesel Level LO Alarm | 25 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_DFT1_LI1.DA_LO | No | BXX Diesel Level LO Alarm | 0 | 0
BXX_DFT1_LI1_PB_LL_DE | BXX_DFT1_LI1 | BXX Diesel Level LOLO Alarm Dialer Enable | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_LL.DE | No | BXX Diesel Level LOLO Alarm Dialer Enable | 0 | 0
BXX_DFT1_LI1_PB_ER_DE | BXX_DFT1_LI1 | BXX Diesel Level Signal Error Alarm Dialer En | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_ER.DE | No | BXX Diesel Level Signal Error Alarm Dialer En | 0 | 0
BXX_DFT1_LI1_PB_HH_DE | BXX_DFT1_LI1 | BXX Diesel Level HIHI Alarm Dialer Enable | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_HH.DE | No | BXX Diesel Level HIHI Alarm Dialer Enable | 0 | 0
BXX_DFT1_LI1_PB_LL_SR | BXX_DFT1_LI1 | BXX Diesel Level LOLO Alarm Sup Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_LL.SR | No | BXX Diesel Level LOLO Alarm Sup Enable | 0 | 0
BXX_DFT1_LI1_PB_ER_SR | BXX_DFT1_LI1 | BXX Diesel Level Signal Error Alarm Sup En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_ER.SR | No | BXX Diesel Level Signal Error Alarm Sup En | 0 | 0
BXX_DFT1_LI1_PB_HH_SR | BXX_DFT1_LI1 | BXX Diesel Level HIHI Alarm Sup Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DFT1_LI1.PB_HH.SR | No | BXX Diesel Level HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DFT1_LI1_AI_VI | BXX_DFT1_LI1 | BXX Diesel Level Number of Visible Eng Values | 45 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_DFT1_LI1.AI_VI | No | BXX Diesel Level Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_AI_DC | BXX_DFT1_LI1 | BXX Diesel Level Precision | 26 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DFT1_LI1.AI_DC | No | BXX Diesel Level Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DFT1_LI1_SN_LL | BXX_DFT1_LI1 | BXX Diesel Level LOLO Alarm Delay | 33 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DFT1_LI1.SN_LL | No | BXX Diesel Level LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_SN_HI | BXX_DFT1_LI1 | BXX Diesel Level High Alarm Delay | 33 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DFT1_LI1.SN_HI | No | BXX Diesel Level High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_AI_CV | BXX_DFT1_LI1 | BXX Diesel Level Current Value | 30 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DFT1_LI1.AI_CV | No | BXX Diesel Level Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_AO_XM | BXX_DFT1_LI1 | BXX Diesel Level Span Setpoint | 30 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DFT1_LI1.AO_XM | No | BXX Diesel Level Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_AO_LO | BXX_DFT1_LI1 | BXX Diesel Level Low Setpoint | 29 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DFT1_LI1.AO_LO | No | BXX Diesel Level Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_AO_HH | BXX_DFT1_LI1 | BXX Diesel Level HIHI Setpoint | 30 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DFT1_LI1.AO_HH | No | BXX Diesel Level HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_AO_HI | BXX_DFT1_LI1 | BXX Diesel Level High Setpoint | 30 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DFT1_LI1.AO_HI | No | BXX Diesel Level High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_AO_SV | BXX_DFT1_LI1 | BXX Diesel Level Override Value | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DFT1_LI1.AO_SV | No | BXX Diesel Level Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_AO_EM | BXX_DFT1_LI1 | BXX Diesel Level Zero Setpoint | 30 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DFT1_LI1.AO_EM | No | BXX Diesel Level Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_SN_HH | BXX_DFT1_LI1 | BXX Diesel Level HIHI Alarm Delay | 33 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DFT1_LI1.SN_HH | No | BXX Diesel Level HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_SN_LO | BXX_DFT1_LI1 | BXX Diesel Level Low Alarm Delay | 32 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DFT1_LI1.SN_LO | No | BXX Diesel Level Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DFT1_LI1_AO_LL | BXX_DFT1_LI1 | BXX Diesel Level LOLO Setpoint | 30 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DFT1_LI1.AO_LL | No | BXX Diesel Level LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_DFT1_LI1_DI_NM | BXX_DFT1_LI1 | BXX_DFT1_LI1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_DFT1_LI1_PB_HH_RN | BXX_DFT1_LI1 | BXX Diesel Level HIHI Alarm Disabled Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DFT1_LI1_PB_HH_RN | No | BXX Diesel Level HIHI Alarm Disabled Reason
BXX_DFT1_LI1_PB_LL_RN | BXX_DFT1_LI1 | BXX Diesel Level LOLO Alarm Disabled Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DFT1_LI1_PB_LL_RN | No | BXX Diesel Level LOLO Alarm Disabled Reason
BXX_DFT1_LI1_PB_ER_RN | BXX_DFT1_LI1 | BXX Diesel Level Sig Error Alarm Dis Reason | 43 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_DFT1_LI1_PB_ER_RN | No | BXX Diesel Level Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:IndirectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXWW01LI1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_WW01_LI1 | BXX | BXX Wet Well 1 Level | 20 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IODisc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_WW01_LI1_DI_AD | BXX_DSAB | BXX Wet Well 1 Level Disabled Analog Alarm | 42 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_WW01_LI1.DI_AD | No | BXX Wet Well 1 Level Disabled Analog Alarm | 0 | 0
BXX_WW01_LI1_DI_SC | BXX_WW01_LI1 | BXX Wet Well 1 Level Scan Status | 32 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.DI_SC | No | BXX Wet Well 1 Level Scan Status | 0 | 0
BXX_WW01_LI1_DA_LL | BXX_WW01_LI1 | BXX Wet Well 1 Level LOLO Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_WW01_LI1.DA_LL | No | BXX Wet Well 1 Level LOLO Alarm | 0 | 0
BXX_WW01_LI1_DA_ER | BXX_WW01_LI1 | BXX Wet Well 1 Level Signal Error Alarm | 39 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_WW01_LI1.DA_ER | No | BXX Wet Well 1 Level Signal Error Alarm | 0 | 0
BXX_WW01_LI1_PB_SM | BXX_WW01_LI1 | BXX Wet Well 1 Level Alarm Test | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_SM | No | BXX Wet Well 1 Level Alarm Test | 0 | 0
BXX_WW01_LI1_PB_SV | BXX_WW01_LI1 | BXX Wet Well 1 Level Override Enable | 36 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_SV | No | BXX Wet Well 1 Level Override Enable | 0 | 0
BXX_WW01_LI1_PB_AE | BXX_WW01_LI1 | BXX Wet Well 1 Level Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_AE.RE | No | BXX Wet Well 1 Level Alarm Enable | 0 | 0
BXX_WW01_LI1_PB_HI | BXX_WW01_LI1 | BXX Wet Well 1 Level High Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_HI.RE | No | BXX Wet Well 1 Level High Alarm Enable | 0 | 0
BXX_WW01_LI1_PB_LO | BXX_WW01_LI1 | BXX Wet Well 1 Level Low Alarm Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_LO.RE | No | BXX Wet Well 1 Level Low Alarm Enable | 0 | 0
BXX_WW01_LI1_PB_LL | BXX_WW01_LI1 | BXX Wet Well 1 Level LOLO Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_LL.RE | No | BXX Wet Well 1 Level LOLO Alarm Enable | 0 | 0
BXX_WW01_LI1_PB_ER | BXX_WW01_LI1 | BXX Wet Well 1 Level Signal Error Alarm En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_ER.RE | No | BXX Wet Well 1 Level Signal Error Alarm En | 0 | 0
BXX_WW01_LI1_PB_SC | BXX_WW01_LI1 | BXX Wet Well 1 Level Scan Enable | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_SC | No | BXX Wet Well 1 Level Scan Enable | 0 | 0
BXX_WW01_LI1_DA_HH | BXX_WW01_LI1 | BXX Wet Well 1 Level HIHI Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_WW01_LI1.DA_HH | No | BXX Wet Well 1 Level HIHI Alarm | 0 | 0
BXX_WW01_LI1_DA_HI | BXX_WW01_LI1 | BXX Wet Well 1 Level HI Alarm | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_WW01_LI1.DA_HI | No | BXX Wet Well 1 Level HI Alarm | 0 | 0
BXX_WW01_LI1_PB_HH | BXX_WW01_LI1 | BXX Wet Well 1 Level HIHI Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_HH.RE | No | BXX Wet Well 1 Level HIHI Alarm Enable | 0 | 0
BXX_WW01_LI1_PB_AR | BXX_WW01_LI1 | BXX Wet Well 1 Level Alarm Reset | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_AR | No | BXX Wet Well 1 Level Alarm Reset | 0 | 0
BXX_WW01_LI1_DA_LO | BXX_WW01_LI1 | BXX Wet Well 1 Level LO Alarm | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_WW01_LI1.DA_LO | No | BXX Wet Well 1 Level LO Alarm | 0 | 0
BXX_WW01_LI1_PB_LL_DE | BXX_WW01_LI1 | BXX Wet Well 1 Level LOLO Alarm Dialer Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_LL.DE | No | BXX Wet Well 1 Level LOLO Alarm Dialer Enable | 0 | 0
BXX_WW01_LI1_PB_ER_DE | BXX_WW01_LI1 | BXX Wet Well 1 Level Sig Error Dialer En | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_ER.DE | No | BXX Wet Well 1 Level Sig Error Dialer En | 0 | 0
BXX_WW01_LI1_PB_HH_DE | BXX_WW01_LI1 | BXX Wet Well 1 Level HIHI Alarm Dialer Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_HH.DE | No | BXX Wet Well 1 Level HIHI Alarm Dialer Enable | 0 | 0
BXX_WW01_LI1_PB_LL_SR | BXX_WW01_LI1 | BXX Wet Well 1 Level LOLO Alarm Sup Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_LL.SR | No | BXX Wet Well 1 Level LOLO Alarm Sup Enable | 0 | 0
BXX_WW01_LI1_PB_ER_SR | BXX_WW01_LI1 | BXX Wet Well 1 Level Signal Error Sup En | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_ER.SR | No | BXX Wet Well 1 Level Signal Error Sup En | 0 | 0
BXX_WW01_LI1_PB_HH_SR | BXX_WW01_LI1 | BXX Wet Well 1 Level HIHI Alarm Sup Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW01_LI1.PB_HH.SR | No | BXX Wet Well 1 Level HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_WW01_LI1_AI_VI | BXX_WW01_LI1 | BXX Wet Well 1 Level Number of Vis Eng Values | 45 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_WW01_LI1.AI_VI | No | BXX Wet Well 1 Level Number of Vis Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_AI_DC | BXX_WW01_LI1 | BXX Wet Well 1 Level Precision | 30 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_WW01_LI1.AI_DC | No | BXX Wet Well 1 Level Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_E2_DC | BXX_WW01_LI1 | BXX Wet Well 1 Level Eng Value 2 Precision | 42 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_WW01_LI1.E2_DC | No | BXX Wet Well 1 Level Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_WW01_LI1_SN_LL | BXX_WW01_LI1 | BXX Wet Well 1 Level LOLO Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_WW01_LI1.SN_LL | No | BXX Wet Well 1 Level LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_SN_HI | BXX_WW01_LI1 | BXX Wet Well 1 Level High Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_WW01_LI1.SN_HI | No | BXX Wet Well 1 Level High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_AI_CV | BXX_WW01_LI1 | BXX Wet Well 1 Level Current Value | 34 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW01_LI1.AI_CV | No | BXX Wet Well 1 Level Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_AO_XM | BXX_WW01_LI1 | BXX Wet Well 1 Level Span Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW01_LI1.AO_XM | No | BXX Wet Well 1 Level Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_AO_LO | BXX_WW01_LI1 | BXX Wet Well 1 Level Low Setpoint | 33 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW01_LI1.AO_LO | No | BXX Wet Well 1 Level Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_AO_HH | BXX_WW01_LI1 | BXX Wet Well 1 Level HIHI Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW01_LI1.AO_HH | No | BXX Wet Well 1 Level HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_E2_CV | BXX_WW01_LI1 | BXX Wet Well 1 Level Units 2 | 28 | No | No | 0 | Yes | No | 0 | 0 | m | 0 | 0 | 6.5 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 6.5 | Linear | BXX | No | BXX_WW01_LI1.E2_CV | No | BXX Wet Well 1 Level Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_AO_HI | BXX_WW01_LI1 | BXX Wet Well 1 Level High Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW01_LI1.AO_HI | No | BXX Wet Well 1 Level High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_AO_SV | BXX_WW01_LI1 | BXX Wet Well 1 Level Override Value | 35 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW01_LI1.AO_SV | No | BXX Wet Well 1 Level Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_AO_EM | BXX_WW01_LI1 | BXX Wet Well 1 Level Zero Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW01_LI1.AO_EM | No | BXX Wet Well 1 Level Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_SN_HH | BXX_WW01_LI1 | BXX Wet Well 1 Level HIHI Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_WW01_LI1.SN_HH | No | BXX Wet Well 1 Level HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_SN_LO | BXX_WW01_LI1 | BXX Wet Well 1 Level Low Alarm Delay | 36 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_WW01_LI1.SN_LO | No | BXX Wet Well 1 Level Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW01_LI1_AO_LL | BXX_WW01_LI1 | BXX Wet Well 1 Level LOLO Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW01_LI1.AO_LL | No | BXX Wet Well 1 Level LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_WW01_LI1_DI_NM | BXX_WW01_LI1 | BXX_WW01_LI1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_WW01_LI1_PB_HH_RN | BXX_WW01_LI1 | BXX Wet Well 1 Level HIHI Alarm Dis Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW01_LI1_PB_HH_RN | No | BXX Wet Well 1 Level HIHI Alarm Dis Reason
BXX_WW01_LI1_PB_LL_RN | BXX_WW01_LI1 | BXX Wet Well 1 Level LOLO Alarm Dis Reason | 42 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW01_LI1_PB_LL_RN | No | BXX Wet Well 1 Level LOLO Alarm Dis Reason
BXX_WW01_LI1_PB_ER_RN | BXX_WW01_LI1 | BXX Wet Well 1 Level Sig Error Dis Reason | 41 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW01_LI1_PB_ER_RN | No | BXX Wet Well 1 Level Sig Error Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:IndirectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXWW02LI1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_WW02_LI1 | BXX | BXX Wet Well 2 Level | 20 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_WW02_LI1_DI_AD | BXX_DSAB | BXX Wet Well 2 Level Disabled Analog Alarm | 42 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_WW02_LI1.DI_AD | No | BXX Wet Well 2 Level Disabled Analog Alarm | 0 | 0
BXX_WW02_LI1_DI_SC | BXX_WW02_LI1 | BXX Wet Well 2 Level Scan Status | 32 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.DI_SC | No | BXX Wet Well 2 Level Scan Status | 0 | 0
BXX_WW02_LI1_DA_LL | BXX_WW02_LI1 | BXX Wet Well 2 Level LOLO Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_WW02_LI1.DA_LL | No | BXX Wet Well 2 Level LOLO Alarm | 0 | 0
BXX_WW02_LI1_DA_ER | BXX_WW02_LI1 | BXX Wet Well 2 Level Signal Error Alarm | 39 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_WW02_LI1.DA_ER | No | BXX Wet Well 2 Level Signal Error Alarm | 0 | 0
BXX_WW02_LI1_PB_SM | BXX_WW02_LI1 | BXX Wet Well 2 Level Alarm Test | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_SM | No | BXX Wet Well 2 Level Alarm Test | 0 | 0
BXX_WW02_LI1_PB_SV | BXX_WW02_LI1 | BXX Wet Well 2 Level Override Enable | 36 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_SV | No | BXX Wet Well 2 Level Override Enable | 0 | 0
BXX_WW02_LI1_PB_AE | BXX_WW02_LI1 | BXX Wet Well 2 Level Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_AE.RE | No | BXX Wet Well 2 Level Alarm Enable | 0 | 0
BXX_WW02_LI1_PB_HI | BXX_WW02_LI1 | BXX Wet Well 2 Level High Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_HI.RE | No | BXX Wet Well 2 Level High Alarm Enable | 0 | 0
BXX_WW02_LI1_PB_LO | BXX_WW02_LI1 | BXX Wet Well 2 Level Low Alarm Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_LO.RE | No | BXX Wet Well 2 Level Low Alarm Enable | 0 | 0
BXX_WW02_LI1_PB_LL | BXX_WW02_LI1 | BXX Wet Well 2 Level LOLO Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_LL.RE | No | BXX Wet Well 2 Level LOLO Alarm Enable | 0 | 0
BXX_WW02_LI1_PB_ER | BXX_WW02_LI1 | BXX Wet Well 2 Level Signal Error Alarm En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_ER.RE | No | BXX Wet Well 2 Level Signal Error Alarm En | 0 | 0
BXX_WW02_LI1_PB_SC | BXX_WW02_LI1 | BXX Wet Well 2 Level Scan Enable | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_SC | No | BXX Wet Well 2 Level Scan Enable | 0 | 0
BXX_WW02_LI1_DA_HH | BXX_WW02_LI1 | BXX Wet Well 2 Level HIHI Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_WW02_LI1.DA_HH | No | BXX Wet Well 2 Level HIHI Alarm | 0 | 0
BXX_WW02_LI1_DA_HI | BXX_WW02_LI1 | BXX Wet Well 2 Level HI Alarm | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_WW02_LI1.DA_HI | No | BXX Wet Well 2 Level HI Alarm | 0 | 0
BXX_WW02_LI1_PB_HH | BXX_WW02_LI1 | BXX Wet Well 2 Level HIHI Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_HH.RE | No | BXX Wet Well 2 Level HIHI Alarm Enable | 0 | 0
BXX_WW02_LI1_PB_AR | BXX_WW02_LI1 | BXX Wet Well 2 Level Alarm Reset | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_AR | No | BXX Wet Well 2 Level Alarm Reset | 0 | 0
BXX_WW02_LI1_DA_LO | BXX_WW02_LI1 | BXX Wet Well 2 Level LO Alarm | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_WW02_LI1.DA_LO | No | BXX Wet Well 2 Level LO Alarm | 0 | 0
BXX_WW02_LI1_PB_LL_DE | BXX_WW02_LI1 | BXX Wet Well 2 Level LOLO Alarm Dialer Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_LL.DE | No | BXX Wet Well 2 Level LOLO Alarm Dialer Enable | 0 | 0
BXX_WW02_LI1_PB_ER_DE | BXX_WW02_LI1 | BXX Wet Well 2 Level Signal Error Alarm Dialer En | 49 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_ER.DE | No | BXX Wet Well 2 Level Signal Error Alarm Dialer En | 0 | 0
BXX_WW02_LI1_PB_HH_DE | BXX_WW02_LI1 | BXX Wet Well 2 Level HIHI Alarm Dialer Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_HH.DE | No | BXX Wet Well 2 Level HIHI Alarm Dialer Enable | 0 | 0
BXX_WW02_LI1_PB_LL_SR | BXX_WW02_LI1 | BXX Wet Well 2 Level LOLO Alarm Sup Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_LL.SR | No | BXX Wet Well 2 Level LOLO Alarm Sup Enable | 0 | 0
BXX_WW02_LI1_PB_ER_SR | BXX_WW02_LI1 | BXX Wet Well 2 Level Signal Error Alarm Sup En | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_ER.SR | No | BXX Wet Well 2 Level Signal Error Alarm Sup En | 0 | 0
BXX_WW02_LI1_PB_HH_SR | BXX_WW02_LI1 | BXX Wet Well 2 Level HIHI Alarm Sup Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_WW02_LI1.PB_HH.SR | No | BXX Wet Well 2 Level HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_WW02_LI1_AI_VI | BXX_WW02_LI1 | BXX Wet Well 2 Level Number of Visible Eng Values | 49 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_WW02_LI1.AI_VI | No | BXX Wet Well 2 Level Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_AI_DC | BXX_WW02_LI1 | BXX Wet Well 2 Level Precision | 30 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_WW02_LI1.AI_DC | No | BXX Wet Well 2 Level Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_E2_DC | BXX_WW02_LI1 | BXX Wet Well 2 Level Eng Value 2 Precision | 42 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_WW02_LI1.E2_DC | No | BXX Wet Well 2 Level Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_WW02_LI1_SN_LL | BXX_WW02_LI1 | BXX Wet Well 2 Level LOLO Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_WW02_LI1.SN_LL | No | BXX Wet Well 2 Level LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_SN_HI | BXX_WW02_LI1 | BXX Wet Well 2 Level High Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_WW02_LI1.SN_HI | No | BXX Wet Well 2 Level High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1__AI_CV | BXX_WW02_LI1 | BXX Wet Well 2 Level Current Value | 34 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW02_LI1.AI_CV | No | BXX Wet Well 2 Level Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_AO_XM | BXX_WW02_LI1 | BXX Wet Well 2 Level Span Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW02_LI1.AO_XM | No | BXX Wet Well 2 Level Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_AO_LO | BXX_WW02_LI1 | BXX Wet Well 2 Level Low Setpoint | 33 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW02_LI1.AO_LO | No | BXX Wet Well 2 Level Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_AO_HH | BXX_WW02_LI1 | BXX Wet Well 2 Level HIHI Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW02_LI1.AO_HH | No | BXX Wet Well 2 Level HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_E2_CV | BXX_WW02_LI1 | BXX Wet Well 2 Level Units 2 | 28 | No | No | 0 | Yes | No | 0 | 0 | m | 0 | 0 | 6.5 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 6.5 | Linear | BXX | No | BXX_WW02_LI1.E2_CV | No | BXX Wet Well 2 Level Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_AO_HI | BXX_WW02_LI1 | BXX Wet Well 2 Level High Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW02_LI1.AO_HI | No | BXX Wet Well 2 Level High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_AO_SV | BXX_WW02_LI1 | BXX Wet Well 2 Level Override Value | 35 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW02_LI1.AO_SV | No | BXX Wet Well 2 Level Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_AO_EM | BXX_WW02_LI1 | BXX Wet Well 2 Level Zero Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW02_LI1.AO_EM | No | BXX Wet Well 2 Level Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_SN_HH | BXX_WW02_LI1 | BXX Wet Well 2 Level HIHI Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_WW02_LI1.SN_HH | No | BXX Wet Well 2 Level HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_SN_LO | BXX_WW02_LI1 | BXX Wet Well 2 Level Low Alarm Delay | 36 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_WW02_LI1.SN_LO | No | BXX Wet Well 2 Level Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_WW02_LI1_AO_LL | BXX_WW02_LI1 | BXX Wet Well 2 Level LOLO Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_WW02_LI1.AO_LL | No | BXX Wet Well 2 Level LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_WW02_LI1_DI_NM | BXX_WW02_LI1 | BXX_WW02_LI1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_WW02_LI1_PB_HH_RN | BXX_WW02_LI1 | BXX Wet Well 2 Level HIHI Alarm Disabled Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW02_LI1_PB_HH_RN | No | BXX Wet Well 2 Level HIHI Alarm Disabled Reason
BXX_WW02_LI1_PB_LL_RN | BXX_WW02_LI1 | BXX Wet Well 2 Level LOLO Alarm Disabled Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW02_LI1_PB_LL_RN | No | BXX Wet Well 2 Level LOLO Alarm Disabled Reason
BXX_WW02_LI1_PB_ER_RN | BXX_WW02_LI1 | BXX Wet Well 2 Level Sig Error Alarm Dis Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_WW02_LI1_PB_ER_RN | No | BXX Wet Well 2 Level Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXBLS1LI1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_BLS1_LI1 | BXX | BXX WW1 Backup Level | 20 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_BLS1_LI1_DI_AD | BXX_DSAB | BXX WW1 Backup Level Disabled Analog Alarm | 42 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_BLS1_LI1.DI_AD | No | BXX WW1 Backup Level Disabled Analog Alarm | 0 | 0
BXX_BLS1_LI1_DI_SC | BXX_BLS1_LI1 | BXX WW1 Backup Level Scan Status | 32 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.DI_SC | No | BXX WW1 Backup Level Scan Status | 0 | 0
BXX_BLS1_LI1_DA_LL | BXX_BLS1_LI1 | BXX WW1 Backup Level LOLO Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_BLS1_LI1.DA_LL | No | BXX WW1 Backup Level LOLO Alarm | 0 | 0
BXX_BLS1_LI1_DA_ER | BXX_BLS1_LI1 | BXX WW1 Backup Level Signal Error Alarm | 39 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_BLS1_LI1.DA_ER | No | BXX WW1 Backup Level Signal Error Alarm | 0 | 0
BXX_BLS1_LI1_PB_SM | BXX_BLS1_LI1 | BXX WW1 Backup Level Alarm Test | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_SM | No | BXX WW1 Backup Level Alarm Test | 0 | 0
BXX_BLS1_LI1_PB_SV | BXX_BLS1_LI1 | BXX WW1 Backup Level Override Enable | 36 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_SV | No | BXX WW1 Backup Level Override Enable | 0 | 0
BXX_BLS1_LI1_PB_AE | BXX_BLS1_LI1 | BXX WW1 Backup Level Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_AE.RE | No | BXX WW1 Backup Level Alarm Enable | 0 | 0
BXX_BLS1_LI1_PB_HI | BXX_BLS1_LI1 | BXX WW1 Backup Level High Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_HI.RE | No | BXX WW1 Backup Level High Alarm Enable | 0 | 0
BXX_BLS1_LI1_PB_LO | BXX_BLS1_LI1 | BXX WW1 Backup Level Low Alarm Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_LO.RE | No | BXX WW1 Backup Level Low Alarm Enable | 0 | 0
BXX_BLS1_LI1_PB_LL | BXX_BLS1_LI1 | BXX WW1 Backup Level LOLO Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_LL.RE | No | BXX WW1 Backup Level LOLO Alarm Enable | 0 | 0
BXX_BLS1_LI1_PB_ER | BXX_BLS1_LI1 | BXX WW1 Backup Level Signal Error Alarm En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_ER.RE | No | BXX WW1 Backup Level Signal Error Alarm En | 0 | 0
BXX_BLS1_LI1_PB_SC | BXX_BLS1_LI1 | BXX WW1 Backup Level Scan Enable | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_SC | No | BXX WW1 Backup Level Scan Enable | 0 | 0
BXX_BLS1_LI1_DA_HH | BXX_BLS1_LI1 | BXX WW1 Backup Level HIHI Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_BLS1_LI1.DA_HH | No | BXX WW1 Backup Level HIHI Alarm | 0 | 0
BXX_BLS1_LI1_DA_HI | BXX_BLS1_LI1 | BXX WW1 Backup Level HI Alarm | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_BLS1_LI1.DA_HI | No | BXX WW1 Backup Level HI Alarm | 0 | 0
BXX_BLS1_LI1_PB_HH | BXX_BLS1_LI1 | BXX WW1 Backup Level HIHI Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_HH.RE | No | BXX WW1 Backup Level HIHI Alarm Enable | 0 | 0
BXX_BLS1_LI1_PB_AR | BXX_BLS1_LI1 | BXX WW1 Backup Level Alarm Reset | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_AR | No | BXX WW1 Backup Level Alarm Reset | 0 | 0
BXX_BLS1_LI1_DA_LO | BXX_BLS1_LI1 | BXX WW1 Backup Level LO Alarm | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_BLS1_LI1.DA_LO | No | BXX WW1 Backup Level LO Alarm | 0 | 0
BXX_BLS1_LI1_PB_LL_DE | BXX_BLS1_LI1 | BXX WW1 Backup Level LOLO Alarm Dialer Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_LL.DE | No | BXX WW1 Backup Level LOLO Alarm Dialer Enable | 0 | 0
BXX_BLS1_LI1_PB_ER_DE | BXX_BLS1_LI1 | BXX WW1 Backup Level Sig Error Alarm Dialer En | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_ER.DE | No | BXX WW1 Backup Level Sig Error Alarm Dialer En | 0 | 0
BXX_BLS1_LI1_PB_HH_DE | BXX_BLS1_LI1 | BXX WW1 Backup Level HIHI Alarm Dialer Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_HH.DE | No | BXX WW1 Backup Level HIHI Alarm Dialer Enable | 0 | 0
BXX_BLS1_LI1_PB_LL_SR | BXX_BLS1_LI1 | BXX WW1 Backup Level LOLO Alarm Sup Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_LL.SR | No | BXX WW1 Backup Level LOLO Alarm Sup Enable | 0 | 0
BXX_BLS1_LI1_PB_ER_SR | BXX_BLS1_LI1 | BXX WW1 Backup Level Signal Error Alarm Sup En | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_ER.SR | No | BXX WW1 Backup Level Signal Error Alarm Sup En | 0 | 0
BXX_BLS1_LI1_PB_HH_SR | BXX_BLS1_LI1 | BXX WW1 Backup Level HIHI Alarm Sup Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS1_LI1.PB_HH.SR | No | BXX WW1 Backup Level HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_BLS1_LI1_AI_VI | BXX_BLS1_LI1 | BXX WW1 Backup Level Number of Vis Eng Values | 45 | No | Yes | 700 | Yes | No | 0 | 0 |  | 2 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_BLS1_LI1.AI_VI | No | BXX WW1 Backup Level Number of Vis Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_AI_DC | BXX_BLS1_LI1 | BXX WW1 Backup Level Precision | 30 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_BLS1_LI1.AI_DC | No | BXX WW1 Backup Level Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_E2_DC | BXX_BLS1_LI1 | BXX WW1 Backup Level Eng Value 2 Precision | 42 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_BLS1_LI1.E2_DC | No | BXX WW1 Backup Level Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_BLS1_LI1_SN_LL | BXX_BLS1_LI1 | BXX WW1 Backup Level LOLO Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_BLS1_LI1.SN_LL | No | BXX WW1 Backup Level LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_SN_HI | BXX_BLS1_LI1 | BXX WW1 Backup Level High Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_BLS1_LI1.SN_HI | No | BXX WW1 Backup Level High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_AI_CV | BXX_BLS1_LI1 | BXX WW1 Backup Level Current Value | 34 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS1_LI1.AI_CV | No | BXX WW1 Backup Level Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_AO_XM | BXX_BLS1_LI1 | BXX WW1 Backup Level Span Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS1_LI1.AO_XM | No | BXX WW1 Backup Level Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_AO_LO | BXX_BLS1_LI1 | BXX WW1 Backup Level Low Setpoint | 33 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS1_LI1.AO_LO | No | BXX WW1 Backup Level Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_AO_HH | BXX_BLS1_LI1 | BXX WW1 Backup Level HIHI Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS1_LI1.AO_HH | No | BXX WW1 Backup Level HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_E2_CV | BXX_BLS1_LI1 | BXX WW1 Backup Level Units 2 | 28 | No | No | 0 | Yes | No | 0 | 0 | m | 0 | 0 | 6.5 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 6.5 | Linear | BXX | No | BXX_BLS1_LI1.E2_CV | No | BXX WW1 Backup Level Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_AO_HI | BXX_BLS1_LI1 | BXX WW1 Backup Level High Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS1_LI1.AO_HI | No | BXX WW1 Backup Level High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_AO_SV | BXX_BLS1_LI1 | BXX WW1 Backup Level Override Value | 35 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS1_LI1.AO_SV | No | BXX WW1 Backup Level Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_AO_EM | BXX_BLS1_LI1 | BXX WW1 Backup Level Zero Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS1_LI1.AO_EM | No | BXX WW1 Backup Level Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_SN_HH | BXX_BLS1_LI1 | BXX WW1 Backup Level HIHI Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_BLS1_LI1.SN_HH | No | BXX WW1 Backup Level HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_SN_LO | BXX_BLS1_LI1 | BXX WW1 Backup Level Low Alarm Delay | 36 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_BLS1_LI1.SN_LO | No | BXX WW1 Backup Level Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS1_LI1_AO_LL | BXX_BLS1_LI1 | BXX WW1 Backup Level LOLO Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS1_LI1.AO_LL | No | BXX WW1 Backup Level LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_BLS1_LI1_DI_NM | BXX_BLS1_LI1 | BXX_BLS1_LI1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_BLS1_LI1_PB_HH_RN | BXX_BLS1_LI1 | BXX WW1 Backup Level HIHI Alarm Disabled Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_BLS1_LI1_PB_HH_RN | No | BXX WW1 Backup Level HIHI Alarm Disabled Reason
BXX_BLS1_LI1_PB_LL_RN | BXX_BLS1_LI1 | BXX WW1 Backup Level LOLO Alarm Disabled Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_BLS1_LI1_PB_LL_RN | No | BXX WW1 Backup Level LOLO Alarm Disabled Reason
BXX_BLS1_LI1_PB_ER_RN | BXX_BLS1_LI1 | BXX WW1 Backup Level Sig Error Alarm Dis Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_BLS1_LI1_PB_ER_RN | No | BXX WW1 Backup Level Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXBLS2LI1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_BLS2_LI1 | BXX | BXX WW2 Backup Level | 20 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_BLS2_LI1_DI_AD | BXX_DSAB | BXX WW2 Backup Level Disabled Analog Alarm | 42 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_BLS2_LI1.DI_AD | No | BXX WW2 Backup Level Disabled Analog Alarm | 0 | 0
BXX_BLS2_LI1_DI_SC | BXX_BLS2_LI1 | BXX WW2 Backup Level Scan Status | 32 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.DI_SC | No | BXX WW2 Backup Level Scan Status | 0 | 0
BXX_BLS2_LI1_DA_LL | BXX_BLS2_LI1 | BXX WW2 Backup Level LOLO Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_BLS2_LI1.DA_LL | No | BXX WW2 Backup Level LOLO Alarm | 0 | 0
BXX_BLS2_LI1_DA_ER | BXX_BLS2_LI1 | BXX WW2 Backup Level Signal Error Alarm | 39 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_BLS2_LI1.DA_ER | No | BXX WW2 Backup Level Signal Error Alarm | 0 | 0
BXX_BLS2_LI1_PB_SM | BXX_BLS2_LI1 | BXX WW2 Backup Level Alarm Test | 31 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_SM | No | BXX WW2 Backup Level Alarm Test | 0 | 0
BXX_BLS2_LI1_PB_SV | BXX_BLS2_LI1 | BXX WW2 Backup Level Override Enable | 36 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_SV | No | BXX WW2 Backup Level Override Enable | 0 | 0
BXX_BLS2_LI1_PB_AE | BXX_BLS2_LI1 | BXX WW2 Backup Level Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_AE.RE | No | BXX WW2 Backup Level Alarm Enable | 0 | 0
BXX_BLS2_LI1_PB_HI | BXX_BLS2_LI1 | BXX WW2 Backup Level High Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_HI.RE | No | BXX WW2 Backup Level High Alarm Enable | 0 | 0
BXX_BLS2_LI1_PB_LO | BXX_BLS2_LI1 | BXX WW2 Backup Level Low Alarm Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_LO.RE | No | BXX WW2 Backup Level Low Alarm Enable | 0 | 0
BXX_BLS2_LI1_PB_LL | BXX_BLS2_LI1 | BXX WW2 Backup Level LOLO Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_LL.RE | No | BXX WW2 Backup Level LOLO Alarm Enable | 0 | 0
BXX_BLS2_LI1_PB_ER | BXX_BLS2_LI1 | BXX WW2 Backup Level Signal Error Alarm En | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_ER.RE | No | BXX WW2 Backup Level Signal Error Alarm En | 0 | 0
BXX_BLS2_LI1_PB_SC | BXX_BLS2_LI1 | BXX WW2 Backup Level Scan Enable | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_SC | No | BXX WW2 Backup Level Scan Enable | 0 | 0
BXX_BLS2_LI1_DA_HH | BXX_BLS2_LI1 | BXX WW2 Backup Level HIHI Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_BLS2_LI1.DA_HH | No | BXX WW2 Backup Level HIHI Alarm | 0 | 0
BXX_BLS2_LI1_DA_HI | BXX_BLS2_LI1 | BXX WW2 Backup Level HI Alarm | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_BLS2_LI1.DA_HI | No | BXX WW2 Backup Level HI Alarm | 0 | 0
BXX_BLS2_LI1_PB_HH | BXX_BLS2_LI1 | BXX WW2 Backup Level HIHI Alarm Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_HH.RE | No | BXX WW2 Backup Level HIHI Alarm Enable | 0 | 0
BXX_BLS2_LI1_PB_AR | BXX_BLS2_LI1 | BXX WW2 Backup Level Alarm Reset | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_AR | No | BXX WW2 Backup Level Alarm Reset | 0 | 0
BXX_BLS2_LI1_DA_LO | BXX_BLS2_LI1 | BXX WW2 Backup Level LO Alarm | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_BLS2_LI1.DA_LO | No | BXX WW2 Backup Level LO Alarm | 0 | 0
BXX_BLS2_LI1_PB_LL_DE | BXX_BLS2_LI1 | BXX WW2 Backup Level LOLO Alarm Dialer Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_LL.DE | No | BXX WW2 Backup Level LOLO Alarm Dialer Enable | 0 | 0
BXX_BLS2_LI1_PB_ER_DE | BXX_BLS2_LI1 | BXX WW2 Backup Level Sig Error Alarm Dialer En | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_ER.DE | No | BXX WW2 Backup Level Sig Error Alarm Dialer En | 0 | 0
BXX_BLS2_LI1_PB_HH_DE | BXX_BLS2_LI1 | BXX WW2 Backup Level HIHI Alarm Dialer Enable | 45 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_HH.DE | No | BXX WW2 Backup Level HIHI Alarm Dialer Enable | 0 | 0
BXX_BLS2_LI1_PB_LL_SR | BXX_BLS2_LI1 | BXX WW2 Backup Level LOLO Alarm Sup Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_LL.SR | No | BXX WW2 Backup Level LOLO Alarm Sup Enable | 0 | 0
BXX_BLS2_LI1_PB_ER_SR | BXX_BLS2_LI1 | BXX WW2 Backup Level Signal Error Alarm Sup En | 46 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_ER.SR | No | BXX WW2 Backup Level Signal Error Alarm Sup En | 0 | 0
BXX_BLS2_LI1_PB_HH_SR | BXX_BLS2_LI1 | BXX WW2 Backup Level HIHI Alarm Sup Enable | 42 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_BLS2_LI1.PB_HH.SR | No | BXX WW2 Backup Level HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_BLS2_LI1_AI_VI | BXX_BLS2_LI1 | BXX WW2 Backup Level Number of Vis Eng Values | 45 | No | Yes | 700 | Yes | No | 0 | 0 |  | 2 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_BLS2_LI1.AI_VI | No | BXX WW2 Backup Level Number of Vis Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_AI_DC | BXX_BLS2_LI1 | BXX WW2 Backup Level Precision | 30 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_BLS2_LI1.AI_DC | No | BXX WW2 Backup Level Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_E2_DC | BXX_BLS2_LI1 | BXX WW2 Backup Level Eng Value 2 Precision | 42 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_BLS2_LI1.E2_DC | No | BXX WW2 Backup Level Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_BLS2_LI1_SN_LL | BXX_BLS2_LI1 | BXX WW2 Backup Level LOLO Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_BLS2_LI1.SN_LL | No | BXX WW2 Backup Level LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_SN_HI | BXX_BLS2_LI1 | BXX WW2 Backup Level High Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_BLS2_LI1.SN_HI | No | BXX WW2 Backup Level High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_AI_CV | BXX_BLS2_LI1 | BXX WW2 Backup Level Current Value | 34 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS2_LI1.AI_CV | No | BXX WW2 Backup Level Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_AO_XM | BXX_BLS2_LI1 | BXX WW2 Backup Level Span Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS2_LI1.AO_XM | No | BXX WW2 Backup Level Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_AO_LO | BXX_BLS2_LI1 | BXX WW2 Backup Level Low Setpoint | 33 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS2_LI1.AO_LO | No | BXX WW2 Backup Level Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_AO_HH | BXX_BLS2_LI1 | BXX WW2 Backup Level HIHI Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS2_LI1.AO_HH | No | BXX WW2 Backup Level HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_E2_CV | BXX_BLS2_LI1 | BXX WW2 Backup Level Units 2 | 28 | No | No | 0 | Yes | No | 0 | 0 | m | 0 | 0 | 6.5 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 6.5 | Linear | BXX | No | BXX_BLS2_LI1.E2_CV | No | BXX WW2 Backup Level Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_AO_HI | BXX_BLS2_LI1 | BXX WW2 Backup Level High Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS2_LI1.AO_HI | No | BXX WW2 Backup Level High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_AO_SV | BXX_BLS2_LI1 | BXX WW2 Backup Level Override Value | 35 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS2_LI1.AO_SV | No | BXX WW2 Backup Level Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_AO_EM | BXX_BLS2_LI1 | BXX WW2 Backup Level Zero Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS2_LI1.AO_EM | No | BXX WW2 Backup Level Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_SN_HH | BXX_BLS2_LI1 | BXX WW2 Backup Level HIHI Alarm Delay | 37 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_BLS2_LI1.SN_HH | No | BXX WW2 Backup Level HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_SN_LO | BXX_BLS2_LI1 | BXX WW2 Backup Level Low Alarm Delay | 36 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_BLS2_LI1.SN_LO | No | BXX WW2 Backup Level Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_BLS2_LI1_AO_LL | BXX_BLS2_LI1 | BXX WW2 Backup Level LOLO Setpoint | 34 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_BLS2_LI1.AO_LL | No | BXX WW2 Backup Level LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_BLS2_LI1_DI_NM | BXX_BLS2_LI1 | BXX_BLS2_LI1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_BLS2_LI1_PB_HH_RN | BXX_BLS2_LI1 | BXX WW2 Backup Level HIHI Alarm Disabled Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_BLS2_LI1_PB_HH_RN | No | BXX WW2 Backup Level HIHI Alarm Disabled Reason
BXX_BLS2_LI1_PB_LL_RN | BXX_BLS2_LI1 | BXX WW2 Backup Level LOLO Alarm Disabled Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_BLS2_LI1_PB_LL_RN | No | BXX WW2 Backup Level LOLO Alarm Disabled Reason
BXX_BLS2_LI1_PB_ER_RN | BXX_BLS2_LI1 | BXX WW2 Backup Level Sig Error Alarm Dis Reason | 47 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_BLS2_LI1_PB_ER_RN | No | BXX WW2 Backup Level Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXOVF1FI1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_OVF1_FI1 | BXX | BXX Overflow | 12 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_OVF1_FI1_DI_AD | BXX_DSAB | BXX Overflow Disabled Analog Alarm | 34 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_OVF1_FI1.DI_AD | No | BXX Overflow Disabled Analog Alarm | 0 | 0
BXX_OVF1_FI1_DI_SC | BXX_OVF1_FI1 | BXX Overflow Scan Status | 24 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.DI_SC | No | BXX Overflow Scan Status | 0 | 0
BXX_OVF1_FI1_DA_LL | BXX_OVF1_FI1 | BXX Overflow LOLO Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_OVF1_FI1.DA_LL | No | BXX Overflow LOLO Alarm | 0 | 0
BXX_OVF1_FI1_DA_ER | BXX_OVF1_FI1 | BXX Overflow Signal Error Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_OVF1_FI1.DA_ER | No | BXX Overflow Signal Error Alarm | 0 | 0
BXX_OVF1_FI1_PB_SM | BXX_OVF1_FI1 | BXX Overflow Alarm Test | 23 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_SM | No | BXX Overflow Alarm Test | 0 | 0
BXX_OVF1_FI1_PB_SV | BXX_OVF1_FI1 | BXX Overflow Override Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_SV | No | BXX Overflow Override Enable | 0 | 0
BXX_OVF1_FI1_PB_AE | BXX_OVF1_FI1 | BXX Overflow Alarm Enable | 25 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_AE.RE | No | BXX Overflow Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_HI | BXX_OVF1_FI1 | BXX Overflow High Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HI.RE | No | BXX Overflow High Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_LO | BXX_OVF1_FI1 | BXX Overflow Low Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_LO.RE | No | BXX Overflow Low Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_LL | BXX_OVF1_FI1 | BXX Overflow LOLO Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_LL.RE | No | BXX Overflow LOLO Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_ER | BXX_OVF1_FI1 | BXX Overflow Signal Error Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_ER.RE | No | BXX Overflow Signal Error Alarm En | 0 | 0
BXX_OVF1_FI1_PB_SC | BXX_OVF1_FI1 | BXX Overflow Scan Enable | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_SC | No | BXX Overflow Scan Enable | 0 | 0
BXX_OVF1_FI1_DA_HH | BXX_OVF1_FI1 | BXX Overflow HIHI Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_OVF1_FI1.DA_HH | No | BXX Overflow HIHI Alarm | 0 | 0
BXX_OVF1_FI1_DA_HI | BXX_OVF1_FI1 | BXX Overflow HI Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_OVF1_FI1.DA_HI | No | BXX Overflow HI Alarm | 0 | 0
BXX_OVF1_FI1_PB_HH | BXX_OVF1_FI1 | BXX Overflow HIHI Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HH.RE | No | BXX Overflow HIHI Alarm Enable | 0 | 0
BXX_OVF1_FI1_PB_AR | BXX_OVF1_FI1 | BXX Overflow Alarm Reset | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_AR | No | BXX Overflow Alarm Reset | 0 | 0
BXX_OVF1_FI1_DA_LO | BXX_OVF1_FI1 | BXX Overflow LO Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 90 | Direct | BXX | No | BXX_OVF1_FI1.DA_LO | No | BXX Overflow LO Alarm | 0 | 0
BXX_OVF1_FI1_PB_ER_DE | BXX_OVF1_FI1 | BXX Overflow Signal Error Alarm Dialer En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_ER.DE | No | BXX Overflow Signal Error Alarm Dialer En | 0 | 0
BXX_OVF1_FI1_PB_HH_DE | BXX_OVF1_FI1 | BXX Overflow HIHI Alarm Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HH.DE | No | BXX Overflow HIHI Alarm Dialer Enable | 0 | 0
BXX_OVF1_FI1_PB_ER_SR | BXX_OVF1_FI1 | BXX Overflow Signal Error Alarm Sup En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_ER.SR | No | BXX Overflow Signal Error Alarm Sup En | 0 | 0
BXX_OVF1_FI1_PB_HH_SR | BXX_OVF1_FI1 | BXX Overflow HIHI Alarm Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_OVF1_FI1.PB_HH.SR | No | BXX Overflow HIHI Alarm Sup Enable | 0 | 0
BXX_OVF1_FI1_DI_SS | BXX_OVF1_FI1 | BXX Overflow Event | 18 | No | Yes | 600 | Yes | Off | Normal | Overflow | None | 1 | Direct | BXX | No | BXX_OVFTL1.DI_SS | No | BXX Overflow Event | 0 | 0
BXX_OVF1_FI1_DA_SS | BXX_OVF1_FI1 | BXX Overflow Alarm | 18 | No | No | 0 | Yes | Off | Normal | Alarm | On | 9 | Direct | BXX | No | BXX_OVFTL1.DA_SS | No | BXX Overflow Alarm | 0 | 0
BXX_OVF1_FI1_PB_RS | BXX_OVF1_FI1 | BXX Overflow Manual Reset | 25 | No | Yes | 600 | Yes | Off | Off | Reset | None | 1 | Direct | BXX | No | BXX_OVFTL1.PB_RS | No | BXX Overflow Manual Reset | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_OVF1_FI1_AI_VI | BXX_OVF1_FI1 | BXX Overflow Number of Visible Eng Values | 41 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_OVF1_FI1.AI_VI | No | BXX Overflow Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_DC | BXX_OVF1_FI1 | BXX Overflow Precision | 22 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_OVF1_FI1.AI_DC | No | BXX Overflow Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_E2_DC | BXX_OVF1_FI1 | BXX Overflow Eng Value 2 Precision | 34 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_OVF1_FI1.E2_DC | No | BXX Overflow Eng Value 2 Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_HS | BXX_OVF1_FI1 | BXX Overflow Event Start Hour | 29 | No | Yes | 700 | Yes | No | 0 | 0 | Hour | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_HS | No | BXX Overflow Event Start Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_HS | BXX_OVF1_FI1 | BXX Overflow Event Stop Hour | 28 | No | Yes | 700 | Yes | No | 0 | 0 | Hour | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_HS | No | BXX Overflow Event Stop Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_MM | BXX_OVF1_FI1 | BXX Overflow Event Stop Month | 29 | No | Yes | 700 | Yes | No | 0 | 0 | Month | 1 | 1 | 12 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 12 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_MM | No | BXX Overflow Event Stop Month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_DY | BXX_OVF1_FI1 | BXX Overflow Event Stop Day | 27 | No | Yes | 700 | Yes | No | 0 | 0 | Day | 1 | 1 | 31 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 31 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_DY | No | BXX Overflow Event Stop Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_MS | BXX_OVF1_FI1 | BXX Overflow Event Stop Minute | 30 | No | Yes | 700 | Yes | No | 0 | 0 | Minutes | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_MS | No | BXX Overflow Event Stop Minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_YY | BXX_OVF1_FI1 | BXX Overflow Event Stop Year | 28 | No | Yes | 700 | Yes | No | 0 | 0 | Year | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 9999 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_YY | No | BXX Overflow Event Stop Year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_YY | BXX_OVF1_FI1 | BXX Overflow Event Start Year | 29 | No | Yes | 700 | Yes | No | 0 | 0 | Year | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 9999 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_YY | No | BXX Overflow Event Start Year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_SN | BXX_OVF1_FI1 | BXX Overflow Event Start Second | 31 | No | Yes | 700 | Yes | No | 0 | 0 | Seconds | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_SN | No | BXX Overflow Event Start Second | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_MS | BXX_OVF1_FI1 | BXX Overflow Event Start Minute | 31 | No | Yes | 700 | Yes | No | 0 | 0 | Minutes | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_MS | No | BXX Overflow Event Start Minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_MM | BXX_OVF1_FI1 | BXX Overflow Event Start Month | 30 | No | Yes | 700 | Yes | No | 0 | 0 | Month | 1 | 1 | 12 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 12 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_MM | No | BXX Overflow Event Start Month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_SP1_AI_SN | BXX_OVF1_FI1 | BXX Overflow Event Stop Second | 30 | No | Yes | 700 | Yes | No | 0 | 0 | Seconds | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_OVF1_TL1.SP.AI_SN | No | BXX Overflow Event Stop Second | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_TL1_AI_BE | BXX_OVF1_FI1 | BXX Overflow Total Number of Events | 35 | No | Yes | 700 | Yes | No | 0 | 0 | # | 0 | 0 | 32767 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 32767 | Linear | BXX | No | BXX_OVF1_TL1.AI_BE | No | BXX Overflow Total Number of Events | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_ST1_AI_DY | BXX_OVF1_FI1 | BXX Overflow Event Start Day | 28 | No | Yes | 700 | Yes | No | 0 | 0 | Day | 1 | 1 | 31 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 31 | Linear | BXX | No | BXX_OVF1_TL1.ST.AI_DY | No | BXX Overflow Event Start Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_TL1_AI_TM | BXX_OVF1_FI1 | BXX Overflow Event Duration | 27 | No | No | 0 | Yes | No | 0 | 0 | Minutes | 0 | 0 | 32767 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 32767 | Linear | BXX | No | BXX_OVF1_TL1.AI_TM | No | BXX Overflow Event Duration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_OVF1_FI1_SN_LL | BXX_OVF1_FI1 | BXX Overflow LOLO Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_OVF1_FI1.SN_LL | No | BXX Overflow LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_SN_HI | BXX_OVF1_FI1 | BXX Overflow High Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_OVF1_FI1.SN_HI | No | BXX Overflow High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_CV | BXX_OVF1_FI1 | BXX Overflow Current Value | 26 | Yes | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AI_CV | No | BXX Overflow Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_TD | BXX_OVF1_FI1 | BXX Overflow Total Today | 24 | Yes | No | 0 | Yes | No | 0 | 0 | m3 | 0 | 0 | 20000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 20000 | Linear | BXX | No | BXX_OVF1_FI1.AI_TD | No | BXX Overflow Total Today | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AI_YT | BXX_OVF1_FI1 | BXX Overflow Total Yesterday | 28 | Yes | No | 0 | Yes | No | 0 | 0 | m3 | 0 | 0 | 20000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 20000 | Linear | BXX | No | BXX_OVF1_FI1.AI_YT | No | BXX Overflow Total Yesterday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_XM | BXX_OVF1_FI1 | BXX Overflow Span Setpoint | 26 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_XM | No | BXX Overflow Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_LO | BXX_OVF1_FI1 | BXX Overflow Low Setpoint | 25 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_LO | No | BXX Overflow Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_HH | BXX_OVF1_FI1 | BXX Overflow HIHI Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_HH | No | BXX Overflow HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_E2_CV | BXX_OVF1_FI1 | BXX Overflow Units 2 | 20 | No | No | 0 | Yes | No | 0 | 0 | m3/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.E2_CV | No | BXX Overflow Units 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_HI | BXX_OVF1_FI1 | BXX Overflow High Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_HI | No | BXX Overflow High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_SV | BXX_OVF1_FI1 | BXX Overflow Override Value | 27 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_SV | No | BXX Overflow Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_EM | BXX_OVF1_FI1 | BXX Overflow Zero Setpoint | 26 | No | No | 0 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_EM | No | BXX Overflow Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_SN_HH | BXX_OVF1_FI1 | BXX Overflow HIHI Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_OVF1_FI1.SN_HH | No | BXX Overflow HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_SN_LO | BXX_OVF1_FI1 | BXX Overflow Low Alarm Delay | 28 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_OVF1_FI1.SN_LO | No | BXX Overflow Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_FI1_AO_LL | BXX_OVF1_FI1 | BXX Overflow LOLO Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | L/s | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_OVF1_FI1.AO_LL | No | BXX Overflow LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_OVF1_TL1_AI_CV | BXX_OVF1_FI1 | BXX Overflow Event Volume | 25 | Yes | No | 0 | Yes | No | 0 | 0 | m3 | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_OVF1_TL1.AI_CV | Yes | BXX Overflow Event Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_OVF1_FI1_DI_NM | BXX_OVF1_FI1 | BXX_OVF1_FI1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_OVF1_FI1_PB_HH_RN | BXX_OVF1_FI1 | BXX Overflow HIHI Alarm Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_HH_RN | No | BXX Overflow HIHI Alarm Disabled Reason
BXX_OVF1_FI1_PB_ER_RN | BXX_OVF1_FI1 | BXX Overflow Sig Error Alarm Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_OVF1_FI1_PB_ER_RN | No | BXX Overflow Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
OVF1_DA_SS | $System | Overflow Alarm Indirect Tag | 27 | No | 0 | No
OVF1_DI_SS | $System | Overflow Event Present Indirect Tag | 35 | No | 0 | No
OVF1_PB_RS | $System | Overflow Report Reset Indirect Tag | 34 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
OVF1_AI_BE | $System | Overflow Event Count Indirect Tag | 33 | No | 0 | No
OVF1_AI_CV | $System | Overflow Quantity Indirect Tag | 30 | No | 0 | No
OVF1_AI_TM | $System | Overflow Duration Indirect Tag | 30 | No | 0 | No
OVF1_SP_AI_DY | $System | Overflow End Day Indirect Tag | 29 | No | 0 | No
OVF1_SP_AI_HS | $System | Overflow End Hour Indirect Tag | 30 | No | 0 | No
OVF1_SP_AI_MM | $System | Overflow End Month Indirect Tag | 31 | No | 0 | No
OVF1_SP_AI_MS | $System | Overflow End Minute Indirect Tag | 32 | No | 0 | No
OVF1_SP_AI_SN | $System | Overflow End Second Indirect Tag | 32 | No | 0 | No
OVF1_SP_AI_YY | $System | Overflow End Year Indirect Tag | 30 | No | 0 | No
OVF1_ST_AI_DY | $System | Overflow Start Day Indirect Tag | 31 | No | 0 | No
OVF1_ST_AI_HS | $System | Overflow Start Hour Indirect Tag | 32 | No | 0 | No
OVF1_ST_AI_MM | $System | Overflow Start Month Indirect Tag | 33 | No | 0 | No
OVF1_ST_AI_MS | $System | Overflow Start Minute Indirect Tag | 34 | No | 0 | No
OVF1_ST_AI_SN | $System | Overflow Start Second Indirect Tag | 34 | No | 0 | No
OVF1_ST_AI_YY | $System | Overflow Start Year Indirect Tag | 32 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXSLP1II1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_SLP1_II1 | BXX | SLP1 Current | 12 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_SLP1_II1_DI_AD | BXX_DSAB | SLP1 Current Disabled Analog Alarm | 34 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_SLP1_II1.DI_AD | No | SLP1 Current Disabled Analog Alarm | 0 | 0
BXX_SLP1_II1_DI_SC | BXX_SLP1_II1 | SLP1 Current Scan Status | 24 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.DI_SC | No | SLP1 Current Scan Status | 0 | 0
BXX_SLP1_II1_DA_LL | BXX_SLP1_II1 | SLP1 Current LOLO Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP1_II1.DA_LL | No | SLP1 Current LOLO Alarm | 0 | 0
BXX_SLP1_II1_DA_ER | BXX_SLP1_II1 | SLP1 Current Signal Error Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_SLP1_II1.DA_ER | No | SLP1 Current Signal Error Alarm | 0 | 0
BXX_SLP1_II1_PB_SM | BXX_SLP1_II1 | SLP1 Current Alarm Test | 23 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_SM | No | SLP1 Current Alarm Test | 0 | 0
BXX_SLP1_II1_PB_SV | BXX_SLP1_II1 | SLP1 Current Override Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_SV | No | SLP1 Current Override Enable | 0 | 0
BXX_SLP1_II1_PB_AE | BXX_SLP1_II1 | SLP1 Current Alarm Enable | 25 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_AE.RE | No | SLP1 Current Alarm Enable | 0 | 0
BXX_SLP1_II1_PB_HI | BXX_SLP1_II1 | SLP1 Current High Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_HI.RE | No | SLP1 Current High Alarm Enable | 0 | 0
BXX_SLP1_II1_PB_LO | BXX_SLP1_II1 | SLP1 Current Low Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_LO.RE | No | SLP1 Current Low Alarm Enable | 0 | 0
BXX_SLP1_II1_PB_LL | BXX_SLP1_II1 | SLP1 Current LOLO Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_LL.RE | No | SLP1 Current LOLO Alarm Enable | 0 | 0
BXX_SLP1_II1_PB_ER | BXX_SLP1_II1 | SLP1 Current Signal Error Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_ER.RE | No | SLP1 Current Signal Error Alarm En | 0 | 0
BXX_SLP1_II1_PB_SC | BXX_SLP1_II1 | SLP1 Current Scan Enable | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_SC | No | SLP1 Current Scan Enable | 0 | 0
BXX_SLP1_II1_DA_HH | BXX_SLP1_II1 | SLP1 Current HIHI Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP1_II1.DA_HH | No | SLP1 Current HIHI Alarm | 0 | 0
BXX_SLP1_II1_DA_HI | BXX_SLP1_II1 | SLP1 Current HI Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP1_II1.DA_HI | No | SLP1 Current HI Alarm | 0 | 0
BXX_SLP1_II1_PB_HH | BXX_SLP1_II1 | SLP1 Current HIHI Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_HH.RE | No | SLP1 Current HIHI Alarm Enable | 0 | 0
BXX_SLP1_II1_PB_AR | BXX_SLP1_II1 | SLP1 Current Alarm Reset | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_AR | No | SLP1 Current Alarm Reset | 0 | 0
BXX_SLP1_II1_DA_LO | BXX_SLP1_II1 | SLP1 Current LO Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP1_II1.DA_LO | No | SLP1 Current LO Alarm | 0 | 0
BXX_SLP1_II1_PB_LL_DE | BXX_SLP1_II1 | SLP1 Current LOLO Alarm Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_LL.DE | No | SLP1 Current LOLO Alarm Dialer Enable | 0 | 0
BXX_SLP1_II1_PB_ER_DE | BXX_SLP1_II1 | SLP1 Current Signal Error Alarm Dialer En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_ER.DE | No | SLP1 Current Signal Error Alarm Dialer En | 0 | 0
BXX_SLP1_II1_PB_HH_DE | BXX_SLP1_II1 | SLP1 Current HIHI Alarm Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_HH.DE | No | SLP1 Current HIHI Alarm Dialer Enable | 0 | 0
BXX_SLP1_II1_PB_LL_SR | BXX_SLP1_II1 | SLP1 Current LOLO Alarm Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_LL.SR | No | SLP1 Current LOLO Alarm Sup Enable | 0 | 0
BXX_SLP1_II1_PB_ER_SR | BXX_SLP1_II1 | SLP1 Current Signal Error Alarm Sup En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_ER.SR | No | SLP1 Current Signal Error Alarm Sup En | 0 | 0
BXX_SLP1_II1_PB_HH_SR | BXX_SLP1_II1 | SLP1 Current HIHI Alarm Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_II1.PB_HH.SR | No | SLP1 Current HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP1_II1_AI_VI | BXX_SLP1_II1 | SLP1 Current Number of Visible Eng Values | 41 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_SLP1_II1.AI_VI | No | SLP1 Current Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_AI_DC | BXX_SLP1_II1 | SLP1 Current Precision | 22 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_SLP1_II1.AI_DC | No | SLP1 Current Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP1_II1_SN_LL | BXX_SLP1_II1 | SLP1 Current LOLO Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP1_II1.SN_LL | No | SLP1 Current LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_SN_HI | BXX_SLP1_II1 | SLP1 Current High Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP1_II1.SN_HI | No | SLP1 Current High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_AI_CV | BXX_SLP1_II1 | SLP1 Current Current Value | 26 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP1_II1.AI_CV | No | SLP1 Current Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_AO_XM | BXX_SLP1_II1 | SLP1 Current Span Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP1_II1.AO_XM | No | SLP1 Current Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_AO_LO | BXX_SLP1_II1 | SLP1 Current Low Setpoint | 25 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP1_II1.AO_LO | No | SLP1 Current Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_AO_HH | BXX_SLP1_II1 | SLP1 Current HIHI Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP1_II1.AO_HH | No | SLP1 Current HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_AO_HI | BXX_SLP1_II1 | SLP1 Current High Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP1_II1.AO_HI | No | SLP1 Current High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_AO_SV | BXX_SLP1_II1 | SLP1 Current Override Value | 27 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP1_II1.AO_SV | No | SLP1 Current Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_AO_EM | BXX_SLP1_II1 | SLP1 Current Zero Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP1_II1.AO_EM | No | SLP1 Current Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_SN_HH | BXX_SLP1_II1 | SLP1 Current HIHI Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP1_II1.SN_HH | No | SLP1 Current HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_SN_LO | BXX_SLP1_II1 | SLP1 Current Low Alarm Delay | 28 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP1_II1.SN_LO | No | SLP1 Current Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP1_II1_AO_LL | BXX_SLP1_II1 | SLP1 Current LOLO Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP1_II1.AO_LL | No | SLP1 Current LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_SLP1_II1_DI_NM | BXX_SLP1_II1 | BXX_SLP1_II1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_SLP1_II1_PB_HH_RN | BXX_SLP1_II1 | SLP1 Current HIHI Alarm Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP1_II1_PB_HH_RN | No | SLP1 Current HIHI Alarm Disabled Reason
BXX_SLP1_II1_PB_LL_RN | BXX_SLP1_II1 | SLP1 Current LOLO Alarm Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP1_II1_PB_LL_RN | No | SLP1 Current LOLO Alarm Disabled Reason
BXX_SLP1_II1_PB_ER_RN | BXX_SLP1_II1 | SLP1 Current Sig Error Alarm Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP1_II1_PB_ER_RN | No | SLP1 Current Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXSLP2II1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_SLP2_II1 | BXX | SLP1 Current | 12 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_SLP2_II1_DI_AD | BXX_DSAB | SLP1 Current Disabled Analog Alarm | 34 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_SLP2_II1.DI_AD | No | SLP1 Current Disabled Analog Alarm | 0 | 0
BXX_SLP2_II1_DI_SC | BXX_SLP2_II1 | SLP1 Current Scan Status | 24 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.DI_SC | No | SLP1 Current Scan Status | 0 | 0
BXX_SLP2_II1_DA_LL | BXX_SLP2_II1 | SLP1 Current LOLO Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP2_II1.DA_LL | No | SLP1 Current LOLO Alarm | 0 | 0
BXX_SLP2_II1_DA_ER | BXX_SLP2_II1 | SLP1 Current Signal Error Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_SLP2_II1.DA_ER | No | SLP1 Current Signal Error Alarm | 0 | 0
BXX_SLP2_II1_PB_SM | BXX_SLP2_II1 | SLP1 Current Alarm Test | 23 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_SM | No | SLP1 Current Alarm Test | 0 | 0
BXX_SLP2_II1_PB_SV | BXX_SLP2_II1 | SLP1 Current Override Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_SV | No | SLP1 Current Override Enable | 0 | 0
BXX_SLP2_II1_PB_AE | BXX_SLP2_II1 | SLP1 Current Alarm Enable | 25 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_AE.RE | No | SLP1 Current Alarm Enable | 0 | 0
BXX_SLP2_II1_PB_HI | BXX_SLP2_II1 | SLP1 Current High Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_HI.RE | No | SLP1 Current High Alarm Enable | 0 | 0
BXX_SLP2_II1_PB_LO | BXX_SLP2_II1 | SLP1 Current Low Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_LO.RE | No | SLP1 Current Low Alarm Enable | 0 | 0
BXX_SLP2_II1_PB_LL | BXX_SLP2_II1 | SLP1 Current LOLO Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_LL.RE | No | SLP1 Current LOLO Alarm Enable | 0 | 0
BXX_SLP2_II1_PB_ER | BXX_SLP2_II1 | SLP1 Current Signal Error Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_ER.RE | No | SLP1 Current Signal Error Alarm En | 0 | 0
BXX_SLP2_II1_PB_SC | BXX_SLP2_II1 | SLP1 Current Scan Enable | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_SC | No | SLP1 Current Scan Enable | 0 | 0
BXX_SLP2_II1_DA_HH | BXX_SLP2_II1 | SLP1 Current HIHI Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP2_II1.DA_HH | No | SLP1 Current HIHI Alarm | 0 | 0
BXX_SLP2_II1_DA_HI | BXX_SLP2_II1 | SLP1 Current HI Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP2_II1.DA_HI | No | SLP1 Current HI Alarm | 0 | 0
BXX_SLP2_II1_PB_HH | BXX_SLP2_II1 | SLP1 Current HIHI Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_HH.RE | No | SLP1 Current HIHI Alarm Enable | 0 | 0
BXX_SLP2_II1_PB_AR | BXX_SLP2_II1 | SLP1 Current Alarm Reset | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_AR | No | SLP1 Current Alarm Reset | 0 | 0
BXX_SLP2_II1_DA_LO | BXX_SLP2_II1 | SLP1 Current LO Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP2_II1.DA_LO | No | SLP1 Current LO Alarm | 0 | 0
BXX_SLP2_II1_PB_LL_DE | BXX_SLP2_II1 | SLP1 Current LOLO Alarm Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_LL.DE | No | SLP1 Current LOLO Alarm Dialer Enable | 0 | 0
BXX_SLP2_II1_PB_ER_DE | BXX_SLP2_II1 | SLP1 Current Signal Error Alarm Dialer En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_ER.DE | No | SLP1 Current Signal Error Alarm Dialer En | 0 | 0
BXX_SLP2_II1_PB_HH_DE | BXX_SLP2_II1 | SLP1 Current HIHI Alarm Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_HH.DE | No | SLP1 Current HIHI Alarm Dialer Enable | 0 | 0
BXX_SLP2_II1_PB_LL_SR | BXX_SLP2_II1 | SLP1 Current LOLO Alarm Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_LL.SR | No | SLP1 Current LOLO Alarm Sup Enable | 0 | 0
BXX_SLP2_II1_PB_ER_SR | BXX_SLP2_II1 | SLP1 Current Signal Error Alarm Sup En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_ER.SR | No | SLP1 Current Signal Error Alarm Sup En | 0 | 0
BXX_SLP2_II1_PB_HH_SR | BXX_SLP2_II1 | SLP1 Current HIHI Alarm Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_II1.PB_HH.SR | No | SLP1 Current HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP2_II1_AI_VI | BXX_SLP2_II1 | SLP1 Current Number of Visible Eng Values | 41 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_SLP2_II1.AI_VI | No | SLP1 Current Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_AI_DC | BXX_SLP2_II1 | SLP1 Current Precision | 22 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_SLP2_II1.AI_DC | No | SLP1 Current Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP2_II1_SN_LL | BXX_SLP2_II1 | SLP1 Current LOLO Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP2_II1.SN_LL | No | SLP1 Current LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_SN_HI | BXX_SLP2_II1 | SLP1 Current High Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP2_II1.SN_HI | No | SLP1 Current High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_AI_CV | BXX_SLP2_II1 | SLP1 Current Current Value | 26 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP2_II1.AI_CV | No | SLP1 Current Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_AO_XM | BXX_SLP2_II1 | SLP1 Current Span Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP2_II1.AO_XM | No | SLP1 Current Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_AO_LO | BXX_SLP2_II1 | SLP1 Current Low Setpoint | 25 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP2_II1.AO_LO | No | SLP1 Current Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_AO_HH | BXX_SLP2_II1 | SLP1 Current HIHI Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP2_II1.AO_HH | No | SLP1 Current HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_AO_HI | BXX_SLP2_II1 | SLP1 Current High Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP2_II1.AO_HI | No | SLP1 Current High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_AO_SV | BXX_SLP2_II1 | SLP1 Current Override Value | 27 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP2_II1.AO_SV | No | SLP1 Current Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_AO_EM | BXX_SLP2_II1 | SLP1 Current Zero Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP2_II1.AO_EM | No | SLP1 Current Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_SN_HH | BXX_SLP2_II1 | SLP1 Current HIHI Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP2_II1.SN_HH | No | SLP1 Current HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_SN_LO | BXX_SLP2_II1 | SLP1 Current Low Alarm Delay | 28 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP2_II1.SN_LO | No | SLP1 Current Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_II1_AO_LL | BXX_SLP2_II1 | SLP1 Current LOLO Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP2_II1.AO_LL | No | SLP1 Current LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_SLP2_II1_DI_NM | BXX_SLP2_II1 | BXX_SLP2_II1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_SLP2_II1_PB_HH_RN | BXX_SLP2_II1 | SLP1 Current HIHI Alarm Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP2_II1_PB_HH_RN | No | SLP1 Current HIHI Alarm Disabled Reason
BXX_SLP2_II1_PB_LL_RN | BXX_SLP2_II1 | SLP1 Current LOLO Alarm Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP2_II1_PB_LL_RN | No | SLP1 Current LOLO Alarm Disabled Reason
BXX_SLP2_II1_PB_ER_RN | BXX_SLP2_II1 | SLP1 Current Sig Error Alarm Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP2_II1_PB_ER_RN | No | SLP1 Current Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXSLP3II1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_SLP3_II1 | BXX | SLP1 Current | 12 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_SLP3_II1_DI_AD | BXX_DSAB | SLP1 Current Disabled Analog Alarm | 34 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_SLP3_II1.DI_AD | No | SLP1 Current Disabled Analog Alarm | 0 | 0
BXX_SLP3_II1_DI_SC | BXX_SLP3_II1 | SLP1 Current Scan Status | 24 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.DI_SC | No | SLP1 Current Scan Status | 0 | 0
BXX_SLP3_II1_DA_LL | BXX_SLP3_II1 | SLP1 Current LOLO Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP3_II1.DA_LL | No | SLP1 Current LOLO Alarm | 0 | 0
BXX_SLP3_II1_DA_ER | BXX_SLP3_II1 | SLP1 Current Signal Error Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_SLP3_II1.DA_ER | No | SLP1 Current Signal Error Alarm | 0 | 0
BXX_SLP3_II1_PB_SM | BXX_SLP3_II1 | SLP1 Current Alarm Test | 23 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_SM | No | SLP1 Current Alarm Test | 0 | 0
BXX_SLP3_II1_PB_SV | BXX_SLP3_II1 | SLP1 Current Override Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_SV | No | SLP1 Current Override Enable | 0 | 0
BXX_SLP3_II1_PB_AE | BXX_SLP3_II1 | SLP1 Current Alarm Enable | 25 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_AE.RE | No | SLP1 Current Alarm Enable | 0 | 0
BXX_SLP3_II1_PB_HI | BXX_SLP3_II1 | SLP1 Current High Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_HI.RE | No | SLP1 Current High Alarm Enable | 0 | 0
BXX_SLP3_II1_PB_LO | BXX_SLP3_II1 | SLP1 Current Low Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_LO.RE | No | SLP1 Current Low Alarm Enable | 0 | 0
BXX_SLP3_II1_PB_LL | BXX_SLP3_II1 | SLP1 Current LOLO Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_LL.RE | No | SLP1 Current LOLO Alarm Enable | 0 | 0
BXX_SLP3_II1_PB_ER | BXX_SLP3_II1 | SLP1 Current Signal Error Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_ER.RE | No | SLP1 Current Signal Error Alarm En | 0 | 0
BXX_SLP3_II1_PB_SC | BXX_SLP3_II1 | SLP1 Current Scan Enable | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_SC | No | SLP1 Current Scan Enable | 0 | 0
BXX_SLP3_II1_DA_HH | BXX_SLP3_II1 | SLP1 Current HIHI Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP3_II1.DA_HH | No | SLP1 Current HIHI Alarm | 0 | 0
BXX_SLP3_II1_DA_HI | BXX_SLP3_II1 | SLP1 Current HI Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP3_II1.DA_HI | No | SLP1 Current HI Alarm | 0 | 0
BXX_SLP3_II1_PB_HH | BXX_SLP3_II1 | SLP1 Current HIHI Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_HH.RE | No | SLP1 Current HIHI Alarm Enable | 0 | 0
BXX_SLP3_II1_PB_AR | BXX_SLP3_II1 | SLP1 Current Alarm Reset | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_AR | No | SLP1 Current Alarm Reset | 0 | 0
BXX_SLP3_II1_DA_LO | BXX_SLP3_II1 | SLP1 Current LO Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP3_II1.DA_LO | No | SLP1 Current LO Alarm | 0 | 0
BXX_SLP3_II1_PB_LL_DE | BXX_SLP3_II1 | SLP1 Current LOLO Alarm Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_LL.DE | No | SLP1 Current LOLO Alarm Dialer Enable | 0 | 0
BXX_SLP3_II1_PB_ER_DE | BXX_SLP3_II1 | SLP1 Current Signal Error Alarm Dialer En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_ER.DE | No | SLP1 Current Signal Error Alarm Dialer En | 0 | 0
BXX_SLP3_II1_PB_HH_DE | BXX_SLP3_II1 | SLP1 Current HIHI Alarm Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_HH.DE | No | SLP1 Current HIHI Alarm Dialer Enable | 0 | 0
BXX_SLP3_II1_PB_LL_SR | BXX_SLP3_II1 | SLP1 Current LOLO Alarm Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_LL.SR | No | SLP1 Current LOLO Alarm Sup Enable | 0 | 0
BXX_SLP3_II1_PB_ER_SR | BXX_SLP3_II1 | SLP1 Current Signal Error Alarm Sup En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_ER.SR | No | SLP1 Current Signal Error Alarm Sup En | 0 | 0
BXX_SLP3_II1_PB_HH_SR | BXX_SLP3_II1 | SLP1 Current HIHI Alarm Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_II1.PB_HH.SR | No | SLP1 Current HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP3_II1_AI_VI | BXX_SLP3_II1 | SLP1 Current Number of Visible Eng Values | 41 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_SLP3_II1.AI_VI | No | SLP1 Current Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_AI_DC | BXX_SLP3_II1 | SLP1 Current Precision | 22 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_SLP3_II1.AI_DC | No | SLP1 Current Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP3_II1_SN_LL | BXX_SLP3_II1 | SLP1 Current LOLO Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP3_II1.SN_LL | No | SLP1 Current LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_SN_HI | BXX_SLP3_II1 | SLP1 Current High Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP3_II1.SN_HI | No | SLP1 Current High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_AI_CV | BXX_SLP3_II1 | SLP1 Current Current Value | 26 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP3_II1.AI_CV | No | SLP1 Current Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_AO_XM | BXX_SLP3_II1 | SLP1 Current Span Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP3_II1.AO_XM | No | SLP1 Current Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_AO_LO | BXX_SLP3_II1 | SLP1 Current Low Setpoint | 25 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP3_II1.AO_LO | No | SLP1 Current Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_AO_HH | BXX_SLP3_II1 | SLP1 Current HIHI Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP3_II1.AO_HH | No | SLP1 Current HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_AO_HI | BXX_SLP3_II1 | SLP1 Current High Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP3_II1.AO_HI | No | SLP1 Current High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_AO_SV | BXX_SLP3_II1 | SLP1 Current Override Value | 27 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP3_II1.AO_SV | No | SLP1 Current Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_AO_EM | BXX_SLP3_II1 | SLP1 Current Zero Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP3_II1.AO_EM | No | SLP1 Current Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_SN_HH | BXX_SLP3_II1 | SLP1 Current HIHI Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP3_II1.SN_HH | No | SLP1 Current HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_SN_LO | BXX_SLP3_II1 | SLP1 Current Low Alarm Delay | 28 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP3_II1.SN_LO | No | SLP1 Current Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP3_II1_AO_LL | BXX_SLP3_II1 | SLP1 Current LOLO Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP3_II1.AO_LL | No | SLP1 Current LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_SLP3_II1_DI_NM | BXX_SLP3_II1 | BXX_SLP3_II1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_SLP3_II1_PB_HH_RN | BXX_SLP3_II1 | SLP1 Current HIHI Alarm Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP3_II1_PB_HH_RN | No | SLP1 Current HIHI Alarm Disabled Reason
BXX_SLP3_II1_PB_LL_RN | BXX_SLP3_II1 | SLP1 Current LOLO Alarm Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP3_II1_PB_LL_RN | No | SLP1 Current LOLO Alarm Disabled Reason
BXX_SLP3_II1_PB_ER_RN | BXX_SLP3_II1 | SLP1 Current Sig Error Alarm Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP3_II1_PB_ER_RN | No | SLP1 Current Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN_DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXSLP4II1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_SLP4_II1 | BXX | SLP1 Current | 12 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_SLP4_II1_DI_AD | BXX_DSAB | SLP1 Current Disabled Analog Alarm | 34 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_SLP4_II1.DI_AD | No | SLP1 Current Disabled Analog Alarm | 0 | 0
BXX_SLP4_II1_DI_SC | BXX_SLP4_II1 | SLP1 Current Scan Status | 24 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.DI_SC | No | SLP1 Current Scan Status | 0 | 0
BXX_SLP4_II1_DA_LL | BXX_SLP4_II1 | SLP1 Current LOLO Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP4_II1.DA_LL | No | SLP1 Current LOLO Alarm | 0 | 0
BXX_SLP4_II1_DA_ER | BXX_SLP4_II1 | SLP1 Current Signal Error Alarm | 31 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_SLP4_II1.DA_ER | No | SLP1 Current Signal Error Alarm | 0 | 0
BXX_SLP4_II1_PB_SM | BXX_SLP4_II1 | SLP1 Current Alarm Test | 23 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_SM | No | SLP1 Current Alarm Test | 0 | 0
BXX_SLP4_II1_PB_SV | BXX_SLP4_II1 | SLP1 Current Override Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_SV | No | SLP1 Current Override Enable | 0 | 0
BXX_SLP4_II1_PB_AE | BXX_SLP4_II1 | SLP1 Current Alarm Enable | 25 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_AE.RE | No | SLP1 Current Alarm Enable | 0 | 0
BXX_SLP4_II1_PB_HI | BXX_SLP4_II1 | SLP1 Current High Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_HI.RE | No | SLP1 Current High Alarm Enable | 0 | 0
BXX_SLP4_II1_PB_LO | BXX_SLP4_II1 | SLP1 Current Low Alarm Enable | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_LO.RE | No | SLP1 Current Low Alarm Enable | 0 | 0
BXX_SLP4_II1_PB_LL | BXX_SLP4_II1 | SLP1 Current LOLO Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_LL.RE | No | SLP1 Current LOLO Alarm Enable | 0 | 0
BXX_SLP4_II1_PB_ER | BXX_SLP4_II1 | SLP1 Current Signal Error Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_ER.RE | No | SLP1 Current Signal Error Alarm En | 0 | 0
BXX_SLP4_II1_PB_SC | BXX_SLP4_II1 | SLP1 Current Scan Enable | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_SC | No | SLP1 Current Scan Enable | 0 | 0
BXX_SLP4_II1_DA_HH | BXX_SLP4_II1 | SLP1 Current HIHI Alarm | 23 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP4_II1.DA_HH | No | SLP1 Current HIHI Alarm | 0 | 0
BXX_SLP4_II1_DA_HI | BXX_SLP4_II1 | SLP1 Current HI Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP4_II1.DA_HI | No | SLP1 Current HI Alarm | 0 | 0
BXX_SLP4_II1_PB_HH | BXX_SLP4_II1 | SLP1 Current HIHI Alarm Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_HH.RE | No | SLP1 Current HIHI Alarm Enable | 0 | 0
BXX_SLP4_II1_PB_AR | BXX_SLP4_II1 | SLP1 Current Alarm Reset | 24 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_AR | No | SLP1 Current Alarm Reset | 0 | 0
BXX_SLP4_II1_DA_LO | BXX_SLP4_II1 | SLP1 Current LO Alarm | 21 | No | No | 0 | Yes | Off | Ok | Alarm | On | 74 | Direct | BXX | No | BXX_SLP4_II1.DA_LO | No | SLP1 Current LO Alarm | 0 | 0
BXX_SLP4_II1_PB_LL_DE | BXX_SLP4_II1 | SLP1 Current LOLO Alarm Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_LL.DE | No | SLP1 Current LOLO Alarm Dialer Enable | 0 | 0
BXX_SLP4_II1_PB_ER_DE | BXX_SLP4_II1 | SLP1 Current Signal Error Alarm Dialer En | 41 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_ER.DE | No | SLP1 Current Signal Error Alarm Dialer En | 0 | 0
BXX_SLP4_II1_PB_HH_DE | BXX_SLP4_II1 | SLP1 Current HIHI Alarm Dialer Enable | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_HH.DE | No | SLP1 Current HIHI Alarm Dialer Enable | 0 | 0
BXX_SLP4_II1_PB_LL_SR | BXX_SLP4_II1 | SLP1 Current LOLO Alarm Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_LL.SR | No | SLP1 Current LOLO Alarm Sup Enable | 0 | 0
BXX_SLP4_II1_PB_ER_SR | BXX_SLP4_II1 | SLP1 Current Signal Error Alarm Sup En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_ER.SR | No | SLP1 Current Signal Error Alarm Sup En | 0 | 0
BXX_SLP4_II1_PB_HH_SR | BXX_SLP4_II1 | SLP1 Current HIHI Alarm Sup Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_II1.PB_HH.SR | No | SLP1 Current HIHI Alarm Sup Enable | 0 | 0
:IOInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP4_II1_AI_VI | BXX_SLP4_II1 | SLP1 Current Number of Visible Eng Values | 41 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_SLP4_II1.AI_VI | No | SLP1 Current Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_AI_DC | BXX_SLP4_II1 | SLP1 Current Precision | 22 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_SLP4_II1.AI_DC | No | SLP1 Current Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP4_II1_SN_LL | BXX_SLP4_II1 | SLP1 Current LOLO Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP4_II1.SN_LL | No | SLP1 Current LOLO Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_SN_HI | BXX_SLP4_II1 | SLP1 Current High Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP4_II1.SN_HI | No | SLP1 Current High Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_AI_CV | BXX_SLP4_II1 | SLP1 Current Current Value | 26 | Yes | No | 0 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 1.5 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP4_II1.AI_CV | No | SLP1 Current Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_AO_XM | BXX_SLP4_II1 | SLP1 Current Span Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP4_II1.AO_XM | No | SLP1 Current Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_AO_LO | BXX_SLP4_II1 | SLP1 Current Low Setpoint | 25 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP4_II1.AO_LO | No | SLP1 Current Low Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_AO_HH | BXX_SLP4_II1 | SLP1 Current HIHI Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP4_II1.AO_HH | No | SLP1 Current HIHI Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_AO_HI | BXX_SLP4_II1 | SLP1 Current High Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP4_II1.AO_HI | No | SLP1 Current High Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_AO_SV | BXX_SLP4_II1 | SLP1 Current Override Value | 27 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP4_II1.AO_SV | No | SLP1 Current Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_AO_EM | BXX_SLP4_II1 | SLP1 Current Zero Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP4_II1.AO_EM | No | SLP1 Current Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_SN_HH | BXX_SLP4_II1 | SLP1 Current HIHI Alarm Delay | 29 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP4_II1.SN_HH | No | SLP1 Current HIHI Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_SN_LO | BXX_SLP4_II1 | SLP1 Current Low Alarm Delay | 28 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_SLP4_II1.SN_LO | No | SLP1 Current Low Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_II1_AO_LL | BXX_SLP4_II1 | SLP1 Current LOLO Setpoint | 26 | No | Yes | 900 | Yes | No | 0 | 0 | A | 0 | 0 | 150 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 150 | Linear | BXX | No | BXX_SLP4_II1.AO_LL | No | SLP1 Current LOLO Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_SLP4_II1_DI_NM | BXX_SLP4_II1 | BXX_SLP4_II1 | 12 | No | No | 0 | Yes | 24 | BXXDEV1FI1 | BXXDEV1FI1 | Yes
ALRM_AGRP | $System | Indirect Alarm Query | 20 | No | No | 0 | No | 131
ANIN_NAME | $System | Analog Input Tag Name - Indirect | 32 | No | No | 0 | No | 131
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_SLP4_II1_PB_HH_RN | BXX_SLP4_II1 | SLP1 Current HIHI Alarm Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP4_II1_PB_HH_RN | No | SLP1 Current HIHI Alarm Disabled Reason
BXX_SLP4_II1_PB_LL_RN | BXX_SLP4_II1 | SLP1 Current LOLO Alarm Disabled Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP4_II1_PB_LL_RN | No | SLP1 Current LOLO Alarm Disabled Reason
BXX_SLP4_II1_PB_ER_RN | BXX_SLP4_II1 | SLP1 Current Sig Error Alarm Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP4_II1_PB_ER_RN | No | SLP1 Current Sig Error Alarm Dis Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_PB_AE | $System | Analog Input Enable Request Alarm - Indirect | 44 | No | 0 | No
ANIN_PB_HH | $System | Analog Input Enable HIHI Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_HI | $System | Analog Input Enable HI Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LO | $System | Analog Input Enable LO Alarm - Indirect | 39 | No | 0 | No
ANIN_PB_LL | $System | Analog Input Enable LOLO Alarm - Indirect | 41 | No | 0 | No
ANIN_PB_ER | $System | Analog Input Enable Signal Error Alarm - Indirect | 49 | No | 0 | No
ANIN_PB_SC | $System | Analog Input Scan Enable - Indirect | 35 | No | 0 | No
ANIN_PB_AD | $System | Analog Input Alarms Disabled - Indirect | 39 | No | 0 | No
ANIN__DA_ER | $System | Analog Input Signal Error Alarm - Indirect | 42 | No | 0 | No
ANIN_DI_SC | $System | Analog Input On Scan - Indirect | 31 | No | 0 | No
ANIN_PB_SV | $System | Analog Input Simulation Enable - Indirect | 41 | No | 0 | No
ANIN_PB_SM | $System | Analog Input Simulate Alarms Pushbutton Ind Tag | 47 | No | 0 | No
ANIN_PB_AR | $System | Indirect Analog Alarm Reset PB | 30 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_AO_XM | $System | Analog Input Maximum Engineering Units - Indirect | 49 | No | 0 | No
ANIN_AO_SV | $System | Analog Override Value From HMI - Indirect | 41 | No | 0 | No
ANIN_AI_CV | $System | Analog Input Current Value - Indirect | 37 | No | 0 | No
ANIN_AO_HH | $System | Analog Input HIHI - Indirect | 28 | No | 0 | No
ANIN_AO_HI | $System | Analog Input HI - Indirect | 26 | No | 0 | No
ANIN_AO_LL | $System | Analog Input LOLO - Indirect | 28 | No | 0 | No
ANIN_AO_LO | $System | Analog Input LO - Indirect | 26 | No | 0 | No
ANIN_SN_HH | $System | Indirect HIHI Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_SN_LO | $System | Indirect LO Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_HI | $System | Indirect HI Alarm Delay Time Setpoint | 37 | No | 0 | No
ANIN_SN_LL | $System | Indirect LOLO Alarm Delay Time Setpoint | 39 | No | 0 | No
ANIN_E1_EM | $System | Analog Input Eng Units Range 1 Minimum Value | 44 | No | 0 | No
ANIN_E1_XM | $System | Analog Input Eng Units Range 1 Maximum Value | 44 | No | 0 | No
ANIN_E2_CV | $System | Analog Value Second Units Indirect Tag | 38 | No | 0 | No
ANIN_E3_CV | $System | Analog Value Third Units Indirect Tag | 37 | No | 0 | No
ANIN_AI_VI | $System | Analog Units Visibility Selection - Indirect | 44 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ANIN_SRV | $System | Analog Input Alarm Server Indirect Tag | 38 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
ANIN_GRP | $System | Analog Input Group - Indirect | 29
0

## BXXSLP1DM1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_SLP1_DM1 | BXX | BXX Pump 1 | 10 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:Memory_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_SLP1_DM1_DI_AD | BXX_DSAB | BXX Pump 1 Disabled Alarm | 25 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_SLP1_DM1.DI_AD | No | BXX Pump 1 Disabled Alarm | 0 | 0
BXX_SLP1_DM1_DI_CL | BXX_SLP1_DM1 | BXX Pump 1 Control Mode | 23 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DI_CL.eng | No | BXX Pump 1 Control Mode | 0 | 0
BXX_SLP1_DM1_DI_SS | BXX_SLP1_DM1 | BXX Pump 1 Running Status | 25 | Yes | Yes | 700 | Yes | Off | Stopped | Running | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DI_SS.eng | No | BXX Pump 1 Running Status | 0 | 0
BXX_SLP1_DM1_DA_ES | BXX_SLP1_DM1 | BXX Pump 1 E-Stop | 17 | No | No | 0 | Yes | Off | Normal | Alarm | On | 50 | Direct | BXX | No | BXX_SLP1_DM1.DA_ES.eng | No | BXX Pump 1 E-Stop | 0 | 0
BXX_SLP1_DM1_DA_RA | BXX_SLP1_DM1 | BXX Pump 1 Overload | 19 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_SLP1_DM1.DA_RA.eng | No | BXX Pump 1 Overload | 0 | 0
BXX_SLP1_DM1_DA_DF | BXX_SLP1_DM1 | BXX Pump 1 Not Ready | 20 | No | No | 0 | Yes | Off | Normal | Not Ready | On | 55 | Direct | BXX | No | BXX_SLP1_DM1.DA_DF.eng | No | BXX Pump 1 Not Ready | 0 | 0
BXX_SLP1_DM1_DA_GA | BXX_SLP1_DM1 | BXX Pump 1 Soft Starter Fault | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 55 | Direct | BXX | No | BXX_SLP1_DM1.DA_GA.eng | No | BXX Pump 1 Soft Starter Fault | 0 | 0
BXX_SLP1_DM1_DA_TA | BXX_SLP1_DM1 | BXX Pump 1 Temp/Leak Alarm | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 58 | Direct | BXX | No | BXX_SLP1_DM1.DA_TA.eng | No | BXX Pump 1 Temp/Leak Alarm | 0 | 0
BXX_SLP1_DM1_DI_AA | BXX_SLP1_DM1 | BXX Pump 1 Auto Mode | 20 | No | Yes | 700 | Yes | Off | PLT-MAN | AUTO | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DI_AA | No | BXX Pump 1 Auto Mode | 0 | 0
BXX_SLP1_DM1_DI_PM | BXX_SLP1_DM1 | BXX Pump 1 Plant Manual Mode | 28 | No | Yes | 700 | Yes | Off | AUTO | PLT-MAN | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DI_PM | No | BXX Pump 1 Plant Manual Mode | 0 | 0
BXX_SLP1_DM1_PB_PM | BXX_SLP1_DM1 | BXX Pump 1 Plant Manual Mode RQ | 31 | No | Yes | 600 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_PM | No | BXX Pump 1 Plant Manual Mode RQ | 0 | 0
BXX_SLP1_DM1_PB_PT | BXX_SLP1_DM1 | BXX Pump 1 Plant Manual Start | 29 | No | Yes | 600 | Yes | Off | Normal | Start | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_PT | No | BXX Pump 1 Plant Manual Start | 0 | 0
BXX_SLP1_DM1_PB_PP | BXX_SLP1_DM1 | BXX Pump 1 Plant Manual Stop | 28 | No | Yes | 600 | Yes | Off | Normal | Stop | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_PP | No | BXX Pump 1 Plant Manual Stop | 0 | 0
BXX_SLP1_DM1_PB_AR | BXX_SLP1_DM1 | BXX Pump 1 Alarm Ack | 20 | No | Yes | 600 | Yes | Off | Normal | Ack | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_AR | No | BXX Pump 1 Alarm Ack | 0 | 0
BXX_SLP1_DM1_PB_RT | BXX_SLP1_DM1 | BXX Pump 1 Runtime Reset | 24 | No | Yes | 600 | Yes | Off | Normal | Reset | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_RT | No | BXX Pump 1 Runtime Reset | 0 | 0
BXX_SLP1_DM1_DA_SF | BXX_SLP1_DM1 | BXX Pump 1 Failed To Start | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_SLP1_DM1.DA_SF | No | BXX Pump 1 Failed To Start | 0 | 0
BXX_SLP1_DM1_DA_XF | BXX_SLP1_DM1 | BXX Pump 1 Failed To Stop | 25 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_SLP1_DM1.DA_XF | No | BXX Pump 1 Failed To Stop | 0 | 0
BXX_SLP1_DM1_DA_SU | BXX_SLP1_DM1 | BXX Pump 1 Uncommanded Start | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 53 | Direct | BXX | No | BXX_SLP1_DM1.DA_SU | No | BXX Pump 1 Uncommanded Start | 0 | 0
BXX_SLP1_DM1_DA_XU | BXX_SLP1_DM1 | BXX Pump 1 Uncommanded Stop | 27 | No | No | 0 | Yes | Off | Normal | Alarm | On | 54 | Direct | BXX | No | BXX_SLP1_DM1.DA_XU | No | BXX Pump 1 Uncommanded Stop | 0 | 0
BXX_SLP1_DM1_DI_BP | BXX_SLP1_DM1 | BXX Pump 1 Bypass Mode | 22 | No | Yes | 700 | Yes | Off | Normal | Bypass | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DI_BP.eng | No | BXX Pump 1 Bypass Mode | 0 | 0
BXX_SLP1_DM1_DI_ST | BXX_SLP1_DM1 | BXX Pump 1 Hardwired Start | 26 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DI_ST.eng | No | BXX Pump 1 Hardwired Start | 0 | 0
BXX_SLP1_DM1_DI_SP | BXX_SLP1_DM1 | BXX Pump 1 Hardwired Stop | 25 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DI_SP.eng | No | BXX Pump 1 Hardwired Stop | 0 | 0
BXX_SLP1_DM1_PB_SU | BXX_SLP1_DM1 | BXX Pump 1 Uncomm Start Alarm En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_SU.RE | No | BXX Pump 1 Uncomm Start Alarm En | 0 | 0
BXX_SLP1_DM1_PB_SF | BXX_SLP1_DM1 | BXX Pump 1 Failed To Start Alarm En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_SF.RE | No | BXX Pump 1 Failed To Start Alarm En | 0 | 0
BXX_SLP1_DM1_PB_XF | BXX_SLP1_DM1 | BXX Pump 1 Failed To Stop Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_XF.RE | No | BXX Pump 1 Failed To Stop Alarm En | 0 | 0
BXX_SLP1_DM1_PB_XU | BXX_SLP1_DM1 | BXX Pump 1 Uncomm. Stop Alarm En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_XU.RE | No | BXX Pump 1 Uncomm. Stop Alarm En | 0 | 0
BXX_SLP1_DM1_PB_SM | BXX_SLP1_DM1 | BXX Pump 1 Simulate Alarms PB | 29 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_SM | No | BXX Pump 1 Simulate Alarms PB | 0 | 0
BXX_SLP1_DM1_PB_AE | BXX_SLP1_DM1 | BXX Pump 1 Alarm Enable | 23 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_AE.RE | No | BXX Pump 1 Alarm Enable | 0 | 0
BXX_SLP1_DM1_PB_AE_DE | BXX_SLP1_DM1 | BXX Pump 1 Alarms Dialer Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_AE.DE | No | BXX Pump 1 Alarms Dialer Enable | 0 | 0
BXX_SLP1_DM1_PB_AE_SR | BXX_SLP1_DM1 | BXX Pump 1 Alarms Sup Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.PB_AE.SR | No | BXX Pump 1 Alarms Sup Enable | 0 | 0
BXX_SLP1_DM1_PB_ES_RE | BXX_SLP1_DM1 | BXX Pump 1 E-Stop Enable | 24 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_ES.RE | No | BXX Pump 1 E-Stop Enable | 0 | 0
BXX_SLP1_DM1_PB_RA_RE | BXX_SLP1_DM1 | BXX Pump 1 Overload Enable | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_RA.RE | No | BXX Pump 1 Overload Enable | 0 | 0
BXX_SLP1_DM1_PB_DF_RE | BXX_SLP1_DM1 | BXX Pump 1 Not Ready Enable | 27 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_DF.RE | No | BXX Pump 1 Not Ready Enable | 0 | 0
BXX_SLP1_DM1_PB_GA_RE | BXX_SLP1_DM1 | BXX Pump 1 Soft Starter Fault Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_GA.RE | No | BXX Pump 1 Soft Starter Fault Enable | 0 | 0
BXX_SLP1_DM1_PB_TA_RE | BXX_SLP1_DM1 | BXX Pump 1 Temp/Leak Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_TA.RE | No | BXX Pump 1 Temp/Leak Alarm Enable | 0 | 0
BXX_SLP1_DM1_PB_ES_DE | BXX_SLP1_DM1 | BXX Pump 1 E-Stop Dialer Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_ES.DE | No | BXX Pump 1 E-Stop Dialer Enable | 0 | 0
BXX_SLP1_DM1_PB_RA_DE | BXX_SLP1_DM1 | BXX Pump 1 Overload Dialer Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_RA.DE | No | BXX Pump 1 Overload Dialer Enable | 0 | 0
BXX_SLP1_DM1_PB_DF_DE | BXX_SLP1_DM1 | BXX Pump 1 Not Ready Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_DF.DE | No | BXX Pump 1 Not Ready Dialer Enable | 0 | 0
BXX_SLP1_DM1_PB_MA_DE | BXX_SLP1_DM1 | BXX Pump 1 Loss of Prime Dialer Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_MA.DE | No | BXX Pump 1 Loss of Prime Dialer Enable | 0 | 0
BXX_SLP1_DM1_PB_GA_DE | BXX_SLP1_DM1 | BXX Pump 1 Soft Starter Fault Dialer Enable | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_GA.DE | No | BXX Pump 1 Soft Starter Fault Dialer Enable | 0 | 0
BXX_SLP1_DM1_PB_TA_DE | BXX_SLP1_DM1 | BXX Pump 1 Temp/Leak Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_TA.DE | No | BXX Pump 1 Temp/Leak Dialer Enable | 0 | 0
BXX_SLP1_DM1_PB_ES_SR | BXX_SLP1_DM1 | BXX Pump 1 E-Stop Sup Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_ES.SR | No | BXX Pump 1 E-Stop Sup Enable | 0 | 0
BXX_SLP1_DM1_PB_RA_SR | BXX_SLP1_DM1 | BXX Pump 1 Overload Sup Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_RA.SR | No | BXX Pump 1 Overload Sup Enable | 0 | 0
BXX_SLP1_DM1_PB_DF_SR | BXX_SLP1_DM1 | BXX Pump 1 Not Ready Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_DF.SR | No | BXX Pump 1 Not Ready Sup Enable | 0 | 0
BXX_SLP1_DM1_PB_GA_SR | BXX_SLP1_DM1 | BXX Pump 1 Soft Starter Fault Sup Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_GA.SR | No | BXX Pump 1 Soft Starter Fault Sup Enable | 0 | 0
BXX_SLP1_DM1_PB_TA_SR | BXX_SLP1_DM1 | BXX Pump 1 Temp/Leak Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP1_DM1.DA_TA.SR | No | BXX Pump 1 Temp/Leak Sup Enable | 0 | 0
:MemoryInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinValue | MaxValue | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
PMP_VIS1 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS2 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS3 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS4 | $System | Pump Speed Setpoint Visiblity Control |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Speed Setpoint Visiblity Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP1_DM1_AI_RT | BXX_SLP1_DM1 | BXX Pump 1 Runtime (Hours) | 26 | Yes | No | 0 | Yes | No | 0 | 0 | h | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_SLP1_DM1.AI_RT | No | BXX Pump 1 Runtime (Hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_SLP1_DM1_DI_NM | BXX_SLP1_DM1 | BXX_SLP1_DM1 | 12 | No | No | 0 | Yes | 24 | BXX_SLP1_DM1 | BXX_SLP1_DM1
PMP_NAME | $System | Pump Name - Indirect |  | No | No | 0 | Yes | 131
PMP_SI_NAME | $System | Pump Feedback Tagname |  | No | No | 0 | Yes | 131
PMP_SK_NAME | $System | Stroke Feedback Tagname |  | No | No | 0 | Yes | 131
ALRM_PGRP | $System | Pump Alarm Query |  | No | No | 0 | Yes | 64 |  | Pump Alarm Query
:IOMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_SLP1_DM1_PB_AE_RN | BXX_SLP1_DM1 | BXX Pump 1 Alarms Disabled Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP1_DM1_PB_AE_RN | No | BXX Pump 1 Alarms Disabled Reason
BXX_SLP1_DM1_PB_ES_SR | BXX_SLP1_DM1 | BXX Pump 1 E-Stop Disabled Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP1_DM1_PB_ES_SR | No | BXX Pump 1 E-Stop Disabled Reason
BXX_SLP1_DM1_PB_RA_SR | BXX_SLP1_DM1 | BXX Pump 1 Overload Disabled Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP1_DM1_PB_RA_SR | No | BXX Pump 1 Overload Disabled Reason
BXX_SLP1_DM1_PB_DF_SR | BXX_SLP1_DM1 | BXX Pump 1 Not Ready Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP1_DM1_PB_DF_SR | No | BXX Pump 1 Not Ready Disabled Reason
BXX_SLP1_DM1_PB_GA_SR | BXX_SLP1_DM1 | BXX Pump 1 Soft Starter Fault Disabled Reason | 45 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP1_DM1_PB_GA_SR | No | BXX Pump 1 Soft Starter Fault Disabled Reason
BXX_SLP1_DM1_PB_TA_SR | BXX_SLP1_DM1 | BXX Pump 1 Temp/Leak Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP1_DM1_PB_TA_SR | No | BXX Pump 1 Temp/Leak Disabled Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DI_SC | $System | Pump Feedback On Scan Indirect Tag | 34 | No | 0 | No
PMP_DM_DI_AA | $System | Pump Plant Auto Mode Status - Indirect | 38 | No | 0 | No
PMP_DM_DI_AS | $System | Pump Plant Auto Stroke Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_CL | $System | Pump Control Mode - Indirect | 28 | No | 0 | No
PMP_DM_DI_MS | $System | Pump Plant Manual Stroke Status - Indirect | 42 | No | 0 | No
PMP_DM_DI_PM | $System | Pump Plant Manual Mode Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_SK | $System | Pump Stroke Control Mode - Indirect | 35 | No | 0 | No
PMP_DM_DI_SS | $System | Pump Running Status - Indirect | 30 | No | 0 | No
PMP_DM_PB_AR | $System | Pump Alarm Ack. Req. - Indirect | 31 | No | 0 | No
PMP_DM_PB_MS | $System | Pump Plant Manual Stroke Req. - Indirect | 40 | No | 0 | No
PMP_DM_PB_PM | $System | Pump Plant Manual Mode Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PP | $System | Pump Plant Manual Stop Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PT | $System | Pump Plant Manual Start Req. - Indirect | 39 | No | 0 | No
PMP_DM_PB_RT | $System | Pump Runtime Reset - Indirect | 29 | No | 0 | No
PMP_PB_AE | $System | Pump Alarm Enable Pushbutton Indirect Tag | 41 | No | 0 | No
PMP_PB_ER | $System | Pump Speed Signal Error Enable Indirect Tag | 43 | No | 0 | No
PMP_PB_SC | $System | Pump Speed Feedback Scan Enable Indirect Tag | 44 | No | 0 | No
PMP_PB_SF | $System | Pump Fail To Start Enable Ind. Tag | 34 | No | 0 | No
PMP_PB_SM | $System | Pump Simulate Alarms Pushbutton Indirect Tag | 44 | No | 0 | No
PMP_PB_SU | $System | Pump Fail To Stop Enable Ind. Tag | 33 | No | 0 | No
PMP_PB_SV | $System | Pump Simulate Feedback Indirect Tag | 35 | No | 0 | No
PMP_PB_XF | $System | Pump Uncommanded Start Enable Ind. Tag | 38 | No | 0 | No
PMP_PB_XU | $System | Pump Uncommanded Stop Enable Ind. Tag | 37 | No | 0 | No
PMP_PB_ZA | $System | Pump Deviation Alarm Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_DA_ER | $System | Stroke Feedback Signal Error Indirect Tag | 41 | No | 0 | No
PMP_SK_DI_SC | $System | Stroke Feedback on Scan Indirect Tag | 36 | No | 0 | No
PMP_SK_PB_ER | $System | Stroke Feedback Signal Error Enable Indirect Tag | 48 | No | 0 | No
PMP_SK_PB_SC | $System | Stroke Feedback Scan Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_PB_SV | $System | Stroke Feedback Simulate Value Indirect Tag | 43 | No | 0 | No
PMP_SK_PB_ZA | $System | Stroke Feedback Deviation Alarm Enable Ind. Tag | 47 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DC2 | $System | Pump Signal Engineering Units 2 - Indirect | 42 | No | 0 | No
PMP_DC3 | $System | Pump Signal Engineering Units 3 - Indirect | 42 | No | 0 | No
PMP_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_AI_CV | $System | Pump Signal Feedback Indirect Tag | 33 | No | 0 | No
PMP_AI_VI | $System | Pump Signal Feedback Visible Values Ind. Tag | 44 | No | 0 | No
PMP_AO_SV | $System | Pump Feedback Override Value Indirect Tag | 41 | No | 0 | No
PMP_AO_ZA | $System | Deviation Alarm Setpoint Indirect Tag | 37 | No | 0 | No
PMP_DM_AI_RT | $System | Pump Runtime - Indirect | 23 | No | 0 | No
PMP_E1_EM | $System | Pump Feedback Zero Indirect Tag | 31 | No | 0 | No
PMP_E1_XM | $System | Pump Feedback Span Indirect Tag | 31 | No | 0 | No
PMP_E2_CV | $System | Pump Feedback Secondary Eng Value Ind. Tag | 42 | No | 0 | No
PMP_E3_CV | $System | Pump Feedback Tertiary Eng Value Indirect Tag | 45 | No | 0 | No
PMP_SI_AO_CT | $System | VFD Pump Manual Speed Setpoint - Indirect Analog | 48 | No | 0 | No
PMP_SK_DC2 | $System | Pump Stroke Signal Engineering Units 2 - Indirect | 49 | No | 0 | No
PMP_SK_DC3 | $System | Pump Stroke Signal Engineering Units 3 - Indirect | 49 | No | 0 | No
PMP_SK_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_SK_AI_CV | $System | Stroke Feedback Indirect Tag | 28 | No | 0 | No
PMP_SK_AI_VI | $System | Stroke Feedback Number of Visible Units Ind. Tag | 48 | No | 0 | No
PMP_SK_AO_CT | $System | VFD Pump Stroke Setpoint - Indirect Analog | 42 | No | 0 | No
PMP_SK_AO_SV | $System | Stroke Feedback Simulation Value Indirect Tag | 45 | No | 0 | No
PMP_SK_AO_ZA | $System | Stroke Deviation Setpoint Indirect Tag | 38 | No | 0 | No
PMP_SK_E1_EM | $System | Stroke Feedback Zero Scale Indirect Tag | 39 | No | 0 | No
PMP_SK_E1_XM | $System | Stroke Feedback Spane Indirect Tag | 34 | No | 0 | No
PMP_SK_E2_CV | $System | Stroke Feedback Secondary Units Indirect Tag | 44 | No | 0 | No
PMP_SK_E3_CV | $System | Stroke Feedback Tertiary Units Indirect Tag | 43 | No | 0 | No
PMP_SK_SN_ZA | $System | Stroke Deviation Alarm Delay Indirect Tag | 41 | No | 0 | No
PMP_SN_ZA | $System | Deviation Alarm Delay Time Indirect Tag | 39 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_SRV | $System | Pump Alarm Group Server Indirect Tag | 36 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
PMP_DM_GRP | $System | Pump Group - Indirect | 21

## BXXSLP2VF1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_SLP2_VF1 | BXX | BXX Pump 2 | 10 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1 | BXX_SLP2_VF1 | BXX Pump 2 Speed | 16 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:Memory_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_SLP2_VF1_DI_AD | BXX_DSAB | BXX Pump 2 Disabled Alarm | 25 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_SLP2_VF1.DI_AD | No | BXX Pump 2 Disabled Alarm | 0 | 0
BXX_SLP2_VF1_DI_CL | BXX_SLP2_VF1 | BXX Pump 2 Control Mode | 23 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DI_CL.eng | No | BXX Pump 2 Control Mode | 0 | 0
BXX_SLP2_VF1_DI_SS | BXX_SLP2_VF1 | BXX Pump 2 Running Status | 25 | Yes | Yes | 700 | Yes | Off | Stopped | Running | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DI_SS.eng | No | BXX Pump 2 Running Status | 0 | 0
BXX_SLP2_VF1_DA_ES | BXX_SLP2_VF1 | BXX Pump 2 E-Stop | 17 | No | No | 0 | Yes | Off | Normal | Alarm | On | 50 | Direct | BXX | No | BXX_SLP2_VF1.DA_ES.eng | No | BXX Pump 2 E-Stop | 0 | 0
BXX_SLP2_VF1_DA_RA | BXX_SLP2_VF1 | BXX Pump 2 Overload | 19 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_SLP2_VF1.DA_RA.eng | No | BXX Pump 2 Overload | 0 | 0
BXX_SLP2_VF1_DA_DF | BXX_SLP2_VF1 | BXX Pump 2 Not Ready | 20 | No | No | 0 | Yes | Off | Normal | Not Ready | On | 55 | Direct | BXX | No | BXX_SLP2_VF1.DA_DF.eng | No | BXX Pump 2 Not Ready | 0 | 0
BXX_SLP2_VF1_DA_GA | BXX_SLP2_VF1 | BXX Pump 2 VFD Fault | 20 | No | No | 0 | Yes | Off | Normal | Alarm | On | 55 | Direct | BXX | No | BXX_SLP2_VF1.DA_GA.eng | No | BXX Pump 2 VFD Fault | 0 | 0
BXX_SLP2_VF1_DA_TA | BXX_SLP2_VF1 | BXX Pump 2 Temp/Leak Alarm | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 58 | Direct | BXX | No | BXX_SLP2_VF1.DA_TA.eng | No | BXX Pump 2 Temp/Leak Alarm | 0 | 0
BXX_SLP2_VF1_DI_AA | BXX_SLP2_VF1 | BXX Pump 2 Auto Mode | 20 | No | Yes | 700 | Yes | Off | PLT-MAN | AUTO | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DI_AA | No | BXX Pump 2 Auto Mode | 0 | 0
BXX_SLP2_VF1_DI_PM | BXX_SLP2_VF1 | BXX Pump 2 Plant Manual Mode | 28 | No | Yes | 700 | Yes | Off | AUTO | PLT-MAN | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DI_PM | No | BXX Pump 2 Plant Manual Mode | 0 | 0
BXX_SLP2_VF1_PB_PM | BXX_SLP2_VF1 | BXX Pump 2 Plant Manual Mode RQ | 31 | No | Yes | 600 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_PM | No | BXX Pump 2 Plant Manual Mode RQ | 0 | 0
BXX_SLP2_VF1_PB_PT | BXX_SLP2_VF1 | BXX Pump 2 Plant Manual Start | 29 | No | Yes | 600 | Yes | Off | Normal | Start | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_PT | No | BXX Pump 2 Plant Manual Start | 0 | 0
BXX_SLP2_VF1_PB_PP | BXX_SLP2_VF1 | BXX Pump 2 Plant Manual Stop | 28 | No | Yes | 600 | Yes | Off | Normal | Stop | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_PP | No | BXX Pump 2 Plant Manual Stop | 0 | 0
BXX_SLP2_VF1_PB_AR | BXX_SLP2_VF1 | BXX Pump 2 Alarm Ack | 20 | No | Yes | 600 | Yes | Off | Normal | Ack | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_AR | No | BXX Pump 2 Alarm Ack | 0 | 0
BXX_SLP2_VF1_PB_RT | BXX_SLP2_VF1 | BXX Pump 2 Runtime Reset | 24 | No | Yes | 600 | Yes | Off | Normal | Reset | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_RT | No | BXX Pump 2 Runtime Reset | 0 | 0
BXX_SLP2_VF1_DA_SF | BXX_SLP2_VF1 | BXX Pump 2 Failed To Start | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_SLP2_VF1.DA_SF | No | BXX Pump 2 Failed To Start | 0 | 0
BXX_SLP2_VF1_DA_XF | BXX_SLP2_VF1 | BXX Pump 2 Failed To Stop | 25 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_SLP2_VF1.DA_XF | No | BXX Pump 2 Failed To Stop | 0 | 0
BXX_SLP2_VF1_DA_SU | BXX_SLP2_VF1 | BXX Pump 2 Uncommanded Start | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 53 | Direct | BXX | No | BXX_SLP2_VF1.DA_SU | No | BXX Pump 2 Uncommanded Start | 0 | 0
BXX_SLP2_VF1_DA_XU | BXX_SLP2_VF1 | BXX Pump 2 Uncommanded Stop | 27 | No | No | 0 | Yes | Off | Normal | Alarm | On | 54 | Direct | BXX | No | BXX_SLP2_VF1.DA_XU | No | BXX Pump 2 Uncommanded Stop | 0 | 0
BXX_SLP2_VF1_DI_BP | BXX_SLP2_VF1 | BXX Pump 2 Bypass Mode | 22 | No | Yes | 700 | Yes | Off | Normal | Bypass | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DI_BP.eng | No | BXX Pump 2 Bypass Mode | 0 | 0
BXX_SLP2_VF1_DI_ST | BXX_SLP2_VF1 | BXX Pump 2 Hardwired Start | 26 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DI_ST.eng | No | BXX Pump 2 Hardwired Start | 0 | 0
BXX_SLP2_VF1_DI_SP | BXX_SLP2_VF1 | BXX Pump 2 Hardwired Stop | 25 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DI_SP.eng | No | BXX Pump 2 Hardwired Stop | 0 | 0
BXX_SLP2_VF1_PB_SU | BXX_SLP2_VF1 | BXX Pump 2 Uncomm Start Alarm En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_SU.RE | No | BXX Pump 2 Uncomm Start Alarm En | 0 | 0
BXX_SLP2_VF1_PB_SF | BXX_SLP2_VF1 | BXX Pump 2 Failed To Start Alarm En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_SF.RE | No | BXX Pump 2 Failed To Start Alarm En | 0 | 0
BXX_SLP2_VF1_PB_XF | BXX_SLP2_VF1 | BXX Pump 2 Failed To Stop Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_XF.RE | No | BXX Pump 2 Failed To Stop Alarm En | 0 | 0
BXX_SLP2_VF1_PB_XU | BXX_SLP2_VF1 | BXX Pump 2 Uncomm. Stop Alarm En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_XU.RE | No | BXX Pump 2 Uncomm. Stop Alarm En | 0 | 0
BXX_SLP2_VF1_PB_SM | BXX_SLP2_VF1 | BXX Pump 2 Simulate Alarms PB | 29 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_SM | No | BXX Pump 2 Simulate Alarms PB | 0 | 0
BXX_SLP2_VF1_PB_AE | BXX_SLP2_VF1 | BXX Pump 2 Alarm Enable | 23 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_AE.RE | No | BXX Pump 2 Alarm Enable | 0 | 0
BXX_SLP2_VF1_PB_AE_DE | BXX_SLP2_VF1 | BXX Pump 2 Alarms Dialer Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_AE.DE | No | BXX Pump 2 Alarms Dialer Enable | 0 | 0
BXX_SLP2_VF1_PB_AE_SR | BXX_SLP2_VF1 | BXX Pump 2 Alarms Sup Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.PB_AE.SR | No | BXX Pump 2 Alarms Sup Enable | 0 | 0
BXX_DEV1_SI1_DI_SC | BXX_DEV1_SI1 | BXX Pump 2 Speed Scan Status | 28 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.DI_SC | No | BXX Pump 2 Speed Scan Status | 0 | 0
BXX_DEV1_SI1_PB_SC | BXX_DEV1_SI1 | BXX Pump 2 Speed Scan Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_SC | No | BXX Pump 2 Speed Scan Enable | 0 | 0
BXX_DEV1_SI1_DA_ER | BXX_DEV1_SI1 | BXX Pump 2 Speed Signal Error | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DEV1_SI1.DA_ER | No | BXX Pump 2 Speed Signal Error | 0 | 0
BXX_DEV1_SI1_PB_ER | BXX_DEV1_SI1 | BXX Pump 2 Speed Sig Error Alarm En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_ER.RE | No | BXX Pump 2 Speed Sig Error Alarm En | 0 | 0
BXX_DEV1_SI1_PB_SV | BXX_DEV1_SI1 | BXX Pump 2 Speed Override Enable | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_SV | No | BXX Pump 2 Speed Override Enable | 0 | 0
BXX_DEV1_SI1_DA_ZA | BXX_DEV1_SI1 | BXX Pump 2 Speed Deviation Alarm | 32 | No | No | 0 | Yes | Off | Ok | Alarm | On | 330 | Direct | BXX | No | BXX_DEV1_SI1.DA_ZA | No | BXX Pump 2 Speed Deviation Alarm | 0 | 0
BXX_DEV1_SI1_PB_ZA | BXX_DEV1_SI1 | BXX Pump 2 Speed Deviation Alarm En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_ZA.RE | No | BXX Pump 2 Speed Deviation Alarm En | 0 | 0
BXX_SLP2_VF1_PB_ES_RE | BXX_SLP2_VF1 | BXX Pump 2 E-Stop Enable | 24 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_ES.RE | No | BXX Pump 2 E-Stop Enable | 0 | 0
BXX_SLP2_VF1_PB_RA_RE | BXX_SLP2_VF1 | BXX Pump 2 Overload Enable | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_RA.RE | No | BXX Pump 2 Overload Enable | 0 | 0
BXX_SLP2_VF1_PB_DF_RE | BXX_SLP2_VF1 | BXX Pump 2 Not Ready Enable | 27 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_DF.RE | No | BXX Pump 2 Not Ready Enable | 0 | 0
BXX_SLP2_VF1_PB_GA_RE | BXX_SLP2_VF1 | BXX Pump 2 VFD Fault Enable | 27 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_GA.RE | No | BXX Pump 2 VFD Fault Enable | 0 | 0
BXX_SLP2_VF1_PB_TA_RE | BXX_SLP2_VF1 | BXX Pump 2 Temp/Leak Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_TA.RE | No | BXX Pump 2 Temp/Leak Alarm Enable | 0 | 0
BXX_SLP2_VF1_PB_ES_DE | BXX_SLP2_VF1 | BXX Pump 2 E-Stop Dialer Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_ES.DE | No | BXX Pump 2 E-Stop Dialer Enable | 0 | 0
BXX_SLP2_VF1_PB_RA_DE | BXX_SLP2_VF1 | BXX Pump 2 Overload Dialer Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_RA.DE | No | BXX Pump 2 Overload Dialer Enable | 0 | 0
BXX_SLP2_VF1_PB_DF_DE | BXX_SLP2_VF1 | BXX Pump 2 Not Ready Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_DF.DE | No | BXX Pump 2 Not Ready Dialer Enable | 0 | 0
BXX_SLP2_VF1_PB_GA_DE | BXX_SLP2_VF1 | BXX Pump 2 VFD Fault Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_GA.DE | No | BXX Pump 2 VFD Fault Dialer Enable | 0 | 0
BXX_SLP2_VF1_PB_TA_DE | BXX_SLP2_VF1 | BXX Pump 2 Temp/Leak Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_TA.DE | No | BXX Pump 2 Temp/Leak Dialer Enable | 0 | 0
BXX_SLP2_VF1_PB_ES_SR | BXX_SLP2_VF1 | BXX Pump 2 E-Stop Sup Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_ES.SR | No | BXX Pump 2 E-Stop Sup Enable | 0 | 0
BXX_SLP2_VF1_PB_RA_SR | BXX_SLP2_VF1 | BXX Pump 2 Overload Sup Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_RA.SR | No | BXX Pump 2 Overload Sup Enable | 0 | 0
BXX_SLP2_VF1_PB_DF_SR | BXX_SLP2_VF1 | BXX Pump 2 Not Ready Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_DF.SR | No | BXX Pump 2 Not Ready Sup Enable | 0 | 0
BXX_SLP2_VF1_PB_GA_SR | BXX_SLP2_VF1 | BXX Pump 2 VFD Fault Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_GA.SR | No | BXX Pump 2 VFD Fault Sup Enable | 0 | 0
BXX_SLP2_VF1_PB_TA_SR | BXX_SLP2_VF1 | BXX Pump 2 Temp/Leak Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP2_VF1.DA_TA.SR | No | BXX Pump 2 Temp/Leak Sup Enable | 0 | 0
:MemoryInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinValue | MaxValue | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
PMP_VIS1 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS2 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS3 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS4 | $System | Pump Speed Setpoint Visiblity Control |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Speed Setpoint Visiblity Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DEV1_SI1_AI_VI | BXX_DEV1_SI1 | BXX Pump 2 Speed Number of Visible Eng Values | 45 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_DEV1_SI1.AI_VI | No | BXX Pump 2 Speed Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_DC | BXX_DEV1_SI1 | BXX Pump 2 Speed Precision | 26 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_SI1.AI_DC | No | BXX Pump 2 Speed Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP2_VF1_AI_RT | BXX_SLP2_VF1 | BXX Pump 2 Runtime (Hours) | 26 | Yes | No | 0 | Yes | No | 0 | 0 | h | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_SLP2_VF1.AI_RT | No | BXX Pump 2 Runtime (Hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_VF1_SI_CT | BXX_SLP2_VF1 | BXX Pump 2 Manual Speed Setpoint | 32 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_SLP2_VF1.SI_CT | No | BXX Pump 2 Manual Speed Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP2_VF1_AO_CV | BXX_SLP2_VF1 | BXX Pump 2 Speed Command | 24 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_SLP2_VF1.AO_CT | No | BXX Pump 2 Speed Command | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_CV | BXX_DEV1_SI1 | BXX Pump 2 Speed Current Value | 30 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AI_CV | No | BXX Pump 2 Speed Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_XM | BXX_DEV1_SI1 | BXX Pump 2 Speed Span Setpoint | 30 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_XM | No | BXX Pump 2 Speed Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_EM | BXX_DEV1_SI1 | BXX Pump 2 Speed Zero Setpoint | 30 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_EM | No | BXX Pump 2 Speed Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_SV | BXX_DEV1_SI1 | BXX Pump 2 Speed Override Value | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_SV | No | BXX Pump 2 Speed Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_SN_ZA | BXX_DEV1_SI1 | BXX Pump 2 Speed Deviation Alarm Delay | 38 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DEV1_SI1.SN_LO | No | BXX Pump 2 Speed Deviation Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_ZA | BXX_DEV1_SI1 | BXX Pump 2 Speed Deviation Setpoint | 35 | No | Yes | 900 | Yes | No | 0 | 0 | None | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_LL | No | BXX Pump 2 Speed Deviation Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_SLP2_VF1_DI_NM | BXX_SLP2_VF1 | BXX_SLP2_VF1 | 12 | No | No | 0 | Yes | 24 | BXX_SLP2_VF1 | BXX_SLP2_VF1
BXX_DEV1_SI1_DI_NM | BXX_DEV1_SI1 | BXX_DEV1_SI1 | 12 | No | No | 0 | Yes | 24 | BXX_DEV1_SI1 | BXX_DEV1_SI1
PMP_NAME | $System | Pump Name - Indirect |  | No | No | 0 | Yes | 131
PMP_SI_NAME | $System | Pump Feedback Tagname |  | No | No | 0 | Yes | 131
PMP_SK_NAME | $System | Stroke Feedback Tagname |  | No | No | 0 | Yes | 131
ALRM_PGRP | $System | Pump Alarm Query |  | No | No | 0 | Yes | 64 |  | Pump Alarm Query
:IOMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_SLP2_VF1_PB_AE_RN | BXX_SLP2_VF1 | BXX Pump 2 Alarms Disabled Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP2_VF1_PB_AE_RN | No | BXX Pump 2 Alarms Disabled Reason
BXX_SLP2_VF1_PB_ES_SR | BXX_SLP2_VF1 | BXX Pump 2 E-Stop Disabled Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP2_VF1_PB_ES_SR | No | BXX Pump 2 E-Stop Disabled Reason
BXX_SLP2_VF1_PB_RA_SR | BXX_SLP2_VF1 | BXX Pump 2 Overload Disabled Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP2_VF1_PB_RA_SR | No | BXX Pump 2 Overload Disabled Reason
BXX_SLP2_VF1_PB_DF_SR | BXX_SLP2_VF1 | BXX Pump 2 Not Ready Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP2_VF1_PB_DF_SR | No | BXX Pump 2 Not Ready Disabled Reason
BXX_SLP2_VF1_PB_GA_SR | BXX_SLP2_VF1 | BXX Pump 2 VFD Fault Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP2_VF1_PB_GA_SR | No | BXX Pump 2 VFD Fault Disabled Reason
BXX_SLP2_VF1_PB_TA_SR | BXX_SLP2_VF1 | BXX Pump 2 Temp/Leak Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP2_VF1_PB_TA_SR | No | BXX Pump 2 Temp/Leak Disabled Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DI_SC | $System | Pump Feedback On Scan Indirect Tag | 34 | No | 0 | No
PMP_DM_DI_AA | $System | Pump Plant Auto Mode Status - Indirect | 38 | No | 0 | No
PMP_DM_DI_AS | $System | Pump Plant Auto Stroke Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_CL | $System | Pump Control Mode - Indirect | 28 | No | 0 | No
PMP_DM_DI_MS | $System | Pump Plant Manual Stroke Status - Indirect | 42 | No | 0 | No
PMP_DM_DI_PM | $System | Pump Plant Manual Mode Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_SK | $System | Pump Stroke Control Mode - Indirect | 35 | No | 0 | No
PMP_DM_DI_SS | $System | Pump Running Status - Indirect | 30 | No | 0 | No
PMP_DM_PB_AR | $System | Pump Alarm Ack. Req. - Indirect | 31 | No | 0 | No
PMP_DM_PB_MS | $System | Pump Plant Manual Stroke Req. - Indirect | 40 | No | 0 | No
PMP_DM_PB_PM | $System | Pump Plant Manual Mode Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PP | $System | Pump Plant Manual Stop Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PT | $System | Pump Plant Manual Start Req. - Indirect | 39 | No | 0 | No
PMP_DM_PB_RT | $System | Pump Runtime Reset - Indirect | 29 | No | 0 | No
PMP_PB_AE | $System | Pump Alarm Enable Pushbutton Indirect Tag | 41 | No | 0 | No
PMP_PB_ER | $System | Pump Speed Signal Error Enable Indirect Tag | 43 | No | 0 | No
PMP_PB_SC | $System | Pump Speed Feedback Scan Enable Indirect Tag | 44 | No | 0 | No
PMP_PB_SF | $System | Pump Fail To Start Enable Ind. Tag | 34 | No | 0 | No
PMP_PB_SM | $System | Pump Simulate Alarms Pushbutton Indirect Tag | 44 | No | 0 | No
PMP_PB_SU | $System | Pump Fail To Stop Enable Ind. Tag | 33 | No | 0 | No
PMP_PB_SV | $System | Pump Simulate Feedback Indirect Tag | 35 | No | 0 | No
PMP_PB_XF | $System | Pump Uncommanded Start Enable Ind. Tag | 38 | No | 0 | No
PMP_PB_XU | $System | Pump Uncommanded Stop Enable Ind. Tag | 37 | No | 0 | No
PMP_PB_ZA | $System | Pump Deviation Alarm Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_DA_ER | $System | Stroke Feedback Signal Error Indirect Tag | 41 | No | 0 | No
PMP_SK_DI_SC | $System | Stroke Feedback on Scan Indirect Tag | 36 | No | 0 | No
PMP_SK_PB_ER | $System | Stroke Feedback Signal Error Enable Indirect Tag | 48 | No | 0 | No
PMP_SK_PB_SC | $System | Stroke Feedback Scan Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_PB_SV | $System | Stroke Feedback Simulate Value Indirect Tag | 43 | No | 0 | No
PMP_SK_PB_ZA | $System | Stroke Feedback Deviation Alarm Enable Ind. Tag | 47 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DC2 | $System | Pump Signal Engineering Units 2 - Indirect | 42 | No | 0 | No
PMP_DC3 | $System | Pump Signal Engineering Units 3 - Indirect | 42 | No | 0 | No
PMP_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_AI_CV | $System | Pump Signal Feedback Indirect Tag | 33 | No | 0 | No
PMP_AI_VI | $System | Pump Signal Feedback Visible Values Ind. Tag | 44 | No | 0 | No
PMP_AO_SV | $System | Pump Feedback Override Value Indirect Tag | 41 | No | 0 | No
PMP_AO_ZA | $System | Deviation Alarm Setpoint Indirect Tag | 37 | No | 0 | No
PMP_DM_AI_RT | $System | Pump Runtime - Indirect | 23 | No | 0 | No
PMP_E1_EM | $System | Pump Feedback Zero Indirect Tag | 31 | No | 0 | No
PMP_E1_XM | $System | Pump Feedback Span Indirect Tag | 31 | No | 0 | No
PMP_E2_CV | $System | Pump Feedback Secondary Eng Value Ind. Tag | 42 | No | 0 | No
PMP_E3_CV | $System | Pump Feedback Tertiary Eng Value Indirect Tag | 45 | No | 0 | No
PMP_SI_AO_CT | $System | VFD Pump Manual Speed Setpoint - Indirect Analog | 48 | No | 0 | No
PMP_SK_DC2 | $System | Pump Stroke Signal Engineering Units 2 - Indirect | 49 | No | 0 | No
PMP_SK_DC3 | $System | Pump Stroke Signal Engineering Units 3 - Indirect | 49 | No | 0 | No
PMP_SK_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_SK_AI_CV | $System | Stroke Feedback Indirect Tag | 28 | No | 0 | No
PMP_SK_AI_VI | $System | Stroke Feedback Number of Visible Units Ind. Tag | 48 | No | 0 | No
PMP_SK_AO_CT | $System | VFD Pump Stroke Setpoint - Indirect Analog | 42 | No | 0 | No
PMP_SK_AO_SV | $System | Stroke Feedback Simulation Value Indirect Tag | 45 | No | 0 | No
PMP_SK_AO_ZA | $System | Stroke Deviation Setpoint Indirect Tag | 38 | No | 0 | No
PMP_SK_E1_EM | $System | Stroke Feedback Zero Scale Indirect Tag | 39 | No | 0 | No
PMP_SK_E1_XM | $System | Stroke Feedback Spane Indirect Tag | 34 | No | 0 | No
PMP_SK_E2_CV | $System | Stroke Feedback Secondary Units Indirect Tag | 44 | No | 0 | No
PMP_SK_E3_CV | $System | Stroke Feedback Tertiary Units Indirect Tag | 43 | No | 0 | No
PMP_SK_SN_ZA | $System | Stroke Deviation Alarm Delay Indirect Tag | 41 | No | 0 | No
PMP_SN_ZA | $System | Deviation Alarm Delay Time Indirect Tag | 39 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_SRV | $System | Pump Alarm Group Server Indirect Tag | 36 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
PMP_DM_GRP | $System | Pump Group - Indirect | 21

## BXXSLP3DM1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_SLP3_DM1 | BXX | BXX Pump 3 | 10 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:Memory_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_SLP3_DM1_DI_AD | BXX_DSAB | BXX Pump 3 Disabled Alarm | 25 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_SLP3_DM1.DI_AD | No | BXX Pump 3 Disabled Alarm | 0 | 0
BXX_SLP3_DM1_DI_CL | BXX_SLP3_DM1 | BXX Pump 3 Control Mode | 23 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DI_CL.eng | No | BXX Pump 3 Control Mode | 0 | 0
BXX_SLP3_DM1_DI_SS | BXX_SLP3_DM1 | BXX Pump 3 Running Status | 25 | Yes | Yes | 700 | Yes | Off | Stopped | Running | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DI_SS.eng | No | BXX Pump 3 Running Status | 0 | 0
BXX_SLP3_DM1_DA_ES | BXX_SLP3_DM1 | BXX Pump 3 E-Stop | 17 | No | No | 0 | Yes | Off | Normal | Alarm | On | 50 | Direct | BXX | No | BXX_SLP3_DM1.DA_ES.eng | No | BXX Pump 3 E-Stop | 0 | 0
BXX_SLP3_DM1_DA_RA | BXX_SLP3_DM1 | BXX Pump 3 Overload | 19 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_SLP3_DM1.DA_RA.eng | No | BXX Pump 3 Overload | 0 | 0
BXX_SLP3_DM1_DA_DF | BXX_SLP3_DM1 | BXX Pump 3 Not Ready | 20 | No | No | 0 | Yes | Off | Normal | Not Ready | On | 55 | Direct | BXX | No | BXX_SLP3_DM1.DA_DF.eng | No | BXX Pump 3 Not Ready | 0 | 0
BXX_SLP3_DM1_DA_GA | BXX_SLP3_DM1 | BXX Pump 3 Soft Starter Fault | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 55 | Direct | BXX | No | BXX_SLP3_DM1.DA_GA.eng | No | BXX Pump 3 Soft Starter Fault | 0 | 0
BXX_SLP3_DM1_DA_TA | BXX_SLP3_DM1 | BXX Pump 3 Temp/Leak Alarm | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 58 | Direct | BXX | No | BXX_SLP3_DM1.DA_TA.eng | No | BXX Pump 3 Temp/Leak Alarm | 0 | 0
BXX_SLP3_DM1_DI_AA | BXX_SLP3_DM1 | BXX Pump 3 Auto Mode | 20 | No | Yes | 700 | Yes | Off | PLT-MAN | AUTO | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DI_AA | No | BXX Pump 3 Auto Mode | 0 | 0
BXX_SLP3_DM1_DI_PM | BXX_SLP3_DM1 | BXX Pump 3 Plant Manual Mode | 28 | No | Yes | 700 | Yes | Off | AUTO | PLT-MAN | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DI_PM | No | BXX Pump 3 Plant Manual Mode | 0 | 0
BXX_SLP3_DM1_PB_PM | BXX_SLP3_DM1 | BXX Pump 3 Plant Manual Mode RQ | 31 | No | Yes | 600 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_PM | No | BXX Pump 3 Plant Manual Mode RQ | 0 | 0
BXX_SLP3_DM1_PB_PT | BXX_SLP3_DM1 | BXX Pump 3 Plant Manual Start | 29 | No | Yes | 600 | Yes | Off | Normal | Start | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_PT | No | BXX Pump 3 Plant Manual Start | 0 | 0
BXX_SLP3_DM1_PB_PP | BXX_SLP3_DM1 | BXX Pump 3 Plant Manual Stop | 28 | No | Yes | 600 | Yes | Off | Normal | Stop | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_PP | No | BXX Pump 3 Plant Manual Stop | 0 | 0
BXX_SLP3_DM1_PB_AR | BXX_SLP3_DM1 | BXX Pump 3 Alarm Ack | 20 | No | Yes | 600 | Yes | Off | Normal | Ack | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_AR | No | BXX Pump 3 Alarm Ack | 0 | 0
BXX_SLP3_DM1_PB_RT | BXX_SLP3_DM1 | BXX Pump 3 Runtime Reset | 24 | No | Yes | 600 | Yes | Off | Normal | Reset | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_RT | No | BXX Pump 3 Runtime Reset | 0 | 0
BXX_SLP3_DM1_DA_SF | BXX_SLP3_DM1 | BXX Pump 3 Failed To Start | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_SLP3_DM1.DA_SF | No | BXX Pump 3 Failed To Start | 0 | 0
BXX_SLP3_DM1_DA_XF | BXX_SLP3_DM1 | BXX Pump 3 Failed To Stop | 25 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_SLP3_DM1.DA_XF | No | BXX Pump 3 Failed To Stop | 0 | 0
BXX_SLP3_DM1_DA_SU | BXX_SLP3_DM1 | BXX Pump 3 Uncommanded Start | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 53 | Direct | BXX | No | BXX_SLP3_DM1.DA_SU | No | BXX Pump 3 Uncommanded Start | 0 | 0
BXX_SLP3_DM1_DA_XU | BXX_SLP3_DM1 | BXX Pump 3 Uncommanded Stop | 27 | No | No | 0 | Yes | Off | Normal | Alarm | On | 54 | Direct | BXX | No | BXX_SLP3_DM1.DA_XU | No | BXX Pump 3 Uncommanded Stop | 0 | 0
BXX_SLP3_DM1_DI_BP | BXX_SLP3_DM1 | BXX Pump 3 Bypass Mode | 22 | No | Yes | 700 | Yes | Off | Normal | Bypass | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DI_BP.eng | No | BXX Pump 3 Bypass Mode | 0 | 0
BXX_SLP3_DM1_DI_ST | BXX_SLP3_DM1 | BXX Pump 3 Hardwired Start | 26 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DI_ST.eng | No | BXX Pump 3 Hardwired Start | 0 | 0
BXX_SLP3_DM1_DI_SP | BXX_SLP3_DM1 | BXX Pump 3 Hardwired Stop | 25 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DI_SP.eng | No | BXX Pump 3 Hardwired Stop | 0 | 0
BXX_SLP3_DM1_PB_SU | BXX_SLP3_DM1 | BXX Pump 3 Uncomm Start Alarm En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_SU.RE | No | BXX Pump 3 Uncomm Start Alarm En | 0 | 0
BXX_SLP3_DM1_PB_SF | BXX_SLP3_DM1 | BXX Pump 3 Failed To Start Alarm En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_SF.RE | No | BXX Pump 3 Failed To Start Alarm En | 0 | 0
BXX_SLP3_DM1_PB_XF | BXX_SLP3_DM1 | BXX Pump 3 Failed To Stop Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_XF.RE | No | BXX Pump 3 Failed To Stop Alarm En | 0 | 0
BXX_SLP3_DM1_PB_XU | BXX_SLP3_DM1 | BXX Pump 3 Uncomm. Stop Alarm En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_XU.RE | No | BXX Pump 3 Uncomm. Stop Alarm En | 0 | 0
BXX_SLP3_DM1_PB_SM | BXX_SLP3_DM1 | BXX Pump 3 Simulate Alarms PB | 29 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_SM | No | BXX Pump 3 Simulate Alarms PB | 0 | 0
BXX_SLP3_DM1_PB_AE | BXX_SLP3_DM1 | BXX Pump 3 Alarm Enable | 23 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_AE.RE | No | BXX Pump 3 Alarm Enable | 0 | 0
BXX_SLP3_DM1_PB_AE_DE | BXX_SLP3_DM1 | BXX Pump 3 Alarms Dialer Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_AE.DE | No | BXX Pump 3 Alarms Dialer Enable | 0 | 0
BXX_SLP3_DM1_PB_AE_SR | BXX_SLP3_DM1 | BXX Pump 3 Alarms Sup Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.PB_AE.SR | No | BXX Pump 3 Alarms Sup Enable | 0 | 0
BXX_SLP3_DM1_PB_ES_RE | BXX_SLP3_DM1 | BXX Pump 3 E-Stop Enable | 24 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_ES.RE | No | BXX Pump 3 E-Stop Enable | 0 | 0
BXX_SLP3_DM1_PB_RA_RE | BXX_SLP3_DM1 | BXX Pump 3 Overload Enable | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_RA.RE | No | BXX Pump 3 Overload Enable | 0 | 0
BXX_SLP3_DM1_PB_DF_RE | BXX_SLP3_DM1 | BXX Pump 3 Not Ready Enable | 27 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_DF.RE | No | BXX Pump 3 Not Ready Enable | 0 | 0
BXX_SLP3_DM1_PB_GA_RE | BXX_SLP3_DM1 | BXX Pump 3 Soft Starter Fault Enable | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_GA.RE | No | BXX Pump 3 Soft Starter Fault Enable | 0 | 0
BXX_SLP3_DM1_PB_TA_RE | BXX_SLP3_DM1 | BXX Pump 3 Temp/Leak Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_TA.RE | No | BXX Pump 3 Temp/Leak Alarm Enable | 0 | 0
BXX_SLP3_DM1_PB_ES_DE | BXX_SLP3_DM1 | BXX Pump 3 E-Stop Dialer Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_ES.DE | No | BXX Pump 3 E-Stop Dialer Enable | 0 | 0
BXX_SLP3_DM1_PB_RA_DE | BXX_SLP3_DM1 | BXX Pump 3 Overload Dialer Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_RA.DE | No | BXX Pump 3 Overload Dialer Enable | 0 | 0
BXX_SLP3_DM1_PB_DF_DE | BXX_SLP3_DM1 | BXX Pump 3 Not Ready Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_DF.DE | No | BXX Pump 3 Not Ready Dialer Enable | 0 | 0
BXX_SLP3_DM1_PB_MA_DE | BXX_SLP3_DM1 | BXX Pump 3 Loss of Prime Dialer Enable | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_MA.DE | No | BXX Pump 3 Loss of Prime Dialer Enable | 0 | 0
BXX_SLP3_DM1_PB_GA_DE | BXX_SLP3_DM1 | BXX Pump 3 Soft Starter Fault Dialer Enable | 43 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_GA.DE | No | BXX Pump 3 Soft Starter Fault Dialer Enable | 0 | 0
BXX_SLP3_DM1_PB_TA_DE | BXX_SLP3_DM1 | BXX Pump 3 Temp/Leak Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_TA.DE | No | BXX Pump 3 Temp/Leak Dialer Enable | 0 | 0
BXX_SLP3_DM1_PB_ES_SR | BXX_SLP3_DM1 | BXX Pump 3 E-Stop Sup Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_ES.SR | No | BXX Pump 3 E-Stop Sup Enable | 0 | 0
BXX_SLP3_DM1_PB_RA_SR | BXX_SLP3_DM1 | BXX Pump 3 Overload Sup Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_RA.SR | No | BXX Pump 3 Overload Sup Enable | 0 | 0
BXX_SLP3_DM1_PB_DF_SR | BXX_SLP3_DM1 | BXX Pump 3 Not Ready Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_DF.SR | No | BXX Pump 3 Not Ready Sup Enable | 0 | 0
BXX_SLP3_DM1_PB_GA_SR | BXX_SLP3_DM1 | BXX Pump 3 Soft Starter Fault Sup Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_GA.SR | No | BXX Pump 3 Soft Starter Fault Sup Enable | 0 | 0
BXX_SLP3_DM1_PB_TA_SR | BXX_SLP3_DM1 | BXX Pump 3 Temp/Leak Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP3_DM1.DA_TA.SR | No | BXX Pump 3 Temp/Leak Sup Enable | 0 | 0
:MemoryInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinValue | MaxValue | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
PMP_VIS1 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS2 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS3 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS4 | $System | Pump Speed Setpoint Visiblity Control |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Speed Setpoint Visiblity Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP3_DM1_AI_RT | BXX_SLP3_DM1 | BXX Pump 3 Runtime (Hours) | 26 | Yes | No | 0 | Yes | No | 0 | 0 | h | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_SLP3_DM1.AI_RT | No | BXX Pump 3 Runtime (Hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_SLP3_DM1_DI_NM | BXX_SLP3_DM1 | BXX_SLP3_DM1 | 12 | No | No | 0 | Yes | 24 | BXX_SLP3_DM1 | BXX_SLP3_DM1
PMP_NAME | $System | Pump Name - Indirect |  | No | No | 0 | Yes | 131
PMP_SI_NAME | $System | Pump Feedback Tagname |  | No | No | 0 | Yes | 131
PMP_SK_NAME | $System | Stroke Feedback Tagname |  | No | No | 0 | Yes | 131
ALRM_PGRP | $System | Pump Alarm Query |  | No | No | 0 | Yes | 64 |  | Pump Alarm Query
:IOMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_SLP3_DM1_PB_AE_RN | BXX_SLP3_DM1 | BXX Pump 3 Alarms Disabled Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP3_DM1_PB_AE_RN | No | BXX Pump 3 Alarms Disabled Reason
BXX_SLP3_DM1_PB_ES_SR | BXX_SLP3_DM1 | BXX Pump 3 E-Stop Disabled Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP3_DM1_PB_ES_SR | No | BXX Pump 3 E-Stop Disabled Reason
BXX_SLP3_DM1_PB_RA_SR | BXX_SLP3_DM1 | BXX Pump 3 Overload Disabled Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP3_DM1_PB_RA_SR | No | BXX Pump 3 Overload Disabled Reason
BXX_SLP3_DM1_PB_DF_SR | BXX_SLP3_DM1 | BXX Pump 3 Not Ready Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP3_DM1_PB_DF_SR | No | BXX Pump 3 Not Ready Disabled Reason
BXX_SLP3_DM1_PB_GA_SR | BXX_SLP3_DM1 | BXX Pump 3 Soft Starter Fault Disabled Reason | 45 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP3_DM1_PB_GA_SR | No | BXX Pump 3 Soft Starter Fault Disabled Reason
BXX_SLP3_DM1_PB_TA_SR | BXX_SLP3_DM1 | BXX Pump 3 Temp/Leak Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP3_DM1_PB_TA_SR | No | BXX Pump 3 Temp/Leak Disabled Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DI_SC | $System | Pump Feedback On Scan Indirect Tag | 34 | No | 0 | No
PMP_DM_DI_AA | $System | Pump Plant Auto Mode Status - Indirect | 38 | No | 0 | No
PMP_DM_DI_AS | $System | Pump Plant Auto Stroke Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_CL | $System | Pump Control Mode - Indirect | 28 | No | 0 | No
PMP_DM_DI_MS | $System | Pump Plant Manual Stroke Status - Indirect | 42 | No | 0 | No
PMP_DM_DI_PM | $System | Pump Plant Manual Mode Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_SK | $System | Pump Stroke Control Mode - Indirect | 35 | No | 0 | No
PMP_DM_DI_SS | $System | Pump Running Status - Indirect | 30 | No | 0 | No
PMP_DM_PB_AR | $System | Pump Alarm Ack. Req. - Indirect | 31 | No | 0 | No
PMP_DM_PB_MS | $System | Pump Plant Manual Stroke Req. - Indirect | 40 | No | 0 | No
PMP_DM_PB_PM | $System | Pump Plant Manual Mode Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PP | $System | Pump Plant Manual Stop Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PT | $System | Pump Plant Manual Start Req. - Indirect | 39 | No | 0 | No
PMP_DM_PB_RT | $System | Pump Runtime Reset - Indirect | 29 | No | 0 | No
PMP_PB_AE | $System | Pump Alarm Enable Pushbutton Indirect Tag | 41 | No | 0 | No
PMP_PB_ER | $System | Pump Speed Signal Error Enable Indirect Tag | 43 | No | 0 | No
PMP_PB_SC | $System | Pump Speed Feedback Scan Enable Indirect Tag | 44 | No | 0 | No
PMP_PB_SF | $System | Pump Fail To Start Enable Ind. Tag | 34 | No | 0 | No
PMP_PB_SM | $System | Pump Simulate Alarms Pushbutton Indirect Tag | 44 | No | 0 | No
PMP_PB_SU | $System | Pump Fail To Stop Enable Ind. Tag | 33 | No | 0 | No
PMP_PB_SV | $System | Pump Simulate Feedback Indirect Tag | 35 | No | 0 | No
PMP_PB_XF | $System | Pump Uncommanded Start Enable Ind. Tag | 38 | No | 0 | No
PMP_PB_XU | $System | Pump Uncommanded Stop Enable Ind. Tag | 37 | No | 0 | No
PMP_PB_ZA | $System | Pump Deviation Alarm Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_DA_ER | $System | Stroke Feedback Signal Error Indirect Tag | 41 | No | 0 | No
PMP_SK_DI_SC | $System | Stroke Feedback on Scan Indirect Tag | 36 | No | 0 | No
PMP_SK_PB_ER | $System | Stroke Feedback Signal Error Enable Indirect Tag | 48 | No | 0 | No
PMP_SK_PB_SC | $System | Stroke Feedback Scan Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_PB_SV | $System | Stroke Feedback Simulate Value Indirect Tag | 43 | No | 0 | No
PMP_SK_PB_ZA | $System | Stroke Feedback Deviation Alarm Enable Ind. Tag | 47 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DC2 | $System | Pump Signal Engineering Units 2 - Indirect | 42 | No | 0 | No
PMP_DC3 | $System | Pump Signal Engineering Units 3 - Indirect | 42 | No | 0 | No
PMP_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_AI_CV | $System | Pump Signal Feedback Indirect Tag | 33 | No | 0 | No
PMP_AI_VI | $System | Pump Signal Feedback Visible Values Ind. Tag | 44 | No | 0 | No
PMP_AO_SV | $System | Pump Feedback Override Value Indirect Tag | 41 | No | 0 | No
PMP_AO_ZA | $System | Deviation Alarm Setpoint Indirect Tag | 37 | No | 0 | No
PMP_DM_AI_RT | $System | Pump Runtime - Indirect | 23 | No | 0 | No
PMP_E1_EM | $System | Pump Feedback Zero Indirect Tag | 31 | No | 0 | No
PMP_E1_XM | $System | Pump Feedback Span Indirect Tag | 31 | No | 0 | No
PMP_E2_CV | $System | Pump Feedback Secondary Eng Value Ind. Tag | 42 | No | 0 | No
PMP_E3_CV | $System | Pump Feedback Tertiary Eng Value Indirect Tag | 45 | No | 0 | No
PMP_SI_AO_CT | $System | VFD Pump Manual Speed Setpoint - Indirect Analog | 48 | No | 0 | No
PMP_SK_DC2 | $System | Pump Stroke Signal Engineering Units 2 - Indirect | 49 | No | 0 | No
PMP_SK_DC3 | $System | Pump Stroke Signal Engineering Units 3 - Indirect | 49 | No | 0 | No
PMP_SK_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_SK_AI_CV | $System | Stroke Feedback Indirect Tag | 28 | No | 0 | No
PMP_SK_AI_VI | $System | Stroke Feedback Number of Visible Units Ind. Tag | 48 | No | 0 | No
PMP_SK_AO_CT | $System | VFD Pump Stroke Setpoint - Indirect Analog | 42 | No | 0 | No
PMP_SK_AO_SV | $System | Stroke Feedback Simulation Value Indirect Tag | 45 | No | 0 | No
PMP_SK_AO_ZA | $System | Stroke Deviation Setpoint Indirect Tag | 38 | No | 0 | No
PMP_SK_E1_EM | $System | Stroke Feedback Zero Scale Indirect Tag | 39 | No | 0 | No
PMP_SK_E1_XM | $System | Stroke Feedback Spane Indirect Tag | 34 | No | 0 | No
PMP_SK_E2_CV | $System | Stroke Feedback Secondary Units Indirect Tag | 44 | No | 0 | No
PMP_SK_E3_CV | $System | Stroke Feedback Tertiary Units Indirect Tag | 43 | No | 0 | No
PMP_SK_SN_ZA | $System | Stroke Deviation Alarm Delay Indirect Tag | 41 | No | 0 | No
PMP_SN_ZA | $System | Deviation Alarm Delay Time Indirect Tag | 39 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_SRV | $System | Pump Alarm Group Server Indirect Tag | 36 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
PMP_DM_GRP | $System | Pump Group - Indirect | 21

## BXXSLP4VF1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_SLP4_VF1 | BXX | BXX Pump 4 | 10 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1 | BXX_SLP4_VF1 | BXX Pump 4 Speed | 16 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:Memory_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_SLP4_VF1_DI_AD | BXX_DSAB | BXX Pump 4 Disabled Alarm | 25 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_SLP4_VF1.DI_AD | No | BXX Pump 4 Disabled Alarm | 0 | 0
BXX_SLP4_VF1_DI_CL | BXX_SLP4_VF1 | BXX Pump 4 Control Mode | 23 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DI_CL.eng | No | BXX Pump 4 Control Mode | 0 | 0
BXX_SLP4_VF1_DI_SS | BXX_SLP4_VF1 | BXX Pump 4 Running Status | 25 | Yes | Yes | 700 | Yes | Off | Stopped | Running | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DI_SS.eng | No | BXX Pump 4 Running Status | 0 | 0
BXX_SLP4_VF1_DA_ES | BXX_SLP4_VF1 | BXX Pump 4 E-Stop | 17 | No | No | 0 | Yes | Off | Normal | Alarm | On | 50 | Direct | BXX | No | BXX_SLP4_VF1.DA_ES.eng | No | BXX Pump 4 E-Stop | 0 | 0
BXX_SLP4_VF1_DA_RA | BXX_SLP4_VF1 | BXX Pump 4 Overload | 19 | No | No | 0 | Yes | Off | Normal | Alarm | On | 63 | Direct | BXX | No | BXX_SLP4_VF1.DA_RA.eng | No | BXX Pump 4 Overload | 0 | 0
BXX_SLP4_VF1_DA_DF | BXX_SLP4_VF1 | BXX Pump 4 Not Ready | 20 | No | No | 0 | Yes | Off | Normal | Not Ready | On | 55 | Direct | BXX | No | BXX_SLP4_VF1.DA_DF.eng | No | BXX Pump 4 Not Ready | 0 | 0
BXX_SLP4_VF1_DA_GA | BXX_SLP4_VF1 | BXX Pump 4 VFD Fault | 20 | No | No | 0 | Yes | Off | Normal | Alarm | On | 55 | Direct | BXX | No | BXX_SLP4_VF1.DA_GA.eng | No | BXX Pump 4 VFD Fault | 0 | 0
BXX_SLP4_VF1_DA_TA | BXX_SLP4_VF1 | BXX Pump 4 Temp/Leak Alarm | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 58 | Direct | BXX | No | BXX_SLP4_VF1.DA_TA.eng | No | BXX Pump 4 Temp/Leak Alarm | 0 | 0
BXX_SLP4_VF1_DI_AA | BXX_SLP4_VF1 | BXX Pump 4 Auto Mode | 20 | No | Yes | 700 | Yes | Off | PLT-MAN | AUTO | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DI_AA | No | BXX Pump 4 Auto Mode | 0 | 0
BXX_SLP4_VF1_DI_PM | BXX_SLP4_VF1 | BXX Pump 4 Plant Manual Mode | 28 | No | Yes | 700 | Yes | Off | AUTO | PLT-MAN | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DI_PM | No | BXX Pump 4 Plant Manual Mode | 0 | 0
BXX_SLP4_VF1_PB_PM | BXX_SLP4_VF1 | BXX Pump 4 Plant Manual Mode RQ | 31 | No | Yes | 600 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_PM | No | BXX Pump 4 Plant Manual Mode RQ | 0 | 0
BXX_SLP4_VF1_PB_PT | BXX_SLP4_VF1 | BXX Pump 4 Plant Manual Start | 29 | No | Yes | 600 | Yes | Off | Normal | Start | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_PT | No | BXX Pump 4 Plant Manual Start | 0 | 0
BXX_SLP4_VF1_PB_PP | BXX_SLP4_VF1 | BXX Pump 4 Plant Manual Stop | 28 | No | Yes | 600 | Yes | Off | Normal | Stop | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_PP | No | BXX Pump 4 Plant Manual Stop | 0 | 0
BXX_SLP4_VF1_PB_AR | BXX_SLP4_VF1 | BXX Pump 4 Alarm Ack | 20 | No | Yes | 600 | Yes | Off | Normal | Ack | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_AR | No | BXX Pump 4 Alarm Ack | 0 | 0
BXX_SLP4_VF1_PB_RT | BXX_SLP4_VF1 | BXX Pump 4 Runtime Reset | 24 | No | Yes | 600 | Yes | Off | Normal | Reset | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_RT | No | BXX Pump 4 Runtime Reset | 0 | 0
BXX_SLP4_VF1_DA_SF | BXX_SLP4_VF1 | BXX Pump 4 Failed To Start | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_SLP4_VF1.DA_SF | No | BXX Pump 4 Failed To Start | 0 | 0
BXX_SLP4_VF1_DA_XF | BXX_SLP4_VF1 | BXX Pump 4 Failed To Stop | 25 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_SLP4_VF1.DA_XF | No | BXX Pump 4 Failed To Stop | 0 | 0
BXX_SLP4_VF1_DA_SU | BXX_SLP4_VF1 | BXX Pump 4 Uncommanded Start | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 53 | Direct | BXX | No | BXX_SLP4_VF1.DA_SU | No | BXX Pump 4 Uncommanded Start | 0 | 0
BXX_SLP4_VF1_DA_XU | BXX_SLP4_VF1 | BXX Pump 4 Uncommanded Stop | 27 | No | No | 0 | Yes | Off | Normal | Alarm | On | 54 | Direct | BXX | No | BXX_SLP4_VF1.DA_XU | No | BXX Pump 4 Uncommanded Stop | 0 | 0
BXX_SLP4_VF1_DI_BP | BXX_SLP4_VF1 | BXX Pump 4 Bypass Mode | 22 | No | Yes | 700 | Yes | Off | Normal | Bypass | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DI_BP.eng | No | BXX Pump 4 Bypass Mode | 0 | 0
BXX_SLP4_VF1_DI_ST | BXX_SLP4_VF1 | BXX Pump 4 Hardwired Start | 26 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DI_ST.eng | No | BXX Pump 4 Hardwired Start | 0 | 0
BXX_SLP4_VF1_DI_SP | BXX_SLP4_VF1 | BXX Pump 4 Hardwired Stop | 25 | No | Yes | 700 | Yes | Off | Normal | On | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DI_SP.eng | No | BXX Pump 4 Hardwired Stop | 0 | 0
BXX_SLP4_VF1_PB_SU | BXX_SLP4_VF1 | BXX Pump 4 Uncomm Start Alarm En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_SU.RE | No | BXX Pump 4 Uncomm Start Alarm En | 0 | 0
BXX_SLP4_VF1_PB_SF | BXX_SLP4_VF1 | BXX Pump 4 Failed To Start Alarm En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_SF.RE | No | BXX Pump 4 Failed To Start Alarm En | 0 | 0
BXX_SLP4_VF1_PB_XF | BXX_SLP4_VF1 | BXX Pump 4 Failed To Stop Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_XF.RE | No | BXX Pump 4 Failed To Stop Alarm En | 0 | 0
BXX_SLP4_VF1_PB_XU | BXX_SLP4_VF1 | BXX Pump 4 Uncomm. Stop Alarm En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_XU.RE | No | BXX Pump 4 Uncomm. Stop Alarm En | 0 | 0
BXX_SLP4_VF1_PB_SM | BXX_SLP4_VF1 | BXX Pump 4 Simulate Alarms PB | 29 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_SM | No | BXX Pump 4 Simulate Alarms PB | 0 | 0
BXX_SLP4_VF1_PB_AE | BXX_SLP4_VF1 | BXX Pump 4 Alarm Enable | 23 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_AE.RE | No | BXX Pump 4 Alarm Enable | 0 | 0
BXX_SLP4_VF1_PB_AE_DE | BXX_SLP4_VF1 | BXX Pump 4 Alarms Dialer Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_AE.DE | No | BXX Pump 4 Alarms Dialer Enable | 0 | 0
BXX_SLP4_VF1_PB_AE_SR | BXX_SLP4_VF1 | BXX Pump 4 Alarms Sup Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.PB_AE.SR | No | BXX Pump 4 Alarms Sup Enable | 0 | 0
BXX_DEV1_SI1_DI_SC | BXX_DEV1_SI1 | BXX Pump 4 Speed Scan Status | 28 | No | Yes | 700 | Yes | Off | Disabled | Enabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.DI_SC | No | BXX Pump 4 Speed Scan Status | 0 | 0
BXX_DEV1_SI1_PB_SC | BXX_DEV1_SI1 | BXX Pump 4 Speed Scan Enable | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_SC | No | BXX Pump 4 Speed Scan Enable | 0 | 0
BXX_DEV1_SI1_DA_ER | BXX_DEV1_SI1 | BXX Pump 4 Speed Signal Error | 29 | No | No | 0 | Yes | Off | Ok | Alarm | On | 94 | Direct | BXX | No | BXX_DEV1_SI1.DA_ER | No | BXX Pump 4 Speed Signal Error | 0 | 0
BXX_DEV1_SI1_PB_ER | BXX_DEV1_SI1 | BXX Pump 4 Speed Sig Error Alarm En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_ER.RE | No | BXX Pump 4 Speed Sig Error Alarm En | 0 | 0
BXX_DEV1_SI1_PB_SV | BXX_DEV1_SI1 | BXX Pump 4 Speed Override Enable | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_SV | No | BXX Pump 4 Speed Override Enable | 0 | 0
BXX_DEV1_SI1_DA_ZA | BXX_DEV1_SI1 | BXX Pump 4 Speed Deviation Alarm | 32 | No | No | 0 | Yes | Off | Ok | Alarm | On | 330 | Direct | BXX | No | BXX_DEV1_SI1.DA_ZA | No | BXX Pump 4 Speed Deviation Alarm | 0 | 0
BXX_DEV1_SI1_PB_ZA | BXX_DEV1_SI1 | BXX Pump 4 Speed Deviation Alarm En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_DEV1_SI1.PB_ZA.RE | No | BXX Pump 4 Speed Deviation Alarm En | 0 | 0
BXX_SLP4_VF1_PB_ES_RE | BXX_SLP4_VF1 | BXX Pump 4 E-Stop Enable | 24 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_ES.RE | No | BXX Pump 4 E-Stop Enable | 0 | 0
BXX_SLP4_VF1_PB_RA_RE | BXX_SLP4_VF1 | BXX Pump 4 Overload Enable | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_RA.RE | No | BXX Pump 4 Overload Enable | 0 | 0
BXX_SLP4_VF1_PB_DF_RE | BXX_SLP4_VF1 | BXX Pump 4 Not Ready Enable | 27 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_DF.RE | No | BXX Pump 4 Not Ready Enable | 0 | 0
BXX_SLP4_VF1_PB_GA_RE | BXX_SLP4_VF1 | BXX Pump 4 VFD Fault Enable | 27 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_GA.RE | No | BXX Pump 4 VFD Fault Enable | 0 | 0
BXX_SLP4_VF1_PB_TA_RE | BXX_SLP4_VF1 | BXX Pump 4 Temp/Leak Alarm Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_TA.RE | No | BXX Pump 4 Temp/Leak Alarm Enable | 0 | 0
BXX_SLP4_VF1_PB_ES_DE | BXX_SLP4_VF1 | BXX Pump 4 E-Stop Dialer Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_ES.DE | No | BXX Pump 4 E-Stop Dialer Enable | 0 | 0
BXX_SLP4_VF1_PB_RA_DE | BXX_SLP4_VF1 | BXX Pump 4 Overload Dialer Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_RA.DE | No | BXX Pump 4 Overload Dialer Enable | 0 | 0
BXX_SLP4_VF1_PB_DF_DE | BXX_SLP4_VF1 | BXX Pump 4 Not Ready Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_DF.DE | No | BXX Pump 4 Not Ready Dialer Enable | 0 | 0
BXX_SLP4_VF1_PB_GA_DE | BXX_SLP4_VF1 | BXX Pump 4 VFD Fault Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_GA.DE | No | BXX Pump 4 VFD Fault Dialer Enable | 0 | 0
BXX_SLP4_VF1_PB_TA_DE | BXX_SLP4_VF1 | BXX Pump 4 Temp/Leak Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_TA.DE | No | BXX Pump 4 Temp/Leak Dialer Enable | 0 | 0
BXX_SLP4_VF1_PB_ES_SR | BXX_SLP4_VF1 | BXX Pump 4 E-Stop Sup Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_ES.SR | No | BXX Pump 4 E-Stop Sup Enable | 0 | 0
BXX_SLP4_VF1_PB_RA_SR | BXX_SLP4_VF1 | BXX Pump 4 Overload Sup Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_RA.SR | No | BXX Pump 4 Overload Sup Enable | 0 | 0
BXX_SLP4_VF1_PB_DF_SR | BXX_SLP4_VF1 | BXX Pump 4 Not Ready Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_DF.SR | No | BXX Pump 4 Not Ready Sup Enable | 0 | 0
BXX_SLP4_VF1_PB_GA_SR | BXX_SLP4_VF1 | BXX Pump 4 VFD Fault Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_GA.SR | No | BXX Pump 4 VFD Fault Sup Enable | 0 | 0
BXX_SLP4_VF1_PB_TA_SR | BXX_SLP4_VF1 | BXX Pump 4 Temp/Leak Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_SLP4_VF1.DA_TA.SR | No | BXX Pump 4 Temp/Leak Sup Enable | 0 | 0
:MemoryInt | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinValue | MaxValue | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
PMP_VIS1 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS2 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS3 | $System | Pump Internal Visibility Link - Indirect |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Internal Visibility Link - Indirect | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMP_VIS4 | $System | Pump Speed Setpoint Visiblity Control |  | No | No | 0 | No | No | 0 | 0 |  | 0 | 0 | 9999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | Pump Speed Setpoint Visiblity Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DEV1_SI1_AI_VI | BXX_DEV1_SI1 | BXX Pump 4 Speed Number of Visible Eng Values | 45 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 3 | Linear | BXX | No | BXX_DEV1_SI1.AI_VI | No | BXX Pump 4 Speed Number of Visible Eng Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_DC | BXX_DEV1_SI1 | BXX Pump 4 Speed Precision | 26 | No | Yes | 700 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DEV1_SI1.AI_DC | No | BXX Pump 4 Speed Precision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_SLP4_VF1_AI_RT | BXX_SLP4_VF1 | BXX Pump 4 Runtime (Hours) | 26 | Yes | No | 0 | Yes | No | 0 | 0 | h | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_SLP4_VF1.AI_RT | No | BXX Pump 4 Runtime (Hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_VF1SI_CT | BXX_SLP4_VF1 | BXX Pump 4 Manual Speed Setpoint | 32 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_SLP4_VF1.SI_CT | No | BXX Pump 4 Manual Speed Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_SLP4_VF1_AO_CV | BXX_SLP4_VF1 | BXX Pump 4 Speed Command | 24 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_SLP4_VF1.AO_CT | No | BXX Pump 4 Speed Command | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AI_CV | BXX_DEV1_SI1 | BXX Pump 4 Speed Current Value | 30 | Yes | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AI_CV | No | BXX Pump 4 Speed Current Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_XM | BXX_DEV1_SI1 | BXX Pump 4 Speed Span Setpoint | 30 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_XM | No | BXX Pump 4 Speed Span Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_EM | BXX_DEV1_SI1 | BXX Pump 4 Speed Zero Setpoint | 30 | No | No | 0 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_EM | No | BXX Pump 4 Speed Zero Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_SV | BXX_DEV1_SI1 | BXX Pump 4 Speed Override Value | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_SV | No | BXX Pump 4 Speed Override Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1SN_ZA | BXX_DEV1_SI1 | BXX Pump 4 Speed Deviation Alarm Delay | 38 | No | Yes | 900 | Yes | No | 0 | 0 | s | 0 | 0 | 999 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 999 | Linear | BXX | No | BXX_DEV1_SI1.SN_LO | No | BXX Pump 4 Speed Deviation Alarm Delay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DEV1_SI1_AO_ZA | BXX_DEV1_SI1 | BXX Pump 4 Speed Deviation Setpoint | 35 | No | Yes | 900 | Yes | No | 0 | 0 | None | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DEV1_SI1.AO_LL | No | BXX Pump 4 Speed Deviation Setpoint | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_SLP4_VF1_DI_NM | BXX_SLP4_VF1 | BXX_SLP4_VF1 | 12 | No | No | 0 | Yes | 24 | BXX_SLP4_VF1 | BXX_SLP4_VF1
BXX_DEV1_SI1_DI_NM | BXX_DEV1_SI1 | BXX_DEV1_SI1 | 12 | No | No | 0 | Yes | 24 | BXX_DEV1_SI1 | BXX_DEV1_SI1
PMP_NAME | $System | Pump Name - Indirect |  | No | No | 0 | Yes | 131
PMP_SI_NAME | $System | Pump Feedback Tagname |  | No | No | 0 | Yes | 131
PMP_SK_NAME | $System | Stroke Feedback Tagname |  | No | No | 0 | Yes | 131
ALRM_PGRP | $System | Pump Alarm Query |  | No | No | 0 | Yes | 64 |  | Pump Alarm Query
:IOMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_SLP4_VF1_PB_AE_RN | BXX_SLP4_VF1 | BXX Pump 4 Alarms Disabled Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP4_VF1_PB_AE_RN | No | BXX Pump 4 Alarms Disabled Reason
BXX_SLP4_VF1_PB_ES_SR | BXX_SLP4_VF1 | BXX Pump 4 E-Stop Disabled Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP4_VF1_PB_ES_SR | No | BXX Pump 4 E-Stop Disabled Reason
BXX_SLP4_VF1_PB_RA_SR | BXX_SLP4_VF1 | BXX Pump 4 Overload Disabled Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP4_VF1_PB_RA_SR | No | BXX Pump 4 Overload Disabled Reason
BXX_SLP4_VF1_PB_DF_SR | BXX_SLP4_VF1 | BXX Pump 4 Not Ready Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP4_VF1_PB_DF_SR | No | BXX Pump 4 Not Ready Disabled Reason
BXX_SLP4_VF1_PB_GA_SR | BXX_SLP4_VF1 | BXX Pump 4 VFD Fault Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP4_VF1_PB_GA_SR | No | BXX Pump 4 VFD Fault Disabled Reason
BXX_SLP4_VF1_PB_TA_SR | BXX_SLP4_VF1 | BXX Pump 4 Temp/Leak Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_SLP4_VF1_PB_TA_SR | No | BXX Pump 4 Temp/Leak Disabled Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DI_SC | $System | Pump Feedback On Scan Indirect Tag | 34 | No | 0 | No
PMP_DM_DI_AA | $System | Pump Plant Auto Mode Status - Indirect | 38 | No | 0 | No
PMP_DM_DI_AS | $System | Pump Plant Auto Stroke Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_CL | $System | Pump Control Mode - Indirect | 28 | No | 0 | No
PMP_DM_DI_MS | $System | Pump Plant Manual Stroke Status - Indirect | 42 | No | 0 | No
PMP_DM_DI_PM | $System | Pump Plant Manual Mode Status - Indirect | 40 | No | 0 | No
PMP_DM_DI_SK | $System | Pump Stroke Control Mode - Indirect | 35 | No | 0 | No
PMP_DM_DI_SS | $System | Pump Running Status - Indirect | 30 | No | 0 | No
PMP_DM_PB_AR | $System | Pump Alarm Ack. Req. - Indirect | 31 | No | 0 | No
PMP_DM_PB_MS | $System | Pump Plant Manual Stroke Req. - Indirect | 40 | No | 0 | No
PMP_DM_PB_PM | $System | Pump Plant Manual Mode Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PP | $System | Pump Plant Manual Stop Req. - Indirect | 38 | No | 0 | No
PMP_DM_PB_PT | $System | Pump Plant Manual Start Req. - Indirect | 39 | No | 0 | No
PMP_DM_PB_RT | $System | Pump Runtime Reset - Indirect | 29 | No | 0 | No
PMP_PB_AE | $System | Pump Alarm Enable Pushbutton Indirect Tag | 41 | No | 0 | No
PMP_PB_ER | $System | Pump Speed Signal Error Enable Indirect Tag | 43 | No | 0 | No
PMP_PB_SC | $System | Pump Speed Feedback Scan Enable Indirect Tag | 44 | No | 0 | No
PMP_PB_SF | $System | Pump Fail To Start Enable Ind. Tag | 34 | No | 0 | No
PMP_PB_SM | $System | Pump Simulate Alarms Pushbutton Indirect Tag | 44 | No | 0 | No
PMP_PB_SU | $System | Pump Fail To Stop Enable Ind. Tag | 33 | No | 0 | No
PMP_PB_SV | $System | Pump Simulate Feedback Indirect Tag | 35 | No | 0 | No
PMP_PB_XF | $System | Pump Uncommanded Start Enable Ind. Tag | 38 | No | 0 | No
PMP_PB_XU | $System | Pump Uncommanded Stop Enable Ind. Tag | 37 | No | 0 | No
PMP_PB_ZA | $System | Pump Deviation Alarm Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_DA_ER | $System | Stroke Feedback Signal Error Indirect Tag | 41 | No | 0 | No
PMP_SK_DI_SC | $System | Stroke Feedback on Scan Indirect Tag | 36 | No | 0 | No
PMP_SK_PB_ER | $System | Stroke Feedback Signal Error Enable Indirect Tag | 48 | No | 0 | No
PMP_SK_PB_SC | $System | Stroke Feedback Scan Enable Indirect Tag | 40 | No | 0 | No
PMP_SK_PB_SV | $System | Stroke Feedback Simulate Value Indirect Tag | 43 | No | 0 | No
PMP_SK_PB_ZA | $System | Stroke Feedback Deviation Alarm Enable Ind. Tag | 47 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_DC2 | $System | Pump Signal Engineering Units 2 - Indirect | 42 | No | 0 | No
PMP_DC3 | $System | Pump Signal Engineering Units 3 - Indirect | 42 | No | 0 | No
PMP_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_AI_CV | $System | Pump Signal Feedback Indirect Tag | 33 | No | 0 | No
PMP_AI_VI | $System | Pump Signal Feedback Visible Values Ind. Tag | 44 | No | 0 | No
PMP_AO_SV | $System | Pump Feedback Override Value Indirect Tag | 41 | No | 0 | No
PMP_AO_ZA | $System | Deviation Alarm Setpoint Indirect Tag | 37 | No | 0 | No
PMP_DM_AI_RT | $System | Pump Runtime - Indirect | 23 | No | 0 | No
PMP_E1_EM | $System | Pump Feedback Zero Indirect Tag | 31 | No | 0 | No
PMP_E1_XM | $System | Pump Feedback Span Indirect Tag | 31 | No | 0 | No
PMP_E2_CV | $System | Pump Feedback Secondary Eng Value Ind. Tag | 42 | No | 0 | No
PMP_E3_CV | $System | Pump Feedback Tertiary Eng Value Indirect Tag | 45 | No | 0 | No
PMP_SI_AO_CT | $System | VFD Pump Manual Speed Setpoint - Indirect Analog | 48 | No | 0 | No
PMP_SK_DC2 | $System | Pump Stroke Signal Engineering Units 2 - Indirect | 49 | No | 0 | No
PMP_SK_DC3 | $System | Pump Stroke Signal Engineering Units 3 - Indirect | 49 | No | 0 | No
PMP_SK_DEC | $System | Pump Signal Decimal Points - Indirect | 37 | No | 0 | No
PMP_SK_AI_CV | $System | Stroke Feedback Indirect Tag | 28 | No | 0 | No
PMP_SK_AI_VI | $System | Stroke Feedback Number of Visible Units Ind. Tag | 48 | No | 0 | No
PMP_SK_AO_CT | $System | VFD Pump Stroke Setpoint - Indirect Analog | 42 | No | 0 | No
PMP_SK_AO_SV | $System | Stroke Feedback Simulation Value Indirect Tag | 45 | No | 0 | No
PMP_SK_AO_ZA | $System | Stroke Deviation Setpoint Indirect Tag | 38 | No | 0 | No
PMP_SK_E1_EM | $System | Stroke Feedback Zero Scale Indirect Tag | 39 | No | 0 | No
PMP_SK_E1_XM | $System | Stroke Feedback Spane Indirect Tag | 34 | No | 0 | No
PMP_SK_E2_CV | $System | Stroke Feedback Secondary Units Indirect Tag | 44 | No | 0 | No
PMP_SK_E3_CV | $System | Stroke Feedback Tertiary Units Indirect Tag | 43 | No | 0 | No
PMP_SK_SN_ZA | $System | Stroke Deviation Alarm Delay Indirect Tag | 41 | No | 0 | No
PMP_SN_ZA | $System | Deviation Alarm Delay Time Indirect Tag | 39 | No | 0 | No
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
PMP_SRV | $System | Pump Alarm Group Server Indirect Tag | 36 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
PMP_DM_GRP | $System | Pump Group - Indirect | 21

## BXXGEN1DE1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_GEN1_DE1 | BXX | BXX Generator | 13 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:Memory_DIsc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
ATS_VIS1 | $System | ATS Visible on Generator Pop-up Control | 39 | No | No | 0 | Yes | On |  |  | None | 1 | Duty Select Info Button Visibility | 0 | 0
ATS_VIS2 | $System | Controls Visiblity of Test Buttons | 34 | No | No | 0 | Yes | On |  |  | None | 1 | Duty Select Info Button Visibility | 0 | 0
:IO_DIsc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_GEN1_DE1_DI_AD | BXX_DSAB | BXX Generator Disabled Alarm | 28 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_GEN1_DE1.DI_AD | No | BXX Generator Disabled Alarm | 0 | 0
BXX_GEN1_DE1_DI_CL | BXX_GEN1_DE1 | BXX Generator Control Mode | 26 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DI_CL.eng | No | BXX Generator Control Mode | 0 | 0
BXX_GEN1_DE1_DI_SS | BXX_GEN1_DE1 | BXX Generator Running Status | 28 | No | No | 0 | Yes | Off | Stopped | Running | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DI_SS.eng | No | BXX Generator Running Status | 0 | 0
BXX_GEN1_DE1_DA_SS | BXX_GEN1_DE1 | BXX Generator Running Alarm | 27 | Yes | No | 0 | Yes | Off | Stopped | Running | On | 55 | Direct | BXX | No | BXX_GEN1_DE1.DA_SS.eng | No | BXX Generator Running Alarm | 0 | 0
BXX_GEN1_DE1_DA_ES | BXX_GEN1_DE1 | BXX Generator E-Stop | 20 | No | No | 0 | Yes | Off | Normal | Alarm | On | 50 | Direct | BXX | No | BXX_GEN1_DE1.DA_ES.eng | No | BXX Generator E-Stop | 0 | 0
BXX_GEN1_DE1_DA_JW | BXX_GEN1_DE1 | BXX Generator Warning | 21 | No | No | 0 | Yes | Off | Normal | Alarm | On | 55 | Direct | BXX | No | BXX_GEN1_DE1.DA_JW.eng | No | BXX Generator Warning | 0 | 0
BXX_GEN1_DE1_DA_GA | BXX_GEN1_DE1 | BXX Generator Fault | 19 | No | No | 0 | Yes | Off | Normal | Alarm | On | 55 | Direct | BXX | No | BXX_GEN1_DE1.DA_GA.eng | No | BXX Generator Fault | 0 | 0
BXX_GEN1_DE1_PB_AR | BXX_GEN1_DE1 | BXX Generator Alarm Ack | 23 | No | Yes | 600 | Yes | Off | Normal | Ack | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_AR | No | BXX Generator Alarm Ack | 0 | 0
BXX_GEN1_DE1_PB_RT | BXX_GEN1_DE1 | BXX Generator Runtime Reset | 27 | No | Yes | 600 | Yes | Off | Normal | Reset | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_RT | No | BXX Generator Runtime Reset | 0 | 0
BXX_GEN1_DE1_DA_SF | BXX_GEN1_DE1 | BXX Generator Failed To Start | 29 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_GEN1_DE1.DA_SF | No | BXX Generator Failed To Start | 0 | 0
BXX_GEN1_DE1_DA_XF | BXX_GEN1_DE1 | BXX Generator Failed To Stop | 28 | No | No | 0 | Yes | Off | Normal | Alarm | On | 52 | Direct | BXX | No | BXX_GEN1_DE1.DA_XF | No | BXX Generator Failed To Stop | 0 | 0
BXX_GEN1_DE1_DA_RM | BXX_GEN1_DE1 | BXX Generator Not in Auto | 25 | No | No | 0 | Yes | Off | Normal | Alarm | On | 49 | Direct | BXX | No | BXX_GEN1_DE1.DA_RM | No | BXX Generator Not in Auto | 0 | 0
BXX_GEN1_DE1_PB_SF | BXX_GEN1_DE1 | BXX Generator Failed To Start Alarm En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_SF.RE | No | BXX Generator Failed To Start Alarm En | 0 | 0
BXX_GEN1_DE1_PB_XF | BXX_GEN1_DE1 | BXX Generator Failed To Stop Alarm En | 37 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_XF.RE | No | BXX Generator Failed To Stop Alarm En | 0 | 0
BXX_GEN1_DE1_PB_RM | BXX_GEN1_DE1 | BXX Generator Not in Auto Alarm En | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_RM.RE | No | BXX Generator Not in Auto Alarm En | 0 | 0
BXX_GEN1_DE1_PB_SM | BXX_GEN1_DE1 | BXX Generator Simulate Alarms PB | 32 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_SM | No | BXX Generator Simulate Alarms PB | 0 | 0
BXX_GEN1_DE1_PB_AE | BXX_GEN1_DE1 | BXX Generator Alarm Enable | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_AE.RE | No | BXX Generator Alarm Enable | 0 | 0
BXX_GEN1_DE1_PB_SF_DE | BXX_GEN1_DE1 | BXX Generator Failed To Start Dialer En | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_SF.DE | No | BXX Generator Failed To Start Dialer En | 0 | 0
BXX_GEN1_DE1_PB_XF_DE | BXX_GEN1_DE1 | BXX Generator Failed to Stop Dialer En | 38 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_XF.DE | No | BXX Generator Failed to Stop Dialer En | 0 | 0
BXX_GEN1_DE1_PB_RM_DE | BXX_GEN1_DE1 | BXX Generator Not In Auto Dialer En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_RM.DE | No | BXX Generator Not In Auto Dialer En | 0 | 0
BXX_GEN1_DE1_PB_SF_SR | BXX_GEN1_DE1 | BXX Generator Failed To Start Sup En | 36 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_SF.SR | No | BXX Generator Failed To Start Sup En | 0 | 0
BXX_GEN1_DE1_PB_XF_SR | BXX_GEN1_DE1 | BXX Generator Failed To Stop Sup En | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_XF.SR | No | BXX Generator Failed To Stop Sup En | 0 | 0
BXX_GEN1_DE1_PB_RM_SR | BXX_GEN1_DE1 | BXX Generator Not In Auto Sup En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.PB_RM.SR | No | BXX Generator Not In Auto Sup En | 0 | 0
BXX_GEN1_DE1_PB_ES_RE | BXX_GEN1_DE1 | BXX Generator E-Stop Enable | 27 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_ES.RE | No | BXX Generator E-Stop Enable | 0 | 0
BXX_GEN1_DE1_PB_JW_RE | BXX_GEN1_DE1 | BXX Generator Warning Enable | 28 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_JW.RE | No | BXX Generator Warning Enable | 0 | 0
BXX_GEN1_DE1_PB_GA_RE | BXX_GEN1_DE1 | BXX Generator Fault Enable | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_GA.RE | No | BXX Generator Fault Enable | 0 | 0
BXX_GEN1_DE1_PB_ES_DE | BXX_GEN1_DE1 | BXX Generator E-Stop Dialer Enable | 34 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_ES.DE | No | BXX Generator E-Stop Dialer Enable | 0 | 0
BXX_GEN1_DE1_PB_JW_DE | BXX_GEN1_DE1 | BXX Generator Warning Dialer Enable | 35 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_JW.DE | No | BXX Generator Warning Dialer Enable | 0 | 0
BXX_GEN1_DE1_PB_GA_DE | BXX_GEN1_DE1 | BXX Generator Fault Dialer Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_GA.DE | No | BXX Generator Fault Dialer Enable | 0 | 0
BXX_GEN1_DE1_PB_ES_SR | BXX_GEN1_DE1 | BXX Generator E-Stop Sup Enable | 31 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_ES.SR | No | BXX Generator E-Stop Sup Enable | 0 | 0
BXX_GEN1_DE1_PB_JW_SR | BXX_GEN1_DE1 | BXX Generator Warning Sup Enable | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_JW.SR | No | BXX Generator Warning Sup Enable | 0 | 0
BXX_GEN1_DE1_PB_GA_SR | BXX_GEN1_DE1 | BXX Generator Fault Sup Enable | 30 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_GEN1_DE1.DA_GA.SR | No | BXX Generator Fault Sup Enable | 0 | 0
BXX_GEN1_DE1_DA_SS | BXX_GEN1_DE1 | BXX Generator Running Alarm | 27 | Yes | No | 0 | Yes | Off | Stopped | Running | On | 55 | Direct | BXX | No | BXX_GEN1_DE1.DA_SS.eng | No | BXX Generator Running Alarm | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_GEN1_DE1_AI_RT | BXX_GEN1_DE1 | BXX Generator Runtime (Hours) | 29 | Yes | No | 0 | Yes | No | 0 | 0 | h | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_GEN1_DE1.AI_RT | No | BXX Generator Runtime (Hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_GEN1_DE1_DI_NM | BXX_GEN1_DE1 | BXX_GEN1_DE1 | 12 | No | No | 0 | Yes | 24 | BXX_GEN1_DE1 | BXX_GEN1_DE1
GEN_NAME | $System | Generator Name | 14 | No | No | 0 | Yes | 64
:IOMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_GEN1_DE1_PB_SF_RN | BXX_GEN1_DE1 | BXX Generator Failed To Start Dis Reason | 40 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_SF_RN | No | BXX Generator Failed To Start Dis Reason
BXX_GEN1_DE1_PB_XF_RN | BXX_GEN1_DE1 | BXX Generator Failed To Stop Dis Reason | 39 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_XF_RN | No | BXX Generator Failed To Stop Dis Reason
BXX_GEN1_DE1_PB_ES_RN | BXX_GEN1_DE1 | BXX Generator E-Stop Disabled Reason | 36 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_ES_RN | No | BXX Generator E-Stop Disabled Reason
BXX_GEN1_DE1_PB_JW_RN | BXX_GEN1_DE1 | BXX Generator Warning Disabled Reason | 37 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_JW_RN | No | BXX Generator Warning Disabled Reason
BXX_GEN1_DE1_PB_GA_RN | BXX_GEN1_DE1 | BXX Generator Fault Disabled Reason | 35 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_GA_RN | No | BXX Generator Fault Disabled Reason
BXX_GEN1_DE1_PB_RM_RN | BXX_GEN1_DE1 | BXX Generator Not In Auto Disabled Reason | 41 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_GEN1_DE1_PB_RM_RN | No | BXX Generator Not In Auto Disabled Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
GEN_DI_AA | $System | Generator in Auto Indirect Tag | 30 | No | 0 | No
GEN_DI_CL | $System | Generator Control Mode Indirect Tag | 35 | No | 0 | No
GEN_DI_SS | $System | Generator Running Indirect Tag | 30 | No | 0 | No
GEN_PB_AE | $System | Generator Alarms Enable PB Indirect Tag | 39 | No | 0 | No
GEN_PB_AR | $System | Generator Alarm Reset Indirect Tag | 34 | No | 0 | No
GEN_PB_RM | $System | Generator Not In Auto Enable PB Indirect Tag | 44 | No | 0 | No
GEN_PB_RT | $System | Generator Runtime Reset Indirect Tag | 36 | No | 0 | No
GEN_PB_SF | $System | Generator Fail to Start Enable PB Indirect Tag | 46 | No | 0 | No
GEN_PB_SM | $System | Generator Simulate Alarms PB Indirect Tag | 41 | No | 0 | No
GEN_PB_XF | $System | Generator Fail to Stop Enable Indirect Tag | 42 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
GEN_AI_RT | $System | Generator Runtime Indirect Tag | 30 | No | 0 | No
:GroupVar | Group | Comment | 7 | SymbolicName
GEN_GRP | $System | GENSET Group - Indirect | 23
:InDIrectMsg | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
GEN_SRV | $System | Generator Alarm Server Indirect Tag | 35 | No | 0 | No

## BXXATS1SG1
:mode=ask
:AlarmGroup | Group | Comment | Description Lengths | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_ATS1_SG1 | BXX_GEN1_DE1 | BXX ATS | 7 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DSAB | Disabled_Alarms | BXX Disabled Alarms | 19 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_ATS1_SG1_DI_AD | BXX_DSAB | BXX ATS Disabled Alarm | 22 | No | No | 0 | Yes | Off | Off | On | On | 98 | Direct | BXX | No | BXX_ATS1_SG1.DI_AD | No | BXX ATS Disabled Alarm | 0 | 0
BXX_ATS1_SG1_DI_CL | BXX_ATS1_SG1 | BXX ATS Control Mode | 20 | No | Yes | 700 | Yes | Off | Local | Remote | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DI_CL.eng | No | BXX ATS Control Mode | 0 | 0
BXX_ATS1_SG1_DI_JN | BXX_ATS1_SG1 | BXX ATS Normal Power | 20 | No | Yes | 700 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DI_JN.eng | No | BXX ATS Normal Power | 0 | 0
BXX_ATS1_SG1_DA_JE | BXX_ATS1_SG1 | BXX ATS On Emergency Power | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 20 | Direct | BXX | No | BXX_ATS1_SG1.DA_JE.eng | No | BXX ATS On Emergency Power | 0 | 0
BXX_ATS1_SG1_PB_AR | BXX_ATS1_SG1 | BXX ATS Alarm Ack | 17 | No | Yes | 600 | Yes | Off | Normal | Ack | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_AR | No | BXX ATS Alarm Ack | 0 | 0
BXX_ATS1_SG1_PB_RT | BXX_ATS1_SG1 | BXX ATS Runtime Reset | 21 | No | Yes | 600 | Yes | Off | Normal | Reset | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_RT | No | BXX ATS Runtime Reset | 0 | 0
BXX_ATS1_SG1_PB_PO | BXX_ATS1_SG1 | BXX ATS Start Test Request | 26 | No | Yes | 600 | Yes | Off | Normal | Start | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_PO | No | BXX ATS Start Test Request | 0 | 0
BXX_ATS1_SG1_PB_PC | BXX_ATS1_SG1 | BXX ATS Stop Test Request | 25 | No | Yes | 600 | Yes | Off | Normal | Stop | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_PC | No | BXX ATS Stop Test Request | 0 | 0
BXX_ATS1_SG1_DA_JR | BXX_ATS1_SG1 | BXX ATS Failed To Transfer | 26 | No | No | 0 | Yes | Off | Normal | Alarm | On | 51 | Direct | BXX | No | BXX_ATS1_SG1.DA_SF | No | BXX ATS Failed To Transfer | 0 | 0
BXX_ATS1_SG1_DA_RM | BXX_ATS1_SG1 | BXX ATS Not in Auto | 19 | No | No | 0 | Yes | Off | Normal | Alarm | On | 49 | Direct | BXX | No | BXX_ATS1_SG1.DA_RM | No | BXX ATS Not in Auto | 0 | 0
BXX_ATS1_SG1_PB_JR | BXX_ATS1_SG1 | BXX ATS Failed To Xfer En | 25 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_JR.RE | No | BXX ATS Failed To Xfer En | 0 | 0
BXX_ATS1_SG1_PB_RM | BXX_ATS1_SG1 | BXX ATS Not in Auto Alarm En | 28 | No | No | 0 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_RM.RE | No | BXX ATS Not in Auto Alarm En | 0 | 0
BXX_ATS1_SG1_PB_SM | BXX_ATS1_SG1 | BXX ATS Simulate Alarms PB | 26 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_SM | No | BXX ATS Simulate Alarms PB | 0 | 0
BXX_ATS1_SG1_PB_AE | BXX_ATS1_SG1 | BXX ATS Alarm Enable | 20 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_AE.RE | No | BXX ATS Alarm Enable | 0 | 0
BXX_ATS1_SG1_PB_JR_DE | BXX_ATS1_SG1 | BXX ATS Failed To Xfer Dialer En | 32 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_JR.DE | No | BXX ATS Failed To Xfer Dialer En | 0 | 0
BXX_ATS1_SG1_PB_RM_DE | BXX_ATS1_SG1 | BXX ATS Not In Auto Dialer En | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_RM.DE | No | BXX ATS Not In Auto Dialer En | 0 | 0
BXX_ATS1_SG1_PB_JR_SR | BXX_ATS1_SG1 | BXX ATS Failed To Xfer Sup En | 29 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_JR.SR | No | BXX ATS Failed To Xfer Sup En | 0 | 0
BXX_ATS1_SG1_PB_RM_SR | BXX_ATS1_SG1 | BXX ATS Not In Auto Sup En | 26 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.PB_RM.SR | No | BXX ATS Not In Auto Sup En | 0 | 0
BXX_ATS1_SG1_PB_JE_RE | BXX_ATS1_SG1 | BXX ATS On Emergency Power Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DA_JE.RE | No | BXX ATS On Emergency Power Enable | 0 | 0
BXX_ATS1_SG1_PB_JE_DE | BXX_ATS1_SG1 | BXX ATS On Emergency Power Dialer Enable | 40 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DA_JE.DE | No | BXX ATS On Emergency Power Dialer Enable | 0 | 0
BXX_ATS1_SG1_PB_JE_SR | BXX_ATS1_SG1 | BXX ATS On Emerg Power Sup Enable | 33 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 1 | Direct | BXX | No | BXX_ATS1_SG1.DA_JE.SR | No | BXX ATS On Emerg Power Sup Enable | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_ATS1_SG1_AI_RT | BXX_ATS1_SG1 | BXX ATS Hours on Emerg. Power | 29 | Yes | No | 0 | Yes | No | 0 | 0 | h | 0 | 0 | 1000000 | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 1000000 | Linear | BXX | No | BXX_ATS1_SG1.AI_RT | No | BXX ATS Hours on Emerg. Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
BXX_ATS1_SG1_DI_NM | BXX_ATS1_SG1 | BXX_ATS1_SG1 | 12 | No | No | 0 | Yes | 24 | BXX_ATS1_SG1 | BXX_ATS1_SG1
ATSNAME | $System | ATS Name | 8 | No | No | 0 | Yes | 64
:IOMsg | Group | Comment |  | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | SymbolicName
BXX_ATS1_SG1_PB_SF_RN | BXX_ATS1_SG1 | BXX ATS Failed To Start Dis Reason | 34 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_ATS1_SG1_PB_SF_RN | No | BXX ATS Failed To Start Dis Reason
BXX_ATS1_SG1_PB_XF_RN | BXX_ATS1_SG1 | BXX ATS Failed To Stop Dis Reason | 33 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_ATS1_SG1_PB_XF_RN | No | BXX ATS Failed To Stop Dis Reason
BXX_ATS1_SG1_PB_JE_SR | BXX_ATS1_SG1 | BXX ATS on Emerg Power Disabled Reason | 38 | No | No | 0 | Yes | 131 | Please Type The Reason Here | BXXCPU01_1 | Yes | BXX_ATS1_SG1_PB_JE_SR | No | BXX ATS on Emerg Power Disabled Reason
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ATS_DA_JE | $System | ATS On Emergency Power Indirect Tag |  | No | 0 | No
ATS_DI_CL | $System | ATS Control Mode Indirect Tag |  | No | 0 | No
ATS_DI_JN | $System | ATS on Normal Power Indirect Tag |  | No | 0 | No
ATS_PB_AE | $System | ATS Alarm Enable Indirect Tag |  | No | 0 | No
ATS_PB_JR | $System | ATS Fail to Transfer Enable PB Indirect Tag |  | No | 0 | No
ATS_PB_PP | $System | ATS Plant Manual Stop Req. - Indirect |  | No | 0 | No
ATS_PB_PT | $System | ATS Plant Manual Start Req. - Indirect |  | No | 0 | No
ATS_PB_RM | $System | ATS Fail to Transfer Enable PB Indirect Tag |  | No | 0 | No
ATS_PB_RT | $System | ATS Runtime Reset Indirect Tag |  | No | 0 | No
ATS_PB_SM | $System | ATS Simulate Alarms PB Indirect Tag |  | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
ATS_AI_RT | $System | ATS Runtime Indirect Tag | 24 | No | 0 | No

## BXXDTY1DP
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DTY1_DP | BXX | BXX SLP Duty | 12 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:Memory_DIsc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
DTY_IN_VIS1 | $System | Duty Select Info Button Visibility | 34 | No | No | 0 | Yes | Off |  |  | None | 1 | Duty Select Info Button Visibility | 0 | 0
DTY_IN_D1_VIS1 | $System | Position 1 Device 1 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 1 Device 1 Selection Visibility | 0 | 0
DTY_IN_D1_VIS2 | $System | Position 1 Device 2 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 1 Device 2 Selection Visibility | 0 | 0
DTY_IN_D1_VIS3 | $System | Position 1 Device 3 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 1 Device 3 Selection Visibility | 0 | 0
DTY_IN_D1_VIS4 | $System | Position 1 Device 4 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 1 Device 4 Selection Visibility | 0 | 0
DTY_IN_D2_VIS1 | $System | Position 2 Device 1 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 2 Device 1 Selection Visibility | 0 | 0
DTY_IN_D2_VIS2 | $System | Position 2 Device 2 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 2 Device 2 Selection Visibility | 0 | 0
DTY_IN_D2_VIS3 | $System | Position 2 Device 3 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 2 Device 3 Selection Visibility | 0 | 0
DTY_IN_D2_VIS4 | $System | Position 2 Device 4 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 2 Device 4 Selection Visibility | 0 | 0
DTY_IN_D3_VIS1 | $System | Position 3 Device 1 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 3 Device 1 Selection Visibility | 0 | 0
DTY_IN_D3_VIS2 | $System | Position 3 Device 2 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 3 Device 2 Selection Visibility | 0 | 0
DTY_IN_D3_VIS3 | $System | Position 3 Device 3 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 3 Device 3 Selection Visibility | 0 | 0
DTY_IN_D3_VIS4 | $System | Position 3 Device 4 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 3 Device 4 Selection Visibility | 0 | 0
DTY_IN_D4_VIS1 | $System | Position 4 Device 1 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 4 Device 1 Selection Visibility | 0 | 0
DTY_IN_D4_VIS2 | $System | Position 4 Device 2 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 4 Device 2 Selection Visibility | 0 | 0
DTY_IN_D4_VIS3 | $System | Position 4 Device 3 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 4 Device 3 Selection Visibility | 0 | 0
DTY_IN_D4_VIS4 | $System | Position 4 Device 4 Selection Visibility | 40 | No | No | 0 | Yes | Off |  |  | None | 1 | Position 4 Device 4 Selection Visibility | 0 | 0
:IO_DIsc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DTY1_DP1_DI_UE | BXX_DTY1_DP | BXX SLP Duty Assignment Update Error | 36 | No | Yes | 700 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DTY1_DP.DI_UE | Yes | BXX SLP Duty Assignment Update Error | 0 | 0
BXX_DTY1_DP1_PB_AU | BXX_DTY1_DP | BXX SLP Duty Assignment Update | 30 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DTY1_DP.PB_AU | No | BXX SLP Duty Assignment Update | 0 | 0
BXX_DTY1_DP1_PB_SU | BXX_DTY1_DP | BXX SLP Duty Setpoint Update | 28 | No | Yes | 600 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DTY1_DP.PB_SU | No | BXX SLP Duty Setpoint Update | 0 | 0
BXX_DTY1_DP1_DI_EE | BXX_DTY1_DP | BXX SLP Duty Setpoint Update Error | 34 | No | Yes | 700 | Yes | Off | Off | On | None | 1 | Direct | BXX | No | BXX_DTY1_DP.DI_EE | No | BXX SLP Duty Setpoint Update Error | 0 | 0
:IOInt | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DTY1_DP1_AI_CT | BXX_DTY1_DP | BXX SLP Duty Pump 1 | 19 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AI_CT | Yes | BXX SLP Duty Pump 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_CT | BXX_DTY1_DP | BXX SLP Duty Pump 2 | 19 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_CT | Yes | BXX SLP Duty Pump 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AI_CT | BXX_DTY1_DP | BXX SLP Duty Pump 3 | 19 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AI_CT | Yes | BXX SLP Duty Pump 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_CT | BXX_DTY1_DP | BXX SLP Duty Pump 4 | 19 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_CT | Yes | BXX SLP Duty Pump 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AI_TY | BXX_DTY1_DP | BXX SLP Duty Days Remaining | 27 | No | Yes | 700 | Yes | No | 0 | 0 | Days | 0 | 0 | 10 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 10 | Linear | BXX | No | BXX_DTY1_DP.AI_TY | Yes | BXX SLP Duty Days Remaining | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_EN | BXX_DTY1_DP | BXX SLP Duty Rotation Mode | 26 | No | Yes | 900 | Yes | No | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 3 | Linear | BXX | No | BXX_DTY1_DP.AO_EN | No | BXX SLP Duty Rotation Mode | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_CT | BXX_DTY1_DP | BXX SLP Duty Pump 1 Entry | 25 | No | Yes | 900 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AO_CT | No | BXX SLP Duty Pump 1 Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_CT | BXX_DTY1_DP | BXX SLP Duty Pump 2 Entry | 25 | No | Yes | 900 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_CT | No | BXX SLP Duty Pump 2 Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AO_CT | BXX_DTY1_DP | BXX SLP Duty Pump 3 Entry | 25 | No | Yes | 900 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AO_CT | No | BXX SLP Duty Pump 3 Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_CT | BXX_DTY1_DP | BXX SLP Duty Pump 4 Entry | 25 | No | Yes | 900 | Yes | No | 0 | 0 |  | 1 | 1 | 4 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 4 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_CT | No | BXX SLP Duty Pump 4 Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_DY | BXX_DTY1_DP | BXX SLP Duty Rotation Daily Interval | 36 | No | Yes | 900 | Yes | No | 0 | 0 | d | 1 | 1 | 10 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 10 | Linear | BXX | No | BXX_DTY1_DP.AO_DY | No | BXX SLP Duty Rotation Daily Interval | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_HS | BXX_DTY1_DP | BXX SLP Duty Rotate Daily At Hour | 33 | No | Yes | 900 | Yes | No | 0 | 0 | hr | 0 | 0 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 23 | Linear | BXX | No | BXX_DTY1_DP.AO_HS | No | BXX SLP Duty Rotate Daily At Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_MS | BXX_DTY1_DP | BXX SLP Duty Rotate Daily At Minute | 35 | No | Yes | 900 | Yes | No | 0 | 0 | min | 0 | 0 | 59 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 59 | Linear | BXX | No | BXX_DTY1_DP.AO_MS | No | BXX SLP Duty Rotate Daily At Minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO__AI | BXX_DTY1_DP | BXX SLP Duty Rotation Hourly Interval | 37 | No | Yes | 900 | Yes | No | 0 | 0 | Hours | 1 | 1 | 23 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 23 | Linear | BXX | No | BXX_DTY1_DP.AO_AI | No | BXX SLP Duty Rotation Hourly Interval | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DTY1_DP1_AO_TS | BXX_DTY1_DP | BXX SLP Duty 1 Start Level Entry | 32 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AO_TS | No | BXX SLP Duty 1 Start Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_TS | BXX_DTY1_DP | BXX SLP Duty 2 Start Level Entry | 32 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_TS | No | BXX SLP Duty 2 Start Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AO_TS | BXX_DTY1_DP | BXX SLP Duty 3 Start Level Entry | 32 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AO_TS | No | BXX SLP Duty 3 Start Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_TS | BXX_DTY1_DP | BXX SLP Duty 4 Start Level Entry | 32 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_TS | No | BXX SLP Duty 4 Start Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AO_PS | BXX_DTY1_DP | BXX SLP Duty 1 Stop Level Entry | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AO_PS | No | BXX SLP Duty 1 Stop Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_PS | BXX_DTY1_DP | BXX SLP Duty 2 Stop Level Entry | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_PS | No | BXX SLP Duty 2 Stop Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AO_PS | BXX_DTY1_DP | BXX SLP Duty 3 Stop Level Entry | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AO_PS | No | BXX SLP Duty 3 Stop Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_PS | BXX_DTY1_DP | BXX SLP Duty 4 Stop Level Entry | 31 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_PS | No | BXX SLP Duty 4 Stop Level Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AI_TS | BXX_DTY1_DP | BXX SLP Duty 1 Start Level | 26 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AI_TS | No | BXX SLP Duty 1 Start Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_TS | BXX_DTY1_DP | BXX SLP Duty 2 Start Level | 26 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_TS | No | BXX SLP Duty 2 Start Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AI_TS | BXX_DTY1_DP | BXX SLP Duty 3 Start Level | 26 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AI_TS | No | BXX SLP Duty 3 Start Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_TS | BXX_DTY1_DP | BXX SLP Duty 4 Start Level | 26 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_TS | No | BXX SLP Duty 4 Start Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP1_AI_PS | BXX_DTY1_DP | BXX SLP Duty 1 Stop Level | 25 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY1_STS.AI_PS | No | BXX SLP Duty 1 Stop Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_PS | BXX_DTY1_DP | BXX SLP Duty 2 Stop Level | 25 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_PS | No | BXX SLP Duty 2 Stop Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP3_AI_PS | BXX_DTY1_DP | BXX SLP Duty 3 Stop Level | 25 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY3_STS.AI_PS | No | BXX SLP Duty 3 Stop Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_PS | BXX_DTY1_DP | BXX SLP Duty 4 Stop Level | 25 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_PS | No | BXX SLP Duty 4 Stop Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_XD | BXX_DTY1_DP | BXX SLP Duty 2 Level for Max. Speed | 35 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_XD | No | BXX SLP Duty 2 Level for Max. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_XD | BXX_DTY1_DP | BXX SLP Duty 4 Level for Max. Speed | 35 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_XD | No | BXX SLP Duty 4 Level for Max. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_XD | BXX_DTY1_DP | BXX SLP Duty 2 Level for Max. Speed Entry | 41 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_XD | No | BXX SLP Duty 2 Level for Max. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_XD | BXX_DTY1_DP | BXX SLP Duty 4 Level for Max. Speed Entry | 41 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_XD | No | BXX SLP Duty 4 Level for Max. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AI_ND | BXX_DTY1_DP | BXX SLP Duty 2 Level for Min. Speed | 35 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AI_ND | No | BXX SLP Duty 2 Level for Min. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AI_ND | BXX_DTY1_DP | BXX SLP Duty 4 Level for Min. Speed | 35 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AI_ND | No | BXX SLP Duty 4 Level for Min. Speed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP2_AO_ND | BXX_DTY1_DP | BXX SLP Duty 2 Level for Min. Speed Entry | 41 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY2_STS.AO_ND | No | BXX SLP Duty 2 Level for Min. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_DP4_AO_ND | BXX_DTY1_DP | BXX SLP Duty 4 Level for Min. Speed Entry | 41 | No | Yes | 900 | Yes | No | 0 | 0 | % | 0 | 0 | 100 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 0 | 100 | Linear | BXX | No | BXX_DTY1_DP.DTY4_STS.AO_ND | No | BXX SLP Duty 4 Level for Min. Speed Entry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
DTY_IN_DV1_NM | $System | Device 1 Name | 13 | No | No | 0 | No | 64
DTY_IN_DV2_NM | $System | Device 2 Name | 13 | No | No | 0 | No | 64
DTY_IN_DV3_NM | $System | Device 3 Name | 13 | No | No | 0 | No | 64
DTY_IN_DV4_NM | $System | Device 4 Name | 13 | No | No | 0 | No | 64
DTY_IN_D1_DP | $System | Description of Position 1 | 25 | No | No | 0 | No | 64
DTY_IN_D2_DP | $System | Description of Position 2 | 25 | No | No | 0 | No | 64
DTY_IN_D3_DP | $System | Description of Position 3 | 25 | No | No | 0 | No | 64
DTY_IN_D4_DP | $System | Description of Position 4 | 25 | No | No | 0 | No | 64
DTY_IN_DV_NM | $System | Duty Rotation Popup Device Type Description | 43 | No | No | 0 | No | 64
DTY_IN_INFO_LN1 | $System | Duty Select Info Popup Line 1 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 1 String
DTY_IN_INFO_LN2 | $System | Duty Select Info Popup Line 2 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 2 String
DTY_IN_INFO_LN3 | $System | Duty Select Info Popup Line 3 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 3 String
DTY_IN_INFO_LN4 | $System | Duty Select Info Popup Line 4 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 4 String
DTY_IN_INFO_LN5 | $System | Duty Select Info Popup Line 5 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 5 String
DTY_IN_INFO_LN6 | $System | Duty Select Info Popup Line 6 String | 36 | No | No | 0 | No | 64 |  | Duty Select Info Popup Line 6 String
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
DTY_IN_DA_UE | $System | Duty Selection Assignment Update Error | 38 | No | 0 | No
DTY_IN_PB_AU | $System | Duty Selection Assignment Update Request | 40 | No | 0 | No
:InDIrectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
DTY_IN_AI_DV | $System | Number of Devices for Duty Logic | 32 | No | 0 | No
DTY_IN_AI_TY | $System | Duty Timed Rotation Days Remaining | 34 | No | 0 | No
DTY_IN_AO__AI | $System | Duty Rotation Hour Setpoint | 27 | No | 0 | No
DTY_IN_AO_CT | $System | Duty Rotation Number of Days Setpoint | 37 | No | 0 | No
DTY_IN_AO_EN | $System | Duty Rotation Mode Select | 25 | No | 0 | No
DTY_IN_AO_HS | $System | Duty Timed Rotation Hour Setpoint | 33 | No | 0 | No
DTY_IN_AO_MS | $System | Duty Timed Rotation Minute Setpoint | 35 | No | 0 | No
DTY_IN_D1_AI_CT | $System | Duty 1 Assignment Current | 25 | No | 0 | No
DTY_IN_D1_AO_CT | $System | Duty 1 Assignment Entry | 23 | No | 0 | No
DTY_IN_D2_AI_CT | $System | Duty 2 Assignment Current | 25 | No | 0 | No
DTY_IN_D2_AO_CT | $System | Duty 2 Assignment Entry | 23 | No | 0 | No
DTY_IN_D3_AI_CT | $System | Duty 3 Assignment Current | 25 | No | 0 | No
DTY_IN_D3_AO_CT | $System | Duty 3 Assignment Entry | 23 | No | 0 | No
DTY_IN_D4_AI_CT | $System | Duty 4 Assignment Current | 25 | No | 0 | No
DTY_IN_D4_AO_CT | $System | Duty 4 Assignment Entry | 23 | No | 0 | No

## BXXDTY1LI
:mode=ask |  |  | Description Lengths
:AlarmGroup | Group | Comment | 7 | EventLogged | EventLoggingPriority | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | DSCAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | DSCAlarmInhibitor
BXX_DTY1_LI | BXX | BXX Wet Well Level Duty | 23 | Yes | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:IO_DIsc | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | InitialDisc | OffMsg | OnMsg | AlarmState | AlarmPri | DConversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | DSCAlarmDisable | DSCAlarmInhibitor | SymbolicName
BXX_DTY1_LI1_PB_EN | BXX_DTY1_LI | BXX Wet Well Level Duty Rotation Enable | 39 | No | Yes | 600 | Yes | Off | Enabled | Disabled | None | 94 | Direct | BXX | No | BXX_DTY1_LI.PB_EN | No | BXX Wet Well Level Duty Rotation Enable | 0 | 0
:IOReal | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | RetentiveAlarmParameters | AlarmValueDeadband | AlarmDevDeadband | EngUnits | InitialValue | MinEU | MaxEU | Deadband | LogDeadband | LoLoAlarmState | LoLoAlarmValue | LoLoAlarmPri | LoAlarmState | LoAlarmValue | LoAlarmPri | HiAlarmState | HiAlarmValue | HiAlarmPri | HiHiAlarmState | HiHiAlarmValue | HiHiAlarmPri | MinorDevAlarmState | MinorDevAlarmValue | MinorDevAlarmPri | MajorDevAlarmState | MajorDevAlarmValue | MajorDevAlarmPri | DevTarget | ROCAlarmState | ROCAlarmValue | ROCAlarmPri | ROCTimeBase | MinRaw | MaxRaw | Conversion | AccessName | ItemUseTagname | ItemName | ReadOnly | AlarmComment | AlarmAckModel | LoLoAlarmDisable | LoAlarmDisable | HiAlarmDisable | HiHiAlarmDisable | MinDevAlarmDisable | MajDevAlarmDisable | RocAlarmDisable | LoLoAlarmInhibitor | LoAlarmInhibitor | HiAlarmInhibitor | HiHiAlarmInhibitor | MinDevAlarmInhibitor | MajDevAlarmInhibitor | RocAlarmInhibitor | SymbolicName
BXX_DTY1_LI1_AO_CT | BXX_DTY1_LI | BXX Wet Well Level Duty Device Selected | 39 | No | Yes | 600 | Yes | No | 0 | 0 |  | 1 | 1 | 2 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 2 | Linear | BXX | No | BXX_DTY1_LI.AO_CT | No | BXX Wet Well Level Duty Device Selected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BXX_DTY1_LI1_AI_CV | BXX_DTY1_LI | BXX Wet Well Level Duty Transmitter | 35 | No | Yes | 700 | Yes | No | 0 | 0 |  | 1 | 1 | 2 | 0 | 0 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | Off | 0 | 1 | 0 | Off | 0 | 1 | Min | 1 | 2 | Linear | BXX | No | BXX_DTY1_LI.AI_CT | No | BXX Wet Well Level Duty Transmitter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
:MemoryMsg | Group | Comment | 7 | Logged | EventLogged | EventLoggingPriority | RetentiveValue | MaxLength | InitialMessage | AlarmComment | SymbolicName
DTY_IN_DV1_NM | $System | Device 1 Name | 13 | No | No | 0 | No | 64
DTY_IN_DV2_NM | $System | Device 2 Name | 13 | No | No | 0 | No | 64
DTY_IN_D1_DP | $System | Description of Position 1 | 25 | No | No | 0 | No | 64
DTY_IN_D2_DP | $System | Description of Position 2 | 25 | No | No | 0 | No | 64
DTY_IN_D3_DP | $System | Description of Position 3 | 25 | No | No | 0 | No | 64
DTY_IN_D4_DP | $System | Description of Position 4 | 25 | No | No | 0 | No | 64
:InDIrectDIsc | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
WW00_DY_PB_EN | $System | Duty Level Enable Indirect Tag | 30 | No | 0 | No
:IndirectAnalog | Group | Comment | 7 | EventLogged | EventLoggingPriority | RetentiveValue | SymbolicName
WW00_DY_AI_CV | $System | Duty Level Selected Transmitter Indirect Tag | 44 | No | 0 | No
WW00_DY_AO_CT | $System | Duty Level Transmitter Selected Indirect Tag | 44 | No | 0 | No
0
0
0