Regional Municipality of Halton

SCADA Standards Manual

Section 8 Wastewater Pumping Stations

SCADA STANDARDS 2022

Table of Contents

SECTION 8 WASTEWATER PUMPING STATIONS	1

8.1	DESIGN GUIDELINES	1

8.2	TEMPORARY WASTEWATER PUMPING STATIONS	1

8.3	CONTROL NARRATIVE	1

8.4	STANDARD SCADA 85% COMPLETE DRAWINGS	2

8.5	PLC PROGRAMS	2

8.6	Application Specific PLC Programming	3

Virtual Flow Meter	3

Building/Panel Security	3

8.7	HMI GRAPHICS	3

8.8	NETWORK COMMUNICATION STANDARDS	4

8.9	PROJECT DEVELOPMENT	4

Appendix 8A – Process Control Narrative Templates	5

Appendix 8B- Type I & II WWPS SCADA 85% Design Drawings	6

Appendix 8C – Type III & IV WWPS SCADA 85% Design Drawings	7

# WASTEWATER PUMPING STATIONS

## DESIGN GUIDELINES

#### Halton Region has developed design standards and templates specifically for Wastewater Pumping Stations. In general, the SCADA design is considered to be 85% complete.  It is the responsibility of the consultant to complete the project-specific SCADA design such that the final package is 100% complete.

#### Halton Region has developed within the Water, Wastewater, Solid Waste Facilities design manuals, a section specific to Wastewater Pumping Stations.  This section should be read in conjunction with the SCADA standards for Wastewater Pumping Stations.

#### This section is an explanation of the standards specific to Wastewater Pumping Stations.  All other SCADA standards still apply.

#### Should the consultant identify a discrepancy between the standards specified in this section and the standards from the other Sections, they should inform Halton Region in writing.

## TEMPORARY WASTEWATER PUMPING STATIONS

#### In cases where a temporary Wastewater Pumping Station is installed as an interim solution while the primary pumping station is undergoing construction/retrofitting, the consultant must ensure that the temporary station adheres to all of Halton Region’s SCADA standards.

#### In cases where temporary power is required as an interim solution while the primary pumping station is undergoing construction/retrofitting, the consultant must ensure that the temporary power and all equipment operating on the temporary power adheres to all of Halton Region’s SCADA standards.

#### In cases where an existing Wastewater Pumping Station is being upgraded or retrofitted as an interim solution, the consultant must follow the guidelines and templates identified in this section as closely as possible.  The consultant will issue a standards deviation memo as part of their submission package to identify any deviations.

## CONTROL NARRATIVE

#### Halton Region has developed Control Narrative templates specific to Wastewater Pumping Stations.  Consultants are required to develop their own project specific Control Narrative for each Wastewater Pumping Station.  The consultant Process Control Narrative should follow the same format as identified in the template.

#### In the body of the Process Control Narrative, there are specific instructions to the consultant. These instructions are in italics and are highlighted in yellow. Instructions are to be removed from the document when the consultant develops their project-specific narrative. All references to other sections have been highlighted in green. These all need to be checked before the narrative is finalized and submitted to the Region.

#### It is the responsibility of the consultant to contact Halton Region and ensure they are using the latest Process Control Narrative Template.

#### The Process Control Narrative prepared by the consultant shall be submitted as per the Consultant Procedure Manual.

#### Appendix 8A contains the following Control Narratives

##### Type I II WWPS Standard Control Narrative (2 Pumps)

##### Type III IV WWPS Standard Control Narrative (4 Pumps)

## STANDARD SCADA 85% COMPLETE DRAWINGS

#### Halton Region has developed P&ID Drawings, Single Line Drawings, Control Schematics, Backup Pump Control Schematics, Control Panel Layout Drawings, and PLC Loop drawing templates.  Refer to Appendix 8B and 8C. The consultant is required to develop their own project specific drawings for each Wastewater Pumping Station.  The drawings should follow the same format as shown in the templates.

#### For reference, additional Halton SCADA standard drawings are contained in Section 1, Appendix 1B, if required.

#### It is the responsibility of the consultant to contact Halton Region and ensure they are using the latest template drawings.

#### For pump control schematics there are 3 different types of motor starters used by Halton Region. They are, FVNR, soft starter with bypass, and VFD with bypass. Note that on the soft starter and the VFD, the bypass is an across-the-…line FVNR starter. There is a control schematic for each of these types of starters. The control schematics are in the Appendix 8B, Type I&II Drawing Templates and in Appendix 8C, Type III & IV Drawing Templates. This is done for organization only. The consultant can use a drawing from the Type I & II drawing set for the design of a Type III & IV drawing set and vice versa.

#### For the Type I & II stations, the 85% drawings show one pump as FVNR while the other pump has a VFD with bypass. The designer must adjust as required. If both pumps are FVNR, then simply copy the drawing for pump 1, and make the required minor changes.

#### For Type III & IV stations, the 85% drawings show Pumps 1 and 3 as soft starters with bypass, while the Pumps 2 and 4 have VFDs with bypass. The designer must adjust as required. If a FVNR is used, then use the drawing from Appendix 8B, Type I&II Drawing Templates as the starting point. If a soft starter without a bypass or VFD without bypass is used, refer to the drawings in Section 1 to assist in the necessary modifications.

#### For optional I/O, locations have been identified on the P&ID’s and the loop drawings. If the designer decides that these are not required, they are to be removed from the drawings.

## PLC PROGRAMS

#### Halton Region has developed template PLC programs for Type I and II and Type III and IV Stations in RSLogix5000.

#### The consultant is required to develop their own project specific PLC program. The program should follow the same format as identified in the template.

#### When programming the Auto Dialer PLC, the programmer should follow the example set by the most recently commissioned pumping station. The programmer is required to contact the Halton Region for the reference pumping station.

#### It is the responsibility of the consultant to contact Halton Region and ensure they are using the latest template programs.

#### Once the consultant has developed their program, it must be submitted to Halton Region as identified in Section 9 of these SCADA Standards.

## Application Specific PLC Programming

### Virtual Flow Meter

#### The purpose of the virtual flow meter is to provide an inexpensive method for measuring flow totals at Wastewater Pumping Stations.

#### This Source Code should only be installed at Wastewater Pumping Stations that have constant speed pumps.

#### Halton Region’s preference is to use a flow measuring instrument when possible.  This Source Code should only be used at locations where the installation of a flow meter is cost prohibitive.

#### The virtual flow meter accomplishes flow measurement by repeatedly performing draw down tests.  This method requires the volume between the Duty 1 start and stop setpoints be calculated.

#### The discharge flow is totalized for one calendar day.

#### The operation of the virtual flow meter is described in the standard Process Control Narratives.

### Building/Panel Security

#### All doors at the station are monitored by a normally closed magnetic door contact.  These contacts are individual inputs into the PLC.

#### When any door is opened, the input to the PLC opens and the Illegal Entry time starts (60 seconds default).

#### The person entering the station must insert a key into the switch and turn the key to disarm the security system.

#### The key switch is connected as a digital input to the PLC.  Once the PLC registers that the security key switch has been disarmed, the illegal entry timer stops and the security system armed light is no longer illuminated.

#### When a person is ready to leave, they will return to the security key switch, turn the key back to the “Armed” position remove their key and exit the station.

#### Once the key switch is returned to the “Armed” position, the exit timer (60 seconds default) starts and the person exiting the station has the duration of the timer to exit the building and ensure that all of the doors are closed.

#### Halton Region has developed security software and HMI graphics for this system as part of the base load programs.

## HMI GRAPHICS

#### Halton Region has developed HMI template graphics for 2 Pump and 4 Pump Stations.  The consultant is required to develop their own project-specific HMI graphics.  The HMI graphics should follow the same format as the template.

#### It is the responsibility of the consultant to contact Halton Region and ensure they are using the latest template HMI graphics.

#### Standard HMI Graphics shall be submitted for review as per Section 9 of the SCADA Standards and the Consultant Procedure Manual.

## NETWORK COMMUNICATION STANDARDS

#### For WAN requirements refer to section 4 – Structured Cabling.

## PROJECT DEVELOPMENT

#### Project requirements such as design reviews, FAT/SAT testing, commissioning/startup, and training are identified in Section 9 of the SCADA Standards and the Consultants Procedure Manual.

## Appendix 8A – Process Control Narrative Templates

| # | Document Name |
| --- | --- |
| 1 | Type I & II WWPS Standard Process Narrative (for 2 Pumps) |
| 2 | Type III & IV WWPS Standard Process Narrative (for 4 Pumps) |
| 3 |  |
| 4 |  |

## Appendix 8B- Type I & II WWPS SCADA 85% Design Drawings

## Appendix 8C – Type III & IV WWPS SCADA 85% Design Drawings