Regional Municipality of Halton

SCADA Standards Manual

Section 9 Testing and Commissioning

SCADASCADA STANDARDS 2022

Table of Contents

SECTION 9 Testing and Commissioning	1

9.1	Intent of this Section	1

9.2	SCADA Commissioning Binder	1

9.3	Control Narrative	1

9.4	Software Submission #1 – 50 % Complete Program	2

9.5	Software Submission #2 - Pre-Software FAT	2

9.6	Control Panel FAT Checklist	3

9.7	I/O Loop and PLC Panel Demonstration (SAT)	3

9.8	Software Factory Acceptance Testing	3

9.9	Final Checklist	3

9.10	Commissioning and Testing Procedures	4

9.11	I/O Loop and PLC Panel Testing (SAT) Procedure	4

9.12	I/O Loop and PLC Panel Demonstration (SAT) Procedure	5

9.13	Network Connectivity Testing	5

9.14	Software Site Acceptance Testing	6

9.15	Appendixes	6

9.16	Use of the Checklists	7

List of Tables

No table of figures entries found.

# Testing and Commissioning

## Intent of this Section

#### The intent of this section is to identify and detail the SCADA specific testing and commissioning requirements. This section must be read in conjunction with Section 4 - Structured Cabling, as that section details the testing requirements for all components related to structured cabling. It must also be read in conjunction with Section 17 of the Consultants Procedure Manual – Facilities.

#### This section provides many checklists that are to be used as templates for the development of job specific checklists by the Consultant. The items on these templates are to be considered as a minimum standard and nothing is to be removed when the job specific checklists are created. If an item does not apply to a specific job, then mark that item as “Not Applicable” on the checklist rather than removing it. The Consultant is free to add additional items to the checks as required to meet the specifics of any job.

#### The following terms are used throughout this document and the appendices.

#### Factory Acceptance Test (FAT)

#### Site Acceptance Test (SAT)

## SCADA Commissioning Binder

#### The Consultant is to prepare a master commissioning binder for each PLC. The binder is to be maintained by the consultant or system integrator until the Certificate of Total Performance is awarded to the contractor. At that point the binder is to be scanned and both a hard copy and an electronic copy is to be handed over to the Region’s Gate Keeper that has been assigned to the project. The electronic copy can be emailed or on USB stick. Either method is acceptable.

#### The Commissioning Binder is to be organized into several sections with a separate tab for each section. All the tabs are to be put in the binder right from the initial creation of the binder. All appropriate binders are to be brought to every check or testing event related to the binder. The following sections are to be included in the Commissioning Binder;

#### Tab 1 - Control Narrative;

#### Tab 2 - Software Submission #1 – 50 % Complete Program

#### Tab 3 - Software Submission #2 - Pre-Software FAT;

#### Tab 4 - Control Panel Shop Drawings and Panel FAT Checklist (FAT);

#### Tab 5 - I/O Loop and PLC Panel Demonstration;

#### Tab 6 - Software Factory Acceptance Testing (FAT);

#### Tab 7 - Software Site Acceptance Testing (SAT);

#### Tab 8 - Final Checklist.

#### Below is a description of how each section is to be used and what should be in the Commissioning Binder in each of the sections

## Control Narrative

#### This section should contain a copy of the most up to date version of the Control Narrative. This should be the version that the programmer used to write the final PLC and HMI programming. If the programmer deviates from this narrative while programming, this copy of the narrative is to be updated by hand at the time of the deviation, and an updated version should be edited, printed, and inserted into the Commissioning Binder as soon as possible. Any handwritten comments in the narrative are to be reviewed and initialed by the Region SCADA representative on the project. This is the version that the software will be tested against during the software FAT.

## Software Submission #1 – 50 % Complete Program

#### Submission #1 is to include a partially complete PLC program, a CSV file containing all the fully configured HMI tags, and static screenshots from the HMI application. Note that these static screenshots are to be same screens that were reviewed and approved during the Control Narrative review process.

#### Partially Complete PLC Program

#### Consultants can use SCADA Continuum to generate their PLC program or it can be generated manually. If the PLC program is generated using the SCADA Continuum, then the PLC program output from SCADA Continuum is to be submitted with Submission #1. If the PLC program is generated manually then the PLC program should be 50% complete and contain a minimum of the following;

#### All I/O properly mapped

#### One of every type of UDT that will be used in the PLC program

#### CSV File of all HMI Tags

#### Provide a CSV file that contains all the tags associated with the processes that the PLC is part of.

#### HMI Windows

#### Provide a copy of every HMI window that is pertinent to the PLC including any windows that are common to multiple PLCs such as the trending windows, the security windows, the server, work stations window, etc.

#### The programming should be done and submitted to the Region on a PLC by PLC basis. SCADA Continuum can be used to generate the PLC code and HMI tags. If it is used, then the Consultant will submit the PLC program and HMI tags generated by SCADA Continuum to the Region for review after the I/O list is loaded into SCADA Continuum. The Region will review the code for compliance with the standards as well as documentation, neatness, etc. Region staff will review the submission and fill out the checklist in Appendix 9A. Region staff will complete the checklist and send it to the consultant when the review is complete. The Consultant will then put the checklist into the Commissioning Binder. The consultant must provide 10 business days of review time for each PLC submission.

#### The checklist for this can be found in Appendix 9A. The Standard Deficiency List that can be found in the Appendix 9K is to be inserted in at the end of this section, and serve as the deficiency list for this section.

## Software Submission #2 - Pre-Software FAT

#### The Consultant is to make the second submission when the Consultant believes the PLC code and HMI is 100% complete and ready for Factory Acceptance Testing. The consultant must provide a 10-business day review period for each PLC submission. Software Factory Acceptance Testing is not to occur until all deficiencies from Submission #1 have been completed and approved by the Region’s SCADA representative. The Region will review the code for compliance with the standards as well as documentation, neatness, etc. Region staff will review the submission and fill out the checklist ‘Second Submission’ and ‘Checklist of Screens’ in Appendix 9B. Region staff will complete the checklist and send it to the consultant when the review is complete. The Consultant will then put the checklist into the Commissioning Binder.

#### The checklist for this can be found in Appendix 9B. The Standard Deficiency List that can be found in the Appendix 9K and it is to be inserted in at the end of this section, and serve as the deficiency list for this section.

## Control Panel FAT Checklist

#### This section is to contain a shop drawing review checklist and the final approved version of the shop drawings that the panel manufacturer used for the construction of the PLC panel.  The checklist is a minimum requirement and not a comprehensive list. The Consultant is responsible for all aspects of the shop drawing review, but the Region wants assurance that as a minimum, the items on the checklist were confirmed.

#### The shop drawings are to be the drawings that the PLC panel manufacturer produced and had approved for the construction of the panel. This section is to include the drawings used for the construction of the panel and the BOM that is part of those drawings. It does not need to include any product specific information such as catalogue cuts, owner’s manuals, etc. These shop drawings are to be used at the Panel FAT. If during the FAT, any deviations from these drawings are found that will remain, the drawings must be marked up by hand or notes made on the drawings so that this set of drawings remains an accurate set of as constructed drawing at the conclusion of the Panel FAT. Any other deficiencies are to be noted on the checklist.

#### The checklist for this can be found in Appendix 9C. The Standard Deficiency List that can be found in the Appendix 9K is to be inserted in at the end of this section, and serve as the deficiency list for this section.

## I/O Loop and PLC Panel Demonstration (SAT)

#### This section is to contain the checklist to be used during the I/O Loop and PLC Panel Demonstration. The check list for this can be found in Appendix 9D. Further details on how to conduct the I/O Loop and PLC Panel Demonstration are given below. In addition to the check list in Appendix 9D, this section of the commissioning binder should also include a standard deficiency list that can be found in Appendix 9K

## Software Factory Acceptance Testing

#### This section is to contain the checklist to be used during the Software FAT. In addition to this, the Consultant is to add a pump driver checklist for each pump, as found in Appendix 9H, a valve driver checklist for each valve, as found in Appendix 9I, and an analog signal checklist for each analog input, as found in Appendix 9J. The consultant is to use these checklists as a template and develop a full set of testing documentation to be used for the software FAT.

#### As a minimum, this test should be attended by the Region’s SCADA representative or designate, one representative from operations, and the Region’s maintenance representative on the project.

#### The Software Factory Acceptance Testing (FAT) checklist for this can be found in Appendix 9E. The Standard Deficiency List that can be found in the Appendix 9K is to be inserted in at the end of this section, and serve as the deficiency list for this section.

## Final Checklist

#### This section contains a checklist that is to be completed and signed off by the Region’s Gate Keeper on the job. It is a high level checklist to be completed to make sure all the ancillary SCADA related items were successfully completed, and that all old programming, tags, etc. have been deleted and removed.

#### It is the Consultant’s responsibility to include this checklist in the Commissioning Binder and to schedule a meeting between the Region’s Gate Keeper assigned to the project and to demonstrate that all of the items on the checklist have been finished.

#### The Final Checklist for this can be found in Appendix 9G. The Standard Deficiency List that can be found in the Appendix 9K is to be inserted in at the end of this section, and serve as the deficiency list for this section.

## Commissioning and Testing Procedures

#### With regards to the on-site testing of the PLC Panel and the I/O loops, there are 2 distinct steps that are to take place.

#### The first step is called the I/O Loop Testing and PLC Panel Testing. Only the contractor and the consultant are involved in this step. No Regional representatives are to attend this step.

#### The second step is the I/O Loop Testing and PLC Panel Demonstration. This step is attended by the contractor, the consultant, and Regional representatives.

#### The Consultant/Resident Engineer shall prepare and provide the Region’s Project Manager with a complete list of all PLC Panels to be checked-out by the Contractor no later than four months after the date of award of contract.

#### The Consultant is to follow the procedures outlined below for the specific activities listed.

## I/O Loop and PLC Panel Testing (SAT) Procedure

#### The purpose of this step is for the Contractor to test all the I/O loops in the presence of the Consultant who will verify and sign off that all the I/O loops have passed. Any deficiencies will be noted. No representative from the Region will be present during this testing. Consultant to arrange for the Contractor, Electrical, Instrumentation and Control Sub-Contractors to be present for testing of loop wiring between field devices and PLC.

#### For each individual PLC, the Consultant/Resident Engineer shall prepare a checklist to be used during the I/O loop testing and PLC Panel Testing. The sample checklist in Appendix 9D is to be used as a starting point. The first step of this process is for the Consultant to verify that all the deficiencies noted in the PLC Panel FAT have been rectified.

#### Permit no splicing of any loop wires between instrument and field devices and reject any connection not in compliance with manufacturers’ recommendations or industry practice of specification.

#### The Consultant’s programmer will be present during this testing. The programmer will have a laptop and will be online with the PLC during the testing. Each loop will be tested from the field device right through to the PLC program. Verification that the loop is functioning properly will be determined by examining the I/O point in the PLC program. Where possible, 4-20 mA signals should be generated using the field instrument and not by injecting a signal into the loop in some other location. For analog out signals, the programmer will use the output card to send 4-20mA signals through the loop via the PLC program. Verification of the signal is to be measured as close to the field device as is possible.

#### Once the Consultant has verified and signed off that each one of the loops have passed and all deficiencies are fixed, an I/O loop and PLC Panel “demonstration” will be scheduled for Regional personal to attend.

## I/O Loop and PLC Panel Demonstration (SAT) Procedure

#### The purpose of this step is for the Contractor and Consultant to demonstrate to the Region’s representative(s) that all the I/O loops and all aspects of the PLC Panel are complete and ready to be put into production.

#### For each individual PLC, the Consultant/Resident Engineer shall prepare a checklist to be used during the I/O loop and PLC Panel demonstration. The sample checklist in Appendix 9D is to be used as a starting point. This checklist includes the minimum items that must be checked. The Consultant can add additional items to be checked but should not remove any items from the checklist.

#### The Consultant/Resident Engineer shall provide the Contractor and Facility Operation and Maintenance Supervisory Staff with two sets of test procedures. Consultant to submit four draft copies of the checklist for review. On approval, provide one final copy to the Region’s SCADA representative, two copies to the Contractor, two copies to Facility Operation and Maintenance Supervisory Staff, and one copy to the Region’s Project Manager.

#### At least one Regional SCADA representative must be present to witness the I/O loop demonstration. Other Regional personal may attend but the demonstration cannot occur without one Regional SCADA representative present.

#### The first step of this process is for the Consultant to verify and sign off that all the deficiencies noted in the PLC Panel FAT have been rectified.

#### When testing I/O loops, ensure that the Contractor performs the testing of each loop in sequence. One PLC panel should be done as a complete group. The testing of a loop will be graded on a pass/fail basis. If more than ten loops within a panel failed the loop checkout, the entire panel of loops will be deemed to have failed the checkout and the testing will be stopped and the Region’s representatives will leave. When the failed loops have been corrected, the entire panel must be tested again. At least 10 business days’ notice must be given before rescheduling of the testing.

#### The Consultant is responsible to ensure that all parties sign the forms at the conclusion of each test. Consultant to complete the checklist for each PLC panel of I/O loop test and provided a copy to:

#### Facility Operation and Maintenance Supervisory Staff

#### Regional SCADA representative

#### Contractor/Sub-Contractors/Supplier

#### Region’s Project Manager

## Network Connectivity Testing

#### The purpose of this testing is to ensure that the network is complete and functional, and that all the devices on the network can talk to each other.  Section 4 of the Region’s SCADA Standards Manual details the testing requirements for the individual components that make up network such as the fiber and CAT6 Ethernet cabling. All this testing must be completed before the Network Connectivity Testing can be done.

#### The Consultant is responsible to ensure that all Ethernet devices have been properly set up, configured, and are able to communicate over the network once connectively is established across the network.

#### Regional SCADA and IT staff will be responsible for programming and installation of network switches and routers. Once installed and configured, the Consultant and Halton staff will confirm that all devices can talk on the network.

#### It is the Consultant and Contractors role to provide support and assistant to Regional staff during this testing. If problems are found with the physical media, then the Consultant and Contractors will be responsible for troubleshooting and repairing any deficiencies found.

## Software Site Acceptance Testing

#### The purpose of this step is to test and verify all the PLC code and HMI software, in a non-simulated mode, while controlling real world devices and responding to real world inputs.  As this testing has a direct impact on the operation and performance of the plant, much planning and organization must be done prior to commencing this test. For details on how this testing is to be carried out, refer to Section 17 of the “Region’s Consultant Procedure Manual – Facilities”.

#### I/O loops that have been demonstrated and passed during the I/O demonstration do not have to be tested from the field to the PLC. Those I/O points can be jumped inside the PLC program.

## Appendixes

#### There are several other appendixes that are provided for convenience. Below is a description of each and where and how they are to be used. 9H –Pump Driver Checklist.

#### The device driver checklist is to be added to the checklist for Software Factory Acceptance Testing and the checklist for the Software Site Acceptance Testing. This checklist is to be duplicated for the number of devices in the PLC.

#### 9I - Valve Driver

#### The valve driver checklist is to be added to the checklist for Software Factory Acceptance Testing and the checklist for the Software Site Acceptance Testing. This checklist is to be duplicated for the number of valves in the PLC.

#### 9J – Analog Input Driver

#### The analog input driver checklist is to be added to the checklist for Software Factory Acceptance Testing and the checklist for the Software Site Acceptance Testing. This checklist is to be duplicated for the number of analog inputs in the PLC.

#### 9K – Standard Deficiency Sheet

#### This sheet is to be copied and inserted at the end of each of the tabs in the binder and it is where all the deficiencies are to be tracked for each tab in the binder.

#### 9L –Generator and ATS Driver Checklist

#### The Generator and ATS driver checklist is to be added to the checklist for Software Factory Acceptance Testing and the checklist for the Software Site Acceptance Testing. This checklist is to be duplicated for the number of generators and ATS in the PLC.

#### 9M –Power Monitor Driver

#### The power monitor driver checklist is to be added to the checklist for Software Factory Acceptance Testing and the checklist for the Software Site Acceptance Testing. This checklist is to be duplicated for the number of power monitor in the PLC.

#### 9N – Rain Gauge Driver

#### The rain gauge driver checklist is to be added to the checklist for Software Factory Acceptance Testing and the checklist for the Software Site Acceptance Testing. This checklist is to be duplicated for the number of rain gauges in the PLC.

#### 9O – North Water Commissioning Checklist

#### This document is to be filled out when PLC or HMI changes are being made at an existing functional site that is part of the North Halton Water System, but not as part of an official SAT or commissioning the same day.  This work is being performed without the Region’s SCADA representative being present, but operations are present. This checklist is to ensure that all related systems are fully functional at completion of the work. This does not replace or preclude a full SAT.

## Use of the Checklists

#### Each of the checklists may need to be customized according to the work that is being done. On some of the checklist, there is wording that is in italics and underlined. This text is instructions to the consultant on how to use the checklists and should be removed when the commission binder is being used.