Changes to the Region of Halton, SCADA Standards for Version 2022

March 2022 Correction

The version of the standards that was released in January 2022 was found to have an error with how InTouch HMI tags were to be structured. There was a dot ”.” in the structure of the tag but the InTouch software does not permit the usage of a dot “.” within the structure of the tag. Therefore, all documents within the SCADA standards that had any reference to the dot “.” have been modified to remove the dot.

Introduction

This document is a summary of changes made to the Region’s SCADA Standards for the release of Version 2022.  Several minor wording changes have been made to many of the Word documents. These changes are insignificant and to numerous to list. These include things like fixing typos, errors, changing wording to add clarification and removing redundant statements.

Significant Changes

- Migrating the InTouch application base load to InTouch version 2020.

- Modifying the Regions tagging system by combining fragments 1 and 2 into one fragment and also placing an underscore “_” between each fragment in the tags. It is expected that all new HMI tags created starting January 1st 2022 will be built on this tagging standard unless otherwise directed by the Region.

- Modifications to the PRVs to allow them to self-reset in the event that communications is lost.

- Part numbers and models were updated in all documentation where required.

Drawing Changes that Apply to Drawing in Section 1 and Section 8

Section 1 General Requirements

- Removed Appendix 1A which contains the Blank Field Services Report and the PLC HMI Gatekeeper protocol.

- The Blank Field Services Report will now be managed as part of the SCADA Maintenance Contractor documentation as it has typically only been used by companies working under that contract.

- The gate keepers assigned to each of the 14 HMI applications was removed from the PLC HMI Gatekeeper protocol. The documentation of the assigned gate keepers will now be managed as a stand-alone document. Anyone requiring the PLC HMI Gatekeeper assignments can contact a member of the Region’s SCADA group.

- Standards were created for a Network Distribution Enclosure that will service remote sites such as water pumping stations and water storage facilities. These drawings are based on and are very similar to the Network Distribution Enclosures located at plants.

- Drawings related to remote facilities’ data connections were modified to include cellular connection, DSL connection and fiber connection. The consultant is then to remove the non-relevant portions of the drawing once the connection type is known.

Section 2 Tagname Convention

- Modifying the Regions tagging system by combining fragments 1 and 2 into on fragment and also placing an underscore “_” between each fragment in the tags.

- Modified the tagname fragments related to Prospect Park to reflect the actual PLC names and codes that are in use.

Section 5 PLC Hardware and Programming

- Rate of change alarms have been masked out when there is a signal error alarm.

Section 7 Supplemental Programming

No significant changes made.

Section 8 Wastewater Pumping Stations

- Separated the door and hatch contacts from being one common input to individual contacts per door.

- Cleaned up the 2 WWPS process control narratives and aligned the 2 pump station narratives with the general process control narrative template in Section 1.

- Added a section on rain gauges to the documents Type III IV WWPS Control Narrative (4 pumps) in Section 8.

- Modified the PLC code and process control narrative so that when a WWPS requires to have 2 VFDs running, the VFDs, will ramp up and down together based on wetwell instead of having on VFD at full speed and the other VFD ramping up and down.

- Updated the table at the end of each of the process control narratives to match the layout of the loop drawings.

- Added lights to all 4 compartments for the outdoor pump station panel.

- Pribusin units are no longer required in the design for wastewater pumping stations.

Section 9 Testing and Commissioning

No significant changes made.

Section 10 Ancillary Equipment

- Updated the auto dialer verification system to show that the Milton WWTP has now been decommissioned and the Mid-Halton WWTP is not the master location for the auto dialer verification system.