Regional Municipality of Halton

PLC, PanelView and HMI Gatekeeper Protocol

SCADA STANDARD 2022

1.0	 INTRODUCTION

The Region of Halton is responsible for the operation and maintenance of 13 water and wastewater plants, a Biosolids management facility, 5 landfill sites and over 140 remote pump stations, booster stations, elevated tanks and reservoirs. Much of the automation and control of these sites is achieved through SCADA systems, which consist of PLCs, PanelViews and Human Machine Interface (HMI) software. The Region has 15 HMI InTouch applications.

The role of maintaining an inventory of active and back-up copies of the PLC, PanelView or HMI code that make up the SCADA system is the responsibility of the Region’s SCADA team. Changes to the PLC, PanelView or HMI code are constantly on going. These changes are driven by many different forces including, but not limited to, process improvements, standards deployment and expansion of the systems. Several different groups working under different scenarios make these changes. The groups include Regional staff, Contractors completing maintenance activities and Consultants working on Capital Projects.

The purpose of this document is to define and put into place protocols that ensure that the Region’s SCADA team always has the active and back-up copies of the PLC, PanelView or HMI code. This document addresses all the possible scenarios that may arise while completing the changes.

# 2.0	 GATEKEEPERS

The Region has assigned a Gatekeeper to each of the 14 HMI InTouch applications and applicable PLCs. For a current list of the Gatekeeper Assignment, contact a member of the Region’s SCADA group.

Each application has also been assigned a back-up Gate Keeper who will fill in during the absence of the Gate Keeper.

## 2.0	Wonderware Historian Database Administrator

The Region uses Wonderware’s Historian as its long-term data collection and archiving tool. This is comprised of one server for the water systems (SCADA1) and one server for the wastewater systems (SCADA2). The wastewater server also collects the Biosolids and the Landfill site data.

The Region’s two SCADA Programmers are responsible for the SCADA Historians. Whenever changes are made to a Wonderware InTouch application that comprises adding, modifying or removing tags that have the Log Data box selected, any modifications to the Access Names, or any modifications to the I/O Server, then the Region’s Historian database needs to be updated. Immediately after completing the change, the Region’s SCADA Programmers need to be notified in writing by e-mail that the database needs to be updated.  The contractor or consultant will not be responsible for updating this database but is responsible to notify the appropriate Gage Keeper and the SCADA Programmers that an update is required.

# 3.0	 CARE AND CONTROL OF CODE AND HMI APPLICATION

The Region will conduct revision management by releasing and relinquishing care and control of the code and HMI applications. Code and HMI applications can only be under development by one party at a time. When a developer needs to complete work, they will request care and control of the code and or HMI application from the Gatekeeper in writing by e-mail for a fixed period of time. All SCADA staff must be copied on the request. The Gatekeeper will then grant them care and control for the requested period of time.

When the work is complete, the developer is to send an email to all SCADA staff informing them that the work is complete and they are now relinquishing care and control of the code and or HMI application. This email should include a summary of the work and all the PLC programs and/or HMI applications impacted.

Duration of Care and Control

Time periods requested must be as short as possible. When requesting care and control the developer is to provide a date and time that care and control will start and a date and time that care and control will end. If the work goes beyond the approved length of time for care and control, the developer must contact the Gatekeeper and request an extension to the period of care and control. This email is to be directed to the Gatekeeper and copied to all SCADA staff. The developer must not assume that since the work was not completed that they still have care and control.

# 4.0	 ARCHIVING AND BACKUP METHODOLOGY

## 4.1	PLC and PanelView Archiving and Backup Methodology

The Region uses FactoryTalk AssetCentre for the storage of PLC and PanelView code.  Note that HMI InTouch applications are not kept in AssetCentre.

Developers shall follow the procedures outlined in the “Contractor Access to AssetCentre” SOP for working with copies of the PLC and PanelView code.  This SOP is available on AssetCentre.

4.1.1 FactoryTalk Security

If the PLC requested by the developer is secured using FactoryTalk Security, then the Gatekeeper will have to unlock the code before the code is checked out by the developer. After the code is checked back in, the Gatekeeper will be responsible for securing the code.

## 4.2	HMI Software Archiving and Backup Methodology

The Region has developed and maintains 14 different InTouch HMI applications. Each individual application is a compilation of many files in one directory. These applications are too large to be transmitted by e-mail.

There are 2 different versions of each InTouch Application.  One version is referred to as the “Tagname Sever” version and this is the version that runs on the 2 I/O servers being CPU01 and CPU02. The second version is the “View Node Version” and this is the version that runs on the SCADA work stations and the Terminal Servers. Each of these versions must be kept up to date all the time.

There are always at least two copies of the Tagname server and two copies of the View Node installed at any one time. These multiple copies serve as back-ups to each other. If an application was to be deleted, become corrupted, or the computer it is running on fails, an exact copy of the application can be taken from one of the other computers/servers running that application.

Each computer/server should have 3 revisions of the application saved. They should be the active version, revision 1 and revision 2. Do not store more than 3 versions including the active version.

If a new version of the InTouch application is left in production on any server or work stations, then all servers and work stations that run the application must be updated before the developer leaves site for the day.

# 5.0	 POSSIBLE SCENARIOS UNDER WHICH CHANGES ARE MADE

There are 3 scenarios under which changes to the PLC, PanelView or HMI code can occur. Each scenario has its own protocol to be followed. These scenarios can be determined by answering 3 questions which allow the developer to determine which scenarios the changes are being made under.

Those questions are:

- Is the work repair work? If yes go to Section 6.1.

- Is the work commissioning of a capital project? If yes go to Section 6.2.

- Is the work a warranty repair from a capital project? If yes go to Section 6.3.

If you are unsure which scenario your work falls under, contact a member of the Region’s SCADA team for clarification and direction.

# 6.0	 SCENARIOS

## 6.1	Scenario 1 – Repair Work

Before starting any work, the developer must request care and control of the PLC or PanelView or HMI code as per section 3.

Once care and control has been granted, the developer is to obtain the PLC, PanelView or HMI code required as per section 4.

At the beginning of each day and prior to the developer going on line with the PLC or PanelView (either locally or remotely) the developer must notify the plant OIC or delegate of the changes to be made.

Make the changes and test the code with the plant OIC or delegate.

Notify the Historian Database Administrator if the Historian database needs to be updated.

All changes in the PLC code are to be fully documented in the rung comments. Things that are to be included in the rung comments are the developer’s initials, company name, date of the changes, description of the changes and reason for the changes.

When the work is complete and the developer is leaving the site they are to notify the OIC of the work status and that you are leaving the site or going off line.

Check the code back in or update the HMI as appropriate as per section 4.

## 6.2	Scenario 2 – Consultant Working During the Commissioning Phase

### 6.2.1	Changes to PLC or PanelView Code

Once the Region’s Gatekeeper has made the determination that a PLC or PanelView is in production, they will add the PLC program to AssetCentre and add the PLC code to the disaster recovery back up and compare function. At that point, the developer is required to start following the procedures outlined in section 4. The one exception is that during this phase the developer is continually in care and control of the code until the gatekeeper determines that the code has been moved to the post commissioning phase. Note that each PLC and PanelView is moved from the commissioning phase to the post commissioning phase on an individual basis.

When PLC or PanelView code is being developed and provided as part of a skid mounted or packaged equipment system, it is the supplier of the equipment that is the developer. Before the PLC or PanelView are in production, the developer is in care and control of the code. Once the Region’s Gatekeeper has made the determination that a PLC or PanelView is in production, they will add the code to Asset Centre and add the PLC code to the disaster recovery back up and compare function. Once this stage is reached, it will be the responsibility of the consultant’s SCADA staff on the project to check in and check out the code for the developer as per the paragraph above. The consultant will have care and control of the code until the Region’s Gatekeeper determines that the PLC or PanelView is moved from the commissioning phase to the post commissioning phase. Note that each PLC and PanelView is moved from the commissioning phase to the post commissioning phase on an individual basis.

### 6.2.2	Changes to the HMI Application

Developers are to do the HMI development work on their own computers. Whenever any HMI changes are put in production and are being used by operations, these changes must be deployed to all servers and work stations as per section 4.2.

## 6.3	Scenario 3 - Warranty Work

When the Region determines that the changes required to the PLC, PanelView or HMI code should be covered under warranty, the consultant will be contacted and informed what the problem is. The consultant will then follow the protocol defined in Section 6.1 Repair Work.

APPENDIX A DEFINITIONS

Developer – the person, people or company primarily responsible for making changes to the PLC, PanelView or HMI code.

Contractor – A contractor is a person or people whose services are recruited through a Work Order as opposed to a Capital Project.

Consultant – A consultant is a person or people whose services are recruited through a Capital Project or a minor capital work order. The majority of this work involves the development and commissioning of new PLCs, PanelViews and HMI programs or the addition of new equipment and/or process to existing PLCs, PanelViews and HMI programs. This work is much more involved than contractor type assignments and usually takes place over days, weeks or months.

OIC – The Operator in Charge at the plant who is responsible for organising and coordinating any work at the plant/facility on any given particular day.

In Production – The decision as to when a PLC, PanelView or HMI modifications are considered to be in production is made at the sole discretion of the Region’s Gatekeeper. Things that the Gatekeeper will consider when making this determination include but are not limited to:

- Has the SAT been completed?

- Is it connected to the SCADA network?

- Is the operator relying on it for operation of the plant/facility?

- Does the plant expect after-hours troubleshooting support from SCADA?

- Is it controlling or monitoring a process, piece of equipment or instrumentation?

- Will it be left running unattended?

Each PLC, PanelView or HMI modification can go into production on an individual basis. This is in no way tied to any formal phases of the delivery of a capital project.

Commissioning Phase – The period of time when equipment and or PLC code are being installed and tested onsite. During this time frame SCADA changes can either be in production or not in production. During this phase the developer is usually returning to site on a frequent basis to continue work.

The Commissioning Phase concludes once the bulk of the site set-up, configuration and tuning is complete and the developer is no longer required to return to site at least once per week. The vast majority of equipment and processes are running in auto mode.

Post Commissioning Phase – Begins immediately following the completion of the Commissioning Phase and generally lasts 1 year. During this period the developer is responsible for making changes to the PLC, PanelView or HMI code as required to provide proper operation of all equipment and processes as described in the approved Process Control Narrative. During this period the developer is to follow section 7.3

Repair Work - The majority of this work is minor changes and usually involves fixes, tweaks and small improvements to the system. There is not normally a commissioning phase associated with this type of work and equipment is considered to be in production at all times. This work is done by Regional staff or a Contractor.