Regional Municipality of Halton

SCADA Standards Manual

Appendix 5A CompactLogix Reference Guide

VERSION 2022

Table of Contents

5A.1	Overall Guidelines	1

5A.2	CompactLogix Hardware Selection	1

5A.3	CompactLogix Hardware Configuration	2

CompactLogix Built In Communication Port Configuration	2

General	2

Internet Protocol	3

Network	3

CompactLogix I/O Cards	4

Digital Input Cards	4

Digital Output Cards	6

Analog Input Cards	9

Analog Output Cards	13

List of Tables

Table 5A.1	CompactLogix Hardware Selection	2

Table 5A.2	Input Signal to User Counts for a 1769-IF4I module (CompactLogix)	13

Table 5A.3	Output Signal to User Counts for a 1769-OF4CI module (CompactLogix)	16

List of Figures

Figure 5A.1	CompactLogix Controller Properties - General Tab	2

Figure 5A.2	CompactLogix Control Properties -  Internet Protocol Tab	3

Figure 5A.3	Adding a New 1769-IA16 Module	4

Figure 5A.4	Selecting the 1769-IA16 Card	4

Figure 5A.5	1769-IA16 New Module Configuration	5

Figure 5A.6	1769-IA16 Connection Tab	6

Figure 5A.7	Adding a New 1769-OA8 Module	6

Figure 5A.8	Selecting the 1769-OA8 Card	7

Figure 5A.9	1769-OA8 New Module Configuration	7

Figure 5A.10	1769-OA8 Connection Tab	8

Figure 5A.11	1769-OA8 Fault/Program Action Tab	9

Figure 5A.12	Adding a new 1769-IF4I Module	9

Figure 5A.13	Selecting the 1769-IF4I Card	10

Figure 5A.14	1769-IF4I Module Configuration	11

Figure 5A.15	1769-IF4I Connection Tab	12

Figure 5A.16	1769-IF4I Configuration Tab	12

Figure 5A.17	Adding a new 1769-OF4CI Module	13

Figure 5A.18	Selecting the 1769-OF4CI	14

Figure 5A.19	1769-OF4CI Module Configuration	14

Figure 5A.20	1769-OF4CI Connection Tab	15

Figure 5A.21	1769-OF4CI Configuration Tab	15

Figure 5A.22	1769-OF4CI Limits Tab	16

Figure 5A.23	1769-OF4CI Fault/Program Action Tab	16

## Overall Guidelines

#### This section must be reviewed in conjunction with the other SCADA standards, specifically section 5.  As the software platform for ControlLogix and CompactLogix is the same, this Appendix is primarily focused on the hardware selection and configuration for CompactLogix.

#### This Appendix provides a reference to existing CompactLogix installations within Halton Region.  If a vendor wishes to use a CompactLogix PLC in their design, they must submit a standards deviation memo justifying their decision.  If approved the vendor is expected to supply enough spare parts to allow for full replacement of the PLC rack.

#### Halton Region requires the use of a ControlLogix platform in the following scenarios:

#### Any installation within a Water or Wastewater Treatment Plant.

#### More than one CompactLogix rack is required to meet the IO requirements.

#### The total CIP connection count exceeds 80% of the PLC’s supported connection limit.

## CompactLogix Hardware Selection

#### Consultants must use the following table when specifying CompactLogix hardware.

#### Consultants must be aware of the limitations to the power supply distance rating for I/O modules.

#### Consultants are required to specify the use of the latest hardware version.

| Processor Selection |  |  |
| --- | --- | --- |
| Model | Memory | Application |
| 1769-L36ERM | 3.0 MB User memory, 1GB non-volatile (SD). | All applications where called for in the platform selection criteria. |
| Power Supply Selection |  |  |
| Description | Module | Notes |
| CompactLogix Power Supply | 1769-PA4 |  |
| End Cap Module Selection |  |  |
| Description | Module | Notes |
| CompactLogix Right End Cap | 1769-ECR |  |
| CompactLogix Rack Extension Cable | 1769-CRL1, 1769-CLR3 | Consultants must seek approval from Halton Region to use remote racks with CompactLogix IO |
| Digital Input Module Selection |  |  |
| Description | Module | Notes |
| 1769-IA16 | 16 120 VAC digital inputs | All Digital Inputs |
| Digital Output Module Selection |  |  |
| Description | Module | Notes |
| 1769-OA8 | 8 120 VAC digital output | All Digital Outputs. |
| Analog Input Module Selection |  |  |
| Description | Module | Notes |
| 1769-IF4I | 4 isolated 4-20 mA analog inputs | All analog inputs. |
| Analog Output Module Selection |  |  |
| Description | Module | Notes |
| 1769-OF4CI | 4 isolated 4-20 mA analog outputs | All analog outputs. |

- CompactLogix Hardware Selection

#### The Consultant must take into consideration all provisions to ensure that adequate memory is available for current and future programming needs.

## CompactLogix Hardware Configuration

### CompactLogix Built In Communication Port Configuration

#### The processor configuration can be modified in RSLogix 5000/Studio 5000 by right clicking on the very top folder of the controller organizer labeled “Controller BXX1” and selecting “Properties”. Note that the base load PLC program will work on the ControlLogix and CompactLogix family of processors. The programmer must fill out the controller, I/O and Communications card configurations to suit the specific application.

#### CompactLogix controllers should be configured in the same manner as ControlLogix processors as documented in Section 5 of the SCADA Standards. The following sections document configurations unique to the CompactLogix platform.

### General

- CompactLogix Controller Properties - General Tab

#### Chassis Type: Does not apply to CompactLogix processors

#### Slot: Does not apply to CompactLogix processors

### Internet Protocol

#### While offline with the processor, the port configuration parameters are not available.

#### The card’s IP configuration is set using RSLinx.  Once the address is set, the programmer must go online with the processor either using the built in USB port or Ethernet and set the Port Configuration settings on the card.  Once on-line, right click on the new ENET card in the “I/O Configuration” folder in the project tree, and then select properties. The module properties dialog will re-appear with all of the fields in the Port Configuration tab available.  These settings must match those configured on the card using RSLinx.

- CompactLogix Control Properties -  Internet Protocol Tab

### Network

#### Use the Network tab of the Controller Properties dialog to configure settings for a Device Level Ring (DLR) topology. No configuration is required.

#### Work Area Outlets (WAO) on each remote I/O panel will be connected to the closest Network Distribution Enclosure. The NDE must not be more than 300 feet from the remote I/O panel.

#### Once all fields have been filled in, click the “SET” button to write the IP address and routing information to the 1769-L36ERM card. At this point, the programmer should be able to go online and monitor the PLC program over the Ethernet.

### CompactLogix I/O Cards

### Digital Input Cards

#### A 1769-IA16 card can be added to the Compact Bus by right clicking on the “CompactBus Local” icon beneath the “I/O Configuration” folder in the RSLogix 5000 project tree, and selecting “New Module…”

- Adding a New 1769-IA16 Module

#### Expand the “Digital” tree node in the “Select Module” window. Select the 1769-IA16 card and click the “OK” button.

- Selecting the 1769-IA16 Card

#### When the “New Module” configuration window appears, enter the following information on each tab

- 1769-IA16 New Module Configuration

##### Name: The card name consists of four fragments separated by the underscore “_” character. The first fragment is the PLC name (BXX1 in this case). The second fragment is Rockwell’s card type identifier (IA16 in this case). The third and fourth fragments are the rack and slot numbers for the card.

##### Description: The description must contain the PLC Name (BXX1), the number of points on the card (16 in this case), the operating electrical voltage/current of the card (120 VAC in this case), the data format of the card (Digital/Analog Input/Output), and finally the rack and slot numbers.

##### Slot: Enter the slot number for the input card.

##### Module Data: Click the “Change” Button, and fill in the module specific revision numbers. Select “Compatible Module” from the Electronic Keying drop down box. Click the “OK” button when complete.

- 1769-IA16 Connection Tab

##### Requested Packet Interval: Leave this box at 5.0 ms (default).

##### Inhibit Module: Leave this box un-checked

##### Major Fault on Controller If Connection Fails While in Run Mode: Leave this box un-checked

### Digital Output Cards

#### A 1769-OA8 card can be added to the Compact Bus by right clicking on the “CompactBus Local” icon beneath the “I/O Configuration” folder in the RSLogix 5000 project tree, and selecting “New Module…”

- Adding a New 1769-OA8 Module

#### Expand the “Digital” tree node in the “Select Module” window. Select the 1769-OA8 card and click the “OK” button.

- Selecting the 1769-OA8 Card

#### When the “New Module” configuration window appears, enter the following information on each tab

- 1769-OA8 New Module Configuration

##### Name: The card name consists of four fragments separated by the underscore “_” character. The first fragment is the PLC name (BXX1 in this case). The second fragment is Rockwell’s card type identifier (OA8 in this case). The third and fourth fragments are the rack and slot numbers for the card.

##### Description: The description must contain the PLC Name (BXX1), the number of points on the card (8 in this case), the operating electrical voltage/current of the card (120 VAC in this case), the data format of the card (Digital/Analog Input/Output), and finally the rack and slot numbers.

##### Slot: Enter the slot number for the input card.

##### Module Data: Click the “Change” Button and fill in the module specific revision numbers. Select “Compatible Module” from the Electronic Keying drop down box. Click the “OK” button when complete.

- 1769-OA8 Connection Tab

##### Requested Packet Interval: Leave this box at 5.0 ms (default).

##### Inhibit Module: Leave this box un-checked

##### Major Fault on Controller If Connection Fails While in Run Mode: Leave this box un-checked

- 1769-OA8 Fault/Program Action Tab

#### All items in this tab should be left in their default state. The Fault and Program mode output states must be set to “off”. During communications failure, the outputs must be left in Program Mode state.

#### Click on the “OK” button when all values have been filled in.

#### All digital output cards must use external relays. Relay output cards are not permitted.

### Analog Input Cards

#### A 1769-IF4I card can be added to the Compact Bus by right clicking on the “CompactBus Local” icon beneath the “I/O Configuration” folder in the RSLogix 5000 project tree, and selecting “New Module…”

- Adding a new 1769-IF4I Module

#### Expand the “Analog” tree node in the “Select Module” window. Select the 1769-IF4I card and click the “OK” button.

- Selecting the 1769-IF4I Card

#### When the “New Module” configuration window appears, enter the following information on each tab

- 1769-IF4I Module Configuration

##### Name: The card name consists of four fragments separated by the underscore “_” character. The first fragment is the PLC name (BXX1 in this case). The second fragment is Rockwell’s card type identifier (IF4I in this case). The third and fourth fragments are the rack and slot numbers for the card.

##### Description: The description must contain the PLC Name (BXX1), the number of points on the card (4 in this case), the operating electrical voltage/current of the card (4-20 mA in this case), the data format of the card (Digital/Analog Input/Output), and finally the rack and slot numbers.

##### Slot: Enter the slot number for the input card.

##### Module Data: Click the “Change” Button and fill in the module specific revision numbers. Select “Compatible Module” from the Electronic Keying drop down box. Click the “OK” button when complete.

- 1769-IF4I Connection Tab

##### Requested Packet Interval: Leave this box at 5.0 ms (default).

##### Inhibit Module: Leave this box un-checked

##### Major Fault on Controller If Connection Fails While in Run Mode: Leave this box un-checked

- 1769-IF4I Configuration Tab

##### All channels must be enabled, set to 0-20 mA range, 60 Hz filter, and “Raw/Proportional” Data format.

##### Click on the “OK” button when all values have been filled in.

#### The following table shows the Integer Value signal for a 1769-IF4I (CompactLogix) module for the corresponding tag element.

| Member Name | Signal Value (mA) | Data representation in Integer Mode | Description |
| --- | --- | --- | --- |
| SYS_AIT_OC | 0 mA | -32767 | Raw Value Open Circuit Limit |
| SYS_AIT_RANGE_MIN | 3.50 mA | -21845 | Raw Value Range Minimum. |
| SYS_AIT_RANGE_MAX | 20.5 mA | 31207 | Raw Value Range Maximum. |
| SYS_AIT_RAW_MIN | 4 mA | -20284 | 4ma signal value |
| SYS_AIT_RAW_MAX | 20 mA | 29646 | 20mA signal value |

- Input Signal to User Counts for a 1769-IF4I module (CompactLogix)

### Analog Output Cards

#### A 1769-OF4CI card can be added to the Compact Bus by right clicking on the “CompactBus Local” icon beneath the “I/O Configuration” folder in the RSLogix 5000 project tree, and selecting “New Module…”

- Adding a new 1769-OF4CI Module

#### Expand the “Analog” tree node in the “Select Module” window. Select the 1769-OF4CI card and click the “OK” button.

- Selecting the 1769-OF4CI

#### When the “New Module” configuration window appears, enter the following information on each tab

- 1769-OF4CI Module Configuration

##### Name: The card name consists of four fragments separated by the underscore “_” character. The first fragment is the PLC name (BXX1 in this case). The second fragment is Rockwell’s card type identifier (OF4CI in this case). The third and fourth fragments are the rack and slot numbers for the card.

##### Description: The description must contain the PLC Name (BXX1), the number of points on the card (4 in this case), the operating electrical voltage/current of the card (4-20 mA in this case), the data format of the card (Digital/Analog Input/Output), and finally the rack and slot numbers.

##### Slot: Enter the slot number for the input card.

#### When finished, click the “Connection” button to continue.

- 1769-OF4CI Connection Tab

##### Requested Packet Interval: Leave this box at 5.0 ms (default).

##### Inhibit Module: Leave this box un-checked

##### Major Fault on Controller If Connection Fails While in Run Mode: Leave this box un-checked

#### When finished, click the “Configuration” button to continue.

- 1769-OF4CI Configuration Tab

#### Click “Enable for each channel on the card, include future or spare analog outputs.

#### The Output Format should be 0mA to 20 mA.  This is the default setting.

#### The Data Format should be Raw/Proportional.  This is the default setting.

#### Leave Hold for Initialization unchecked.  This is the default setting.

#### When finished, click the “Limits” tab to continue.

- 1769-OF4CI Limits Tab

#### Each channel must be assigned a High and Low Limit.  The High Limit is to be set at 29369.  The Low Limit is to be set at -20341.

#### To set each channel, click on the Channel number tab.

#### When finished, click the “Fault/Program Action” tab to continue.

- 1769-OF4CI Fault/Program Action Tab

#### All channels should be selected to Hold Last State.  This is the default setting.

#### When complete click the “Ok” button.

#### The following table shows the Integer Value signals for a 1769-OF4CI (CompactLogix) module for the corresponding tag element.

| Member Name | Signal Value (mA) | Data representation in Integer Mode | Description |
| --- | --- | --- | --- |
| SYS_AO_RAW_MIN | 4 mA | -20284 | Raw Value Range Minimum. |
| SYS_AO_RAW_MAX | 20 mA | 29646 | Raw Value Range Maximum. |

- Output Signal to User Counts for a 1769-OF4CI module (CompactLogix)