Ferric Chloride System General Control Narrative

GENERAL

This control narrative is intended to be a general guide line on the control and operation of phosphorous removal systems at waste water treatment plants in Halton Region. Phosphorous removal is done through the addition of metal ions to the wastewater treatment stream at various strategic locations. The two metal ions that Halton Region uses are Aluminium in the form of Al+ and iron in the form of FE3+.  Through this document they will be referred to generically as metal ions.

This document provides the philosophy and details on pump control, storage tank level monitoring, storage tank concentration monitoring and reporting and dosage calculations. A more detailed narrative would need to be written for each individual plant addressing the specifics of that plant such as the number of pumps, number of dosage points, plant flow monitoring locations etc.

Halton Region’s SCADA Standards

It is anticipated that all of Halton Region’s SCADA standards would apply to all the equipment associated with the chemical system. As a result all the standard alarms for analog signals and device control would apply and therefore will not be restated in this document. The only alarms that will be listed are those that are process specific or are over and above Halton’s standards alarms.

PROCESS OVERVIEW AND EQUIPMENT

Each plant has 2 chemical storage tanks which feed multiple chemical feed pumps. There are 2 or more points that the chemical can be delivered to via the chemical feed piping system. Interconnections with valves between tanks and pumps allows both tanks to feed all  pumps and provides for 2 or more pumps to be able to deliver chemical to each individual dosage point. An inline flow meter measures the volume of chemical delivered to each individual dosage point.

Chemical Storage

Typically there are 2 storage tanks. Each tank has its own ultrasonic level indicator. The tanks current level in meters and volume in m3 is displayed on the SCADA system. At plants which use ferric chloride the current ferric concentration will also be displayed on the SCADA system. The standard analog control and alarms are available for all of these analog signals.

Ferric Chloride Concentration

Each load of ferric chloride has a different concentration. The new load is added to the storage tank which already has ferric chloride in it at a given concentration. This blending produces a new unknown concentration of ferric chloride in the storage tank.

The SCADA systems determines the concentration of the blended ferric chloride in each of the storage tanks based on parameters entered by the operator at each tank fill. The operator can recalibrate current concentration at any time by entering in the new concentration through the SCADA system. This change will take effect immediately but will not impact any historical data.

When a tank is filled, the SCADA system will automatically detect that the tank has been filled. A Tank Fill pop-up window will pop-up on the SCADA system. The window will indicate what the tank volume was at the start of the fill, what the volume was at the end of the tank fill and what the volume added to the tank was. The operator will be able accept these values by doing nothing or can over write the values. The operator would then enter in the specific gravity and concentration of the newly received ferric chloride and then press calculate. The SCADA system would then calculate the concentration of the ferric chloride in the tank. The volume added to the tank would then be reset to zero until such time that the SCADA system detects that a load of chemical has been received.

If the SCADA system detected that the tank was filled in error, the operator can click the deny button on the Tank Fill pop-up window. This action would then reset the volume received value to zero, maintain the existing ferric chloride concentration, and close the pop-up window.

The calculation will be as follows;

VOLUME

Post Fill Volume m3	– 	Pre-fill Volume m3 	= 	Received Volume m3

(Post Fill Level * Tank Area)		(Pre-Fill Level * Tank Area)

CONCENTRATION

Kg iron in Pre-filled tank + 	kg iron in Received volume    =	Concentration of Post Filled Tank

(Concentration *volume)		(Received volume *S.G.* % Conc.)

Ferric Storage Tank Concentration Determination

How will we determine if a load has been received?

If at any time the current ferric concentration is incorrect and needs to be changed, the operator can simply click on and change the value. This will require supervisor level access and the SCADA system will ask for confirmation before over writing the value.

PUMP CONTROL

Pump Stroke Length

The pump stroke length is always a manually adjusted locally at the pump. It does not have a local or remote mode and is independent of the Local/Remote selector switch. At some locations the stroke length is displayed on the SCADA system but it is for display only and there is no control of the stroke length via the SCADA system.

Local Mode

Each pump has its own Local/Remote selector switch. In local mode the pump speed can be adjusted at the pump by the operator. The speed cannot be controlled from any other location. All dosage and flow reporting calculations done by the SCADA system would continue to function but the automatic control would not.

Plt-Manual Mode

Plt-Manual mode is selected by first putting the Local/Remote selector switch into Remote and then putting the pump into Plt-manual on the SCADA system. In Plt-Manual mode the pump speed can be adjusted from the HMI. All dosage and flow reporting calculations done by the SCADA system would continue to function but the automatic control would not.

Plt-Auto Mode

Plt-Auto mode is selected by first putting the Local/Remote selector switch into Remote and then putting the pump into Plt-Auto on the SCADA system. In Plt-Auto mode the pump speed is controlled automatically by the PLC. For details on how the pump speed is controlled, see the section on Dosage Control.

Operator

Can’t select the same pump for more than one dosage point

Need to know which pumps can service which dosage points and build the selection screen appropriately.

DOSAGE CONTROL

For each dosage location (see section X.X for more details) one of two modes can be selected via a radio button on the HMI. They are Time-paced and Flow-paced. For either mode to function automatically, the respective pump must be in Plt-Auto.

Time-paced dosing control will use an operator selected dosage ratio in millilitres of ferric chloride per minute (ml/min) as the input parameter, with a feed back control algorithm based on inline chemical flow measurement. The selected pump must be in Plt-Auto for the

Flow-paced dosing control will be based on an operator selectable dosage ratio in kilograms of metal ion per mega litre (MLD) of plant flow, using plant flow as the input parameter for a feed-forward control algorithm. This algorithm will look at which tank the chemical is coming from and use that tanks concentration to calculate out the instantaneous dosage rate. The instantaneous value and the dosage set point will be displayed on the HMI and will also be compared to each other. If the 2 values deviate by more than 5% for more than 2 continuous minutes and dosage set point deviation alarm will be generated.

The flow-pacing control mode will have an operator selected maximum and minimum plant flow rate (MLD). The intention of the maximum plant flow range is to prevent overdosing of iron when experiencing high diluted flows due to weather events. When the plant flow exceeds the maximum plant flow set point value the control algorithm will function to maintain the selected dosage ratio, above which the dosage (kg) will remain constant, until the flow (MLD) returns to the variable range.

The intention of the minimum plant flow range is to prevent air locking of the pump or solidification of the chemical at low flow rates. When the plant flow drops below the minimum plant flow set point value the control algorithm will function to maintain the selected dosage ratio, below which the dosage (kg) will remain constant, until the plant flow (MLD) returns to the variable range.

DOSAGE LOCATION

Halton Region uses a philosophy of chemical dosage locations. The idea is that the chemical can be dosed or applied to one or several locations at the same time. To control and measure the chemical dosage each dosage location requires a dedicated pump, chemical flow meter, feed piping, a plant flow signal and an automatic control mode (time-paced or flow paced).

For redundancy purposes each dosage location can be serviced by multiple pieces of equipment. To properly control and measure the chemical dosage the SCADA system needs to know which dosage location each piece of equipment is serving. This information is provided by the operator by manually entering it into the SCADA system. Improper entry of this information will cause incorrect control and measurement of chemical dosage.

The SCADA system will check the operator’s selections to make sure they are valid. The system will ensure that that each pump and each flow meter is only selected for one dosage location. It will also ensure that time paced dosage ratio, the flow paced dosage ratio, the maximum flow value and minimum flow values entered by the operator fall between their respective ranges.

Most plants dose chemical to both the primary and secondary clarification stages of the plant. Each of these stages can have multiple locations to where the chemical is added. Individual chemical feed pumps are usually dedicated to one specific dosage location with one pump serving as a stand-by for multiple dosage locations but each of the exact details are plant specific.Each of these dosage locations will have its own dedicated chemical flow meter as well as its own plant flow signal. The Plt-Auto dosage control mode (Time paced or Flow paced) can also be selected by the operator for each individual dosage location. Table 1 below outlines all the program variables that the operator must select for each dosage location using the HMI.

Table 1

| Item | Units | Description |
| --- | --- | --- |
| Chemical flow meter | ml/min | Flow rate of ferric chloride to a dosage location |
| Pump |  | Select the pump for the dosage location |
| Mode |  | Time paced or flow paced |
| Time paced dosage ratio | ml/min | millilitres of ferric chloride per minute |
| Flow paced dosage ratio | kg/MLD | kg of iron per mega litre of plant flow |
| Plant flow value | MLD | This is plant flow value to which the pump speed will be paced to for a given location. |
| Dosage location | Primary/Secondary | This is the location to which the chemical will be pumped to |
| Maximum plant flow value | MLD | This is the maximum flow rate too which the pump will pace too |
| Minimum plant flow rate | MLD | This is the minimum flow rate too which the pump will pace too |

In order for the control and reporting system to work properly the operator must first set all the valves correctly and then select the appropriate program variables on the HMI.

PUMP DUTY ROTATION

Valves between the pumps and dosage points are manual. As a result all duty rotation of pumps is manual. When changes are made the operator must also manually update the dosage point, as well as the controlling plant flow meter by entering this information into the plant HMI.

Additional Alarms

This section details the alarms that are process specific and are over and above the standard Halton Region alarms.

Pump Speed deviation alarm – This alarm will be activated if the pump speed feed back deviates by more than 5% from the set point for 30 continuous seconds.

Flow paced dosage ratio 5% deviation alarm. This alarm will be activated if dosage ratio set point and the instantaneous dosage ration values deviate by more than 5% for more than 2 continuous minutes.

Chemical storage area flood alarm

Pump running but no flow detected – This alarm will be activated if a pump is running but the respective flow meter is recording less than X ml/min for 30 continuous seconds.

REPORTING AND TRENDING

All analog signals whether real or virtual will be trended.

Instantaneous Values displayed on SCADA

Dosage point X chemical flow rate (ml/min)

Dosage point chemical dosage (kg/MLD or mg/l- Steve to provide direction)

Tank Level (m)

Tank Volume (m3)

Tank Concentration (mg/l, or % - Steve to determine)

Plant Flow (all locations recorded)

Daily Report (midnight to midnight)

Dosage point X Average Chemical Flow Rate (ml/min)

Dosage point X Average Chemical Dosage Rate (mg/l)

Dosage point X Chemical Volume Dosed (m3)

Dosage point X Mass of metal ion dosed (kg/day)

Tank 1 Volume used (m3)

Tank 2 Volume used (m3)

Total Tank Volume used (m3)

Mass of metal ion dosed (kg/day) (based on the volume of both tanks)

Monthly Reports

Volume (m3) based on both tanks

Total Mass of metal ion dosed (kg) based on both tanks

Dosage (kg/m3) (based on monthly volume and mass from tanks)

PLC TO PLC DATA EXCHANGE

Typically all the chemical pumps and associated equipment are connected to one PLC. The plant effluent flow meters and possibly the chemical dosage rate flow meters maybe connected to a different PLC and therefore this data would need to be read by the chemical PLC from the other PLC(s). The chemical PLC will also need to determine if any of the flow meters connected to a different PLC have failed by monitoring the signal error bit within the respective PLC.

Do we want to add all the flow meters together?

FAILURE SCENARIOS

Plant Flow Meter Failure

If a plant flow meter fails a Signal Error Alarm will be generated and all dosage locations that are using that plant flow meter for its dosage algorithm will maintain last state meaning the pump speed will no longer change based on plant flow until the plant flow meter Signal Error Alarm is acknowledged and reset. All dosage and reporting calculations would continue based on the last good value of the plant flow meter.

Chemical Dosage Flow Meter Failure

If a chemical dosage flow meter fails a Signal Error Alarm will be generated and all dosage locations that are using that chemical dosage flow meter for its dosage algorithm will maintain last state meaning the pump speed will no longer change based on the feed back from the meter until the chemical flow meter Signal Error Alarm is acknowledged and reset. All dosage and reporting calculations would continue based on the last good value of the chemical dosage flow meter.

PLC Failure

If the PLC controlling the chemical system fails the 4-20-mA output to the pumps would drop to zero causing the pumps to stop. All dosage and reporting calculations would stop functioning as well and Null values would be recorded in the InSQL server database.

Chemical Pump Failure

If a chemical pump fails and stops a Chemical Pump Uncommanded Stop alarm would be generated. If the pump was in Plt-Auto and the dosage location selected to Flow paced dosage ratio mode, a Flow paced dosage ratio 5% deviation alarm would also be generated. The SCADA system would not take any action and the operator would have to select another pump or repair the failed pump in order to resume dosage to the location. All dosage and reporting calculations would continue for the particular dosage location.

PLC Communications Failure

If the chemical system PLC detects a communication failure between its self and any of the other PLCs that it is collecting data form, a PLC to PLC communication alarm will be generated, The control algorithm(s) would continue to function based on the last know good value(s) from the PLC to which it lost communication.