Regional Municipality of Halton

SCADA Standards Manual

Section 1 General Requirements

SCADA STANDARDS 2022

Table of Contents

SECTION 1 GENERAL REQUIREMENTS	1

1.1	Introduction	1

1.2	Abbreviations	1

1.3	Enforcement of the SCADA Standards	2

1.4	Control Narrative Template	2

1.5	Applying the Standards Documents	2

1.6	SCADA Expansion Protocol	3

1.7	Brown Field PLC Transition Protocol	3

1.8	Historian Tag Migration Protocol	4

1.9	Programming Guidelines	5

1.10	Summary of Stakeholder Deliverables	5

1.11	Shop Drawing Review	8

1.12	Gatekeeper Protocol	8

1.13	Electronic File Naming Convention	8

1.14	SCADA System Architecture Overview	8

1.15	SCADA Control Hierarchy	10

1.16	SCADA Device Control Modes	12

Degree of Automation	12

1.17	I.P. Addressing Structure	13

Multiple Rack Applications	13

1.18	Integrated Vendor Packaged Equipment	13

Overall Guidelines	14

Consultant’s Responsibility for Vendor Packaged Equipment	14

Vendor’s Responsibility for Vendor Packaged Equipment	15

1.19	Standard Process Narratives and Control Narratives	17

1.20	Drawing Order and Organization	18

1.21	Standard Drawings	18

Drawing Guidelines	19

Pump Control Schematics	19

Appropriate Pump Control Selection	20

Valve Control	20

SCADA Monitoring Requirements	20

1.22	Halton’s Network Architecture Drawings	20

1.23	Modifications to Standard Drawings	21

Typical P&ID Drawing	21

Standard Motor Control Drawings	21

Standard Valve Control Drawings	21

Standard Control Panel Layout	22

Control Panel Power Distribution Drawings	22

Loop Drawings	22

Appendix 1A – Gatekeeper Protocol	23

Appendix 1B – Standard SCADA Drawings	24

Appendix 1C - Standard Process and Control Narratives	25

List of Tables

Table 1.1	SCADA Stakeholders & Deliverables	7

Table 1.2	SCADA Control Mode	12

Table 1.3	I.P. Addressing Structure	13

Table 1.4	Multiple Local Rack ControlLogix PLC I.P. Addressing Structure	13

List of Figures

N/A

# GENERAL REQUIREMENTS

## Introduction

#### Halton Region has developed this SCADA Standards Manual for use by Consulting Engineering firms, Regional staff, and any other persons involved in the implementation of the SCADA portion of any water, wastewater, and solid waste capital works and maintenance projects. The focus of the SCADA Standards Manual is to define Halton Region’s design philosophy and preferences.

#### Any references to specifications will discuss only the format and tender document structure.  The consulting engineering firms are still expected to use their individual tender specifications and drawings for all Halton Region tenders.  Therefore, the overall responsibility for the quality of the design squarely remains with the designers.

#### The standards and guidelines stipulated in this manual are mandatory. Project constraints, such as the physical space available for new equipment, or process specific applications, may force the designers to deviate from Halton Region’s preferences.  The concept proposed is for the designers to follow the guidelines as much as possible.  They must also use good engineering judgment to provide a cost-effective solution.

#### In situations where the designers have intentionally deviated from the document, they should provide a Standards Deviation Memo with their submissions indicating the deviations that were taken, and their justification.  This will aid the reviewers by focusing their review efforts in the high priority areas.  The “standards deviations” memo also serves as an effective tool for defining and recording the deviations as part of the project documentation process.

#### For each SCADA Upgrade project, the designer must determine whether the new, published SCADA standards, or the original design standards, should be followed. Halton Region’s preference is to utilize the current SCADA standards whenever possible. In very minor SCADA projects, such as adding less than 10 new I/O points, or a minor PLC software change, it may be more prudent to simply follow the existing standards. The designer must review the two options, and if the recommendation is to simply adhere to the existing standards for a small scale project, then a Standards Deviation memo must be immediately submitted at the beginning of the project for Halton Region’s review and potential acceptance.

#### This SCADA Standards Manual is one within a series of Halton Region Design Standards and Guidelines. The manual herein is complemented by the other following documents:

###### Water and Wastewater Facilities Design Manual

###### Water and Wastewater Linear Design Manual

###### Consultants Procedures Manual - Facilities

###### CAD Standards for Linear Design Drawings

#### This SCADA standards manual is focused on the technical details related to SCADA hardware and software. The project team must also closely review and follow the Consultant’s Procedures Manual, which describes how to deliver a capital project within Halton Region.

## Abbreviations

CAD		Computer Aided Design

FAT		Factory Acceptance Test

GUI		Graphical User Interface

HMI		Human Machine Interface

ICP		Instrumentation Control Panel

ISA		International Society of Automation

LAN		Local Area Network

MCC		Motor Control Centre

MOECP	Ministry of the Environment, Conservation & Parks

OIC		Operator in Charge

OHSA		Occupational Health and Safety Act

OIT		Operator Interface Terminal

P&ID		Process and Instrumentation Drawing

PLC		Programmable Logic Controller

QA		Quality Assurance

QC		Quality Control

SAT		Site Acceptance Testing

SCADA		Supervisory Control and Data Acquisition

WAN		Wide Area Network

WHMIS		Workplace Hazardous Material Information System

## Enforcement of the SCADA Standards

#### Enforcement of the standards is a key component of the standards management process.  Halton Region staff recognizes that it is a very onerous task to attempt to identify differences between a design submission of perhaps 100-300 drawings and a 200-400-page specification versus a +200-page SCADA Standards Manual.

#### For this reason, it is recommended that the designers submit attached to their design submissions, the Halton Region Standards Deviations memo.  This approach will substantially reduce the effort required by Halton Region staff when reviewing design submissions and enable them to focus on the critical review areas.  It will also ensure that the designers are aware of, and have considered, the SCADA Standards Manual.

#### If approval of the Standards Deviation is not received prior to proceeding, the project team is responsible for any cost and schedule impacts of re-completing the work to the standard.

#### For each project, a key issue is to define, within Halton Region’s organization, the point person(s) for enforcement on each project.  The responsibility for enforcement will be led by Halton Region’s project manager, with support from one common SCADA group member within the Halton Region organization.

## Control Narrative Template

#### The Region’s standard control narrative template is in Appendix 1C.

#### This template is to be used as the starting point for the development of a Control Narrative. The sample narrative provided has some references to the Oakville South East WWTP which are used for example. The narrative is also written in generic terms in other areas. Some sections are not complete, but the heading and some content are provided as a sample.

#### The narratives are to be written as they would read when the project is complete. The consultant should not use terms like the “the future aeration tanks, or “the existing aeration tanks” or “when the upgrade/expansion is complete, the blower will …”.

## Applying the Standards Documents

#### Halton Region’s SCADA standards have been divided into separate documents for ease of use and navigation.  The documents are written at a level that can be utilized by anyone.  Some of the content presented may not apply to a specific application.

#### When starting a project, the Consultant should review the documents in the order they are presented.  The documents are presented in the order in which the Consultant will require them.

#### Wastewater Pumping Stations have very specific design standards.  If the Consultant is designing a new Wastewater Pumping station, they should specifically refer to Section 8, “Wastewater Pumping Stations”.  This contains sample Control Narratives, sample contract drawings, source PLC and HMI code.  Consultants are still required to conform to all standards presented in the SCADA Standards Manual and should always contact the SCADA group for the latest base load PLC and HMI programs.

## SCADA Expansion Protocol

#### As Halton Region has constructed more SCADA systems, the approach (protocols) and roles and responsibilities have evolved. The following describes the typical SCADA projects and the related roles and responsibilities.

#### SCADA projects can be separated into three different types.  These are:

##### Major Controls Upgrade or Expansion

##### Minor Controls Upgrade

##### Maintenance Upgrade

#### Major control upgrades or expansions typically involve a major change to the SCADA system. This occurs as part of a major plant upgrade or expansion and will likely involve the addition of new PLC’s and/or computers. As such, it is more complex as the base PLC program must be created, as well as the project specific requirements. In general, these are completed with the support of external engineering firms. To complete this work, the designers must carefully review and adhere to all the SCADA standards.

#### A minor controls upgrade is work that does not require a new PLC.  It may involve the replacement of existing equipment with newer equipment that will operate using the existing PLC program; or operate with minor changes to the existing PLC program. In general, these are completed with the support of external SCADA programming resources.

#### A maintenance upgrade is identified as an upgrade that is minor in nature, and generally is led or completed by Regional SCADA or maintenance staff. In these cases, Halton Regional staff will take on the responsibilities of the PLC and HMI programmer, as well as the consulting engineer, so that at the end of the project, all of the required documentation is created.

## Brown Field PLC Transition Protocol

#### The commissioning of upgraded systems or facilities, wherein one or more PLC’s are replaced, may require that an existing PLC be temporarily maintained on the network alongside its replacement.

#### In these cases, when initially installed on the SCADA network, the programmer will append the new PLC name with “_1”. Halton Region staff will assign a temporary I.P. address.

#### A similarly named InTouch Access Name and DAS Server Topic will be configured for temporary use. See Sections 6.48, Polling Setup and 6.60 and DAS Server Configuration respectively, for details.

#### Modify the respective process window(s) to show the temporary name and IP address of the PLC as shown in the example below. The status of both PLCs will remain on the window(s) until the old PLC is removed from the network. If the communications status for the existing PLC does not exist on the respective process window(s), then the Programmer needs to set it up and configure this for BOTH the old PLC and the new PLC

- Figure 1.0 – Examples of PLC Naming Convention for PLC Replacement Projects

#### If the type of PLC is being changed (i.e. from SLC to ControlLogix), upon decommissioning of the existing PLC, the Programmer is to remove the existing DAS Server Topic. If the type of PLC is the same, then the DASABCIP server topic does not need to be modified since the new PLC will have the same IP address as the old PLC.  The DASABCIP topic will point to the new PLC.  The InTouch access name will remain the same, but the properties of the access name may need to be modified to match the appropriate DAS server for the type of PLC (i.e. the application name will change from DASABTCP to DASABCIP, for PLC-5 or SLC500 to ControlLogix upgrade).

#### The PLC will be reassigned to the existing I.P. address. The Programmer will coordinate this work with Operation Staff and inform Halton Region when the Temporary I.P. address is no longer in use. At this point, the Programmer must edit the respective process window(s) to remove the temporary information on the PLC communications. The Programmer must update the Communication Map window, the Plant SLC Process Status window and the Plant Logix Process Status window by removing the old PLC information and adding the new PLC information where applicable.

#### At this time, the Programmer is to confirm functionality of the process trends and callouts.

## Historian Tag Migration Protocol

#### The Region of Halton has suspended the activity of giving existing tags, new tagnames. The Consultant should not be renaming any tags without consulting the Region SCADA staff first.

#### In cases where processes and/or PLC(s) are upgraded, existing HMI tags may need to be modified. This is typically a result of updating tagnames from older tagging standards to the latest available tagging standard. Tags may also be changed to reference a different PLC name or be moved to a different application entirely.

#### To ensure that no historical process data is lost, the migration must be planned in advance and the SCADA Programmer must be scheduled to be available during the migration. The plant processes that are being worked on should be shut down.  The new tag must be brought on-line and be imported into the historian before the old tag is taken offline. Once the new tag is in the Historian, the equipment can be switched over to the new tag.

#### The programmer is required to promptly provide the Halton Region SCADA Programmer with documentation of the affected logged tags. This includes a cross reference of the existing tagname with the new tagname. With this information, the SCADA Programmer will migrate the existing data from the old tagname to the new.

#### If the affected tags are referenced by pre-configured trends, the programmer will be required to provide a new set of trend group buttons alongside the existing buttons which will remain until the migration is complete. Consistent to the temporary naming used for the brown field transitions, described in Section 10.23 – “Brown Field PLC Transition Protocol”, the programmer will append the new trend group button labels with “_1”.

#### When the tag migration is confirmed to be complete, the programmer will remove the old tags and trend group buttons from the application. At the same time the new trend group labels will be updated to remove the temporary “_1” identifier.

## Programming Guidelines

#### The programming, setting up, and maintaining of Routers and Networks Switches is performed by the Region’s Information Technology Services department.  Should consultants require these pieces of equipment adjusted, they should make arrangements with the SCADA group.

#### The programming of VFD drives is performed by the Manufacturer, or an authorized representative, during the equipment startup.  During maintenance activities, should consultants require these parameters adjusted, they are required to notify Halton Region in writing. Consultants are required to arrange for qualified personnel to update the VFD parameters.

#### The programming and configuration of field instrumentation is performed by the contractor during startup.  During maintenance activates, should consultants require these parameters to be adjusted, they are work with the SCADA Gate Keeper who will arrange with maintenance personnel to have the parameters changes and the proper documentation updated.

## Summary of Stakeholder Deliverables

#### This section should be read in conjunction with the other manuals.  In general, each stakeholder is responsible for, but not limited to, the following tasks and deliverables.

| Stakeholder | Key Tasks & Deliverables |
| --- | --- |
| Halton Region SCADA Group and Technology Services | - Specification, coordination, and management of the installation of any new telephone circuits and other related wide area and in plant communication components - Provide all computer and server hardware - Load the purchased software applications on any new computer hardware - Review the relevant shop drawing sections - Complete the initial computer setup including I.P. address - Add and/or modify the tagnames for Wonderware Historian server for each specific project - Coordination of software versions using the Gatekeeper protocol - Maintaining all SCADA standards - Review all draft and final documents prepared by the designers - Confirm all work is completed in accordance with the SCADA standards - Final approval for all FAT and SAT testing - Final approval and acceptance of projects, for turnover to Regional Staff - Regional staff to participate in the testing and commissioning of new SCADA expansions, in order to coordinate changes in facility operation required to accommodate the testing - Receive updated documentation for all work completed - Placing all workstations and servers onto Halton Region’s Domain - Managing the Active Directory users groups for domain security |
| Consulting Engineer | - Preparation of the P&ID’s and field wiring drawings – both Detailed Design and Record (as-built) versions - Preparation of the Process Narratives – both design and record (as-built) versions - Submits and coordinates concurrent shop drawing review with the SCADA group - Review of the PLC & HMI Software Programmer’s Control Narrative - Merges the PLC & HMI Software Programmer’s Control Narrative with the Control Narrative for the plant, so that there is only one document. - In some cases, the drawings will consist of updated existing drawings - In most cases, the Process Control Narrative will consist of updating the existing narrative or using an existing narrative as the template for the new narrative - Specifying that all pre-packaged systems also comply with the SCADA standards, then checking during construction - Lead the FAT and SAT’s related to the pre-packaged systems, which are generally programmed by the supplier - Site inspection confirming that all construction is completed in accordance with the contract specifications and drawings - Quality control check of field work to ensure that all I/O wiring has been verified and field instruments have been verified, calibrated, and are operational - Safety checks of field work to ensure that all onsite contractors are following safety protocols and performing their work in a safe manner - Attend the FAT and SAT to verify that the software and hardware meets the intent of Halton Region’s SCADA standards. - Provide all as-built narratives and drawings - Training on process logic |
| SCADA Contractor | - Construction of SCADA works in accordance with the tender documents - Installation and commissioning of new field instrumentation - Inspection and confirmation that all field work is completed and finalized prior to initiating the SAT activities. This includes verifying the field instrument calibration ranges and wiring to the PLC. |
| PLC & HMI Software Programmer | - Creation of the Control Narrative based upon the Consulting Engineer’s Process Narrative - Installing Halton Region’s standard base SCADA applications - Selecting which standard software modules match the new equipment - Completing all other required, related programming of PLC’s - Lead the FAT and SAT activities - Set-up and configure all devices that connect to the Ethernet network unless they are set-up by Halton staff - Completing all other project specific programming of SCADA database, trends, historical data collection and reporting. - Supplemental programming such as Auto dialers - SCADA Training |

- SCADA Stakeholders & Deliverables

## Shop Drawing Review

#### The Consultant will forward a list of all shop drawing sections to the SCADA group.  Based upon this list, the SCADA group will provide the Consultant with a list of sections the SCADA group chooses to review, in addition to the Consultant’s review.

#### The Consultant will incorporate their shop drawing review comments with the SCADA group’s comments to ensure that the Contractor receives concurrent shop drawing review comments.  The consultant may be required to schedule a separate meeting with the SCADA group to coordinate the comments.

#### The process of submitting requested shop drawings to the SCADA group and performing a concurrent review applies to each shop drawing submission until both the Consultant and the SCADA group are satisfied with the shop drawings.

## Gatekeeper Protocol

#### The Gatekeeper Protocol is a key component of Halton Region’s strategy for the proper management of SCADA software. All programmers must fully adhere to this protocol. Refer to the Appendices for the Gate Keeper Protocol.

## Electronic File Naming Convention

#### Halton Region has established a SCADA electronic file naming convention; it is the Consultant’s responsibility to follow this naming convention.

#### PLC Program File Naming is identified in Section 5.

#### HMI Applications are named after the plant that the application is installed in.

#### Control Narratives are named after the Plant and Process area or the Station the narrative has been created for.

## SCADA System Architecture Overview

#### Halton Region has SCADA systems at almost all Water, Wastewater, Solid Waste and Biosolids facilities.  Each Plant or System has a separate SCADA application that operates independently of the other SCADA Systems. The following is an overview on the various components of each SCADA system.  Although each system is unique, all the systems have been designed using common standards to provide a similar “look and feel” from facility to facility.  More detailed information is available in other sections of the SCADA Standards Manual.  The information presented in this section is to provide the Consultant with a System Overview.

#### Field Controllers

##### Halton Region has standardized on Allen Bradley field controllers.  Halton Region has SLC’s, CompactLogix and ControlLogix Field controllers in service.

##### Halton Region has standardized on installing ControlLogix PLC’s for all new installations.

##### SLC’s are currently in service at most plants.

##### All field controllers have a standard I/O layout, and specifications for standard I/O modules.

#### Instrumentation Control Panels

##### Halton Region has standards for instrumentation control panels which house the field controllers.  These standards apply to all new panels supplied as either a PLC panel for a new process, or as part of a Vendor supplied packaged piece of equipment. These drawings need to follow the following order.

###### PLC panel layout

###### Power distribution

###### Processor and Ethernet cards

###### DI drawings

###### DO drawings

###### AI drawings

###### AO Drawings

###### Network Architecture Drawings

#### SCADA Computers

##### Halton Region has standardized that one (1) SCADA workstation is installed in the Plant Control room.  The SCADA workstation communicates with the SCADA servers for alarm distribution, and SCADA data. The reasoning for the one workstation is to act as a failsafe option to the thin clients in the event that the terminal server fails. This workstation will allow the operations to monitor and make adjustments to SCADA if the terminal server fails rendering the thin clients inoperable.

##### SCADA Thin clients

##### Halton Region has strategically placed SCADA thin clients throughout each facility.  Placement of SCADA thin clients throughout each facility allows operations to make process adjustments while in the field.  Consultants are required to review the location of any new SCADA Thin clients with the SCADA group.

#### SCADA IO Polling Servers

##### Halton Region installs two (2) SCADA servers for each InTouch application.

##### The SCADA servers are configured to provide distributed alarming, including hot backup.

##### The Wonderware DAS or OI (Operations Integration) Servers are installed on both SCADA servers and poll all field controllers for data.

##### All SCADA computers, thin clients and RDP server access the servers for data and alarms.

##### Consultants should not need to install SCADA servers, unless a new facility is being constructed.

##### SCADA Terminal Server

##### Halton Region normally installs one (1) SCADA Terminal Server per plant. The exception is Water Distribution and Wastewater Collections that have two (2) Terminal Servers installed at 2 different locations.

##### Water Distribution and Wastewater Collection’s RDP servers are installed at Mid Halton WWTP and Burloak WPP.  The extra server is provided since this system is geographically large and provides redundancy should one plant network connection be lost, the other server can provide the SCADA information.

##### The Terminal Server has ACP Thin Manager installed that is used to configure and manage the thin clients. The Terminal Server is to provide SCADA sessions to the thin clients with the same functionality of the SCADA workstations.

#### SCADA Historians

##### Halton Region has two dedicated Historian servers installed at Halton Regional Headquarters.  One server, “SCADA1” is dedicated for Water Treatment and Water Distribution.  The other server “SCADA2” is dedicated to Wastewater Collection, Wastewater Treatment, Solid Waste and Biosolids.  The servers collect and store all historical SCADA data.

##### Consultants will not need to install or update the SCADA Historians.  When making changes to the SCADA system, the programmer is required to follow the Gate Keeper Protocol which outlines the process for having the historians updated.

##### The Region also monitors the enabling/disabling of alarms and alarm setpoint values for critical equipment in the water plants and water distribution system.  If the work being completed includes adding, deleting, or modifying equipment whose InTouch alarm priority is between 1 and 10 (specific Critical Compliancy), the consultant will notify the Region of the change and send a list of the affected tags.

#### Field Communication

##### Halton Region utilizes Ethernet as their SCADA communication protocol.  This is used for all SCADA communications.

##### Halton Region has standards on fiber optic and Ethernet cables, as well as network cabinets and media converters.

##### Consultants and OEM equipment Vendors should contact Halton Region when they wish to use ControlNet by using the standards deviation memo.  Ethernet is Halton Region’s primary protocol for all communication requirements. The standards deviation memo must be approved before ControlNet can be used.  Halton Region’s preference is to not use ControlNet, or any other fieldbus type communication protocols.

#### WAN Communications

##### Halton Region has remote connections to some of their Wastewater Collection facilities, and all their Water Distribution facilities.  These communications are set-up and maintained by the Region’s Information Technology group, through the use of Third Party providers.

##### The remote locations that are connected to the WAN are polled by the SCADA servers.

## SCADA Control Hierarchy

#### Halton Region’s SCADA Control Hierarchy has three levels. The Figure 1.1 below shows the control philosophy from the field device level to the Wonderware InTouch HMI Interface.  These levels are:

##### Level 2- Plant

##### Level 1- PLC

##### Field

#### The highest level of control is the Plant level.  At the plant level the Operator can start/stop equipment, change operating speeds and duties using the Plant’s Wonderware InTouch graphics.  Commands from the Plant Level HMI are passed down to the PLC level.  Any computer or thin clients connected to Halton Region’s Wide Area Network (WAN) running a copy of the Plant’s Wonderware InTouch HMI Interface can also start/stop equipment, change operating speeds and duties.  The Plant’s Wonderware InTouch will read any changes made through the WAN.  The same is true that any InTouch application connected across the WAN will update when changes are made by the operator at the Plant.

#### The next level of control is performed at the PLC level.  This level of control is applied to any device that has its selector switch placed in the Remote position.  The starting and stopping of the device is controlled by the PLC.  Any hardwired interlocks from the field, such as backup hardwired control only function when the switch is in the remote position.

#### The first level of control is in the field.  This level of control applies to any device that has its selector switch placed in the Local position.  The device can only be operated at the device MCC, or area control panel.

#### From a control’s priority perspective, control is passed upwards. At each level, starting at the field level, the user can allow control to be passed upwards by the related (hardware/software) selector switch.

Figure 1.1 SCADA Control Hierarchy

## SCADA Device Control Modes

#### Halton Region utilizes three SCADA device control modes.  The following table identifies each control mode that must be provided for any device that can be controlled by the PLC.

| Level | Description |
| --- | --- |
| LOCAL | The selection of LOCAL or REMOTE mode of operation is typically made by an operator at the device, MCC, or area control panel by means of a 2 position “make before break” selector switch. In LOCAL mode the device can be controlled by pushbuttons in the field. Switching from REMOTE to LOCAL will provide a bumpless transfer of device operation. |
| Remote Control Modes |  |
| PLT-MAN | The selection between PLT-MAN and PLT-AUTO is based upon the last selection made at any of the workstations in the SCADA network or the local Operation Interface Terminal (OIT). Switching from PLT-AUTO to PLT-MAN will provide a bumpless transfer of the device operation. Under PLT-MAN mode of control, the starting and stopping of each device is through operator commands on the Human Machine Interface (HMI). Following a power failure, a device in PLT-MAN will require operator intervention for it to start again. |
| PLT-AUTO | Switching from LOCAL to REMOTE mode may cause the device to operate if the device is in PLT-AUTO and required to start/stop by the PLC automatic device logic. Also, switching from PLT-MAN to PLT-AUTO may cause the device to operate if the device is required to start/stop by the PLC automatic device logic. The selection between PLT-MAN and PLT-AUTO is based upon the last selection made at any of the workstations in the SCADA network or the local Operator Interface. |

- SCADA Control Mode

### Degree of Automation

#### Equipment that is frequently operated shall be automated (Ex. Daily basis operations).

#### Automatic control is to be based in the PLC’s automatic control program.

#### The normal mode of operation shall be automatic.

#### Any device capable of being controlled by the PLC is required to have both PLT-AUTO and PLT-MAN modes available.  The exception to this guideline is infrequently operated equipment which shall be capable of manual operation only through the SCADA System.

#### Software interlocks will be provided in the automatic program to protect equipment and personnel.

#### Hardwired safety interlocks are to be incorporated for all manual or local operation through the SCADA system.

## I.P. Addressing Structure

#### Halton Region has developed a standardized I.P. addressing structure for all SCADA related components.

#### Halton Region staff will assign the actual I.P. address for all devices.

#### The Consultant /Systems Integrator may be required to set up the I.P. address in some devices, such as PLC’s or power monitors.  The Consultant must verify the I.P. address with Halton Region before they assign it.

#### The following chart identifies how Halton Region organizes I.P. address assignment.  Systems will be allocated to a second subnet within a facility to preserve IP usage on the main control subnet for future expansion, if required.

| Address | Device |
| --- | --- |
| 192.168.xxx.001 | Router (Gateway) |
| 192.168.xxx.002 – 010 | Core Switches |
| 192.168.xxx.011 – 030 | SCADA Desktops and Thin Clients with fixed IP's |
| 192.168.xxx.031 – 040 | All servers |
| 192.168.xxx.041 - 054 | Switches in the Network Distribution Enclosures |
| 192.168.xxx.055 – 100 | DHCP Scope |
| 192.168.xxx.101 – 140 | PLC's |
| 192.168.xxx.141 – 165 | PanelViews and Power Monitors |
| 192.168.xxx.166 – 199 | Remote Monitoring Devices (ex: Pribusin, Acromag, and Redlion) |
| 192.168.xxx.200 – 210 | Printers |
| 192.168.xxx.211 – 229 | Unallocated |
| 192.168.xxx.230 – 254 | Wireless Access Points |

- I.P. Addressing Structure

### Multiple Rack Applications

#### For multiple local rack ControlLogix PLC applications, additional Ethernet Cards are used to connect the other racks to the main processor rack. These cards are segregated from the SCADA network and follow a different I.P. addressing structure.

#### The following chart identifies how Halton Region organizes Multiple Local Rack ControlLogix PLC I.P. address assignment.

| Address | Device |
| --- | --- |
| 192.168.xxx.101 – 140 | SCADA Ethernet Card |
| 192.168.0.101 – xxx | Additional Main Rack Ethernet Cards |
| 192.168.1.101 – xxx | Rack 1 Ethernet Cards |
| 192.168.2.101 – xxx | Rack 2 Ethernet Cards |
| 192.168.x.101 – xxx | Rack x Ethernet Cards |

- Multiple Local Rack ControlLogix PLC I.P. Addressing Structure

## Integrated Vendor Packaged Equipment

### Overall Guidelines

#### Section 12 of the Consultants Procedure Manual also has guidelines for Vendor Packaged Equipment with a PLC. This section must be read in conjunction with that documentation.

#### In applications where integrated vendor packaged equipment is being supplied, the Consultant must provide the vendor with all sections of the SCADA standards, plus the content specified herein, at the time the request for Pre-qualification or Tender is issued.

#### Packaged panels are of two general types:

##### Equipment supplier furnished

##### Specialty supplier furnished.

#### Examples of equipment supplier furnished materials are: blower or centrifuge control panels, polymer or similar chemical mixing system control panels, if furnished by the mixing system supplier, and pneumatic transport system controls.

#### Examples of specialty panels are:  motor controllers, variable speed drives, sump pump control systems, and HVAC controls.

#### The Consultant and the Vendor have separate responsibilities when Vendor Packaged Equipment is supplied as part of a project.  The responsibilities of both the Consultant and the Vendor are identified below.

### Consultant’s Responsibility for Vendor Packaged Equipment

#### The Consultant is responsible for the tasks noted below. Also, the Consultant is responsible for some work that is also identified in statements that are to be included in the Vendor responsibilities.

#### It is the Consultant’s responsibility to ensure that all SCADA components of the integrated vendor packaged equipment are in compliance with Halton Region’s SCADA standards.

#### The Consultant will create a Process Narrative for the Vendor equipment.  Halton Region will review this Process Narrative with the Consultant.  The reviewed Process Narrative must be included as part of the request for Pre-qualification or Tender.

#### When the Consultant is designing the complete system, it is the responsibility of the Consultant to ensure the design matches Halton Region’s SCADA standards, and to ensure that the Vendor’s packaged equipment meets all of Halton Region’s SCADA standards.

#### When the Vendor is responsible for designing the system, it is the Consultant’s responsibility to ensure the design meets all of Halton Region’s requirements.  The Consultant is required to review the Vendor’s design for conformance to Halton Region’s SCADA standards, plus review and make recommendations on the Vendor’s submitted Design Deviation Memo.  Once the Consultant is satisfied, the Consultant is required to send the Vendor’s design to Halton Region’s SCADA Group.

#### The Consultant is required to forward all shop drawings from the Vendor to Halton Region’s SCADA Group for review.

#### The Consultant will review the Vendor’s Control Narrative and ensure that the control described in the Vendor’s narrative follows the control philosophy presented in the Consultant’s Process Narrative.  When the Consultant is satisfied with the Vendor’s Control Narrative, they will forward it to the SCADA Group for review.

#### It is the responsibility of the Consultant to co-ordinate with the Vendor for the delivery of the HMI graphics.

#### The Consultant is required to review the Vendor’s PLC and HMI programs and ensure they operate as described in the Vendor’s Control Narrative.  Once the Consultant is satisfied with the Vendor’s submission, the Consultant must forward the Vendor’s programs to the SCADA group for their review.

### Vendor’s Responsibility for Vendor Packaged Equipment

#### The Consultant is responsible for ensuring that the Vendor’s responsibilities, noted below, are included in the pre-qualification and/or tender documents issued to the Vendor.

#### As part of the request for pre-qualification or tender it is the Vendor’s responsibility to review all sections of Halton Region’s SCADA standards.

#### The Vendor is required to ensure they have received all Sections of Halton Region’s SCADA standards and the base load PLC and HMI program at the time of request for pre-qualification or tender. The Consultant will provide the vendor with the latest standard base load PLC and Wonderware InTouch HMI programs, clearly documenting the specific versions of each.

#### The Consultant must ensure that The Form of Tender or Pre-qualification package clearly identifies that:

##### The vendor must submit a Standards Deviation Memo indicating all deviations from the SCADA standards. For any deviations not included, the vendor is responsible for providing the deliverable as per the standards.

##### The Standards Deviation Memo is how the Vendor points out which parts of Halton’s SCADA standards they cannot meet or are required to deviate from due to equipment specific requirements.

##### The vendor must provide a list of sub-contractors that they intend to retain.

#### When a Package Panel has a PLC, it must be clearly marked on all shop drawings.

#### The Vendor is responsible for the proper operation and functional requirements of the panel.  The functional requirements include the desired operation, face of panel mounted equipment, panel layout, and interfaces with other control panels or computers.  The Vendor’s control panel(s) must meet all requirements specified in all sections of the SCADA Standards manual, unless specified and agreed to on the Design Deviations Memo.

#### It is not permissible to install any power above 120V within a PLC control panel.

#### It is not permissible to install a PLC control panel in an area where more than 120V is accessible, such as within an MCC or 600V panel.

#### The Vendor will issue their shop drawings to the Consultant.  The Consultant will review the shop drawings and forward a copy to Halton Region’s SCADA group.

#### When the Vendor is designing the system, it must be designed to meet all Sections of Halton Region’s SCADA standards.  The Vendor must submit their design for review and acceptance by the Consultant.

#### The Vendor will create a Control Narrative based upon the Consultant’s Process Narrative.  The Vendor will submit their Control Narrative to the Consultant for review.  The Vendor is required to update their Control Narrative based upon the Consultant’s and Halton Region’s feedback until the Consultant is satisfied with the quality of the document. This Control Narrative is a key deliverable and will be used as the “yardstick” to evaluate whether the software meets the user requirements at the FAT.

#### Prior to the creation of the Vendor’s Control Narrative, the Consultant will meet with the Vendor and present/train the Vendor’s programmer(s) on Halton Region’s standards for PLC and Wonderware InTouch programs.  At this meeting the Consultant will co-ordinate with the Vendor all interlocks and permissive requirements that the Vendor(s) equipment requires so that it can be included in the Vendor’s Control Narrative. Then, the Vendor’s Control Narrative will include any data passing, permissive, and interlocks identified at the meeting, related to both the Vendor supplied equipment and the other equipment being supplied and integrated under the general contract.

#### The Vendor’s programmer(s) and lead staff will attend a minimum of two Control Narrative review meetings with Halton Region and the Consultant. The Consultant will organize the meetings and prepare minutes.

#### Upon system commissioning, the Vendor is required to submit an as-built Control Narrative to the Consultant.

#### After construction is complete, the Consultant will take the Vendor’s as-built Control Narrative and integrate it into the plant Control Narrative, covering the aspects of data passing, permissive, and interlocks, so that the Plant’s Control Narrative reads as one uniform narrative. Therefore, the Vendor is responsible for providing a WORD document that matches the Consultant’s requirements for formatting and content.

#### The Vendor will develop the PLC software for their respective equipment. The Vendor is required to submit their PLC software to the Consultant for review.  The Consultant will also submit the PLC software to Halton Region’s SCADA Group for review. The Vendor’s program must also include all necessary interfaces to the Consultant’s PLC and HMI programs, as specified in the Control Narrative.

#### The Consultant will complete their PLC code and HMI graphics that relates to interfacing with the packaged equipment PLC’s. Prior to the formal FAT, the Consultant will test the Vendor's program with their PLC program(s) so that the FAT will be testing for one uniform system.

#### Data that is passed back and forth between plant PLC(s) and the vendor supplied PLC(s) (should only use READ message blocks), including process data, permissive, and interlocks are to be completed prior to, then tested as part of the software FAT.

#### The Vendor will develop the Wonderware InTouch software for their respective equipment. The Vendor is required to submit their complete InTouch base load to the Consultant for review.  The Consultant will also submit the InTouch Base load application to Halton Region SCADA Group for review.

#### The HMI graphics are to be developed using Halton Region’s base InTouch application.  This includes all InTouch windows, setpoints and any scripting required for the utilization of Halton Region's standard pop-up windows, such as the pump control or analog device control pop-up.

#### The Vendor must program the required HMI linkages to the Consultant’s HMI and PLC programs. This includes both the data sent and received. The Consultant will then receive the Vendor’s HMI application and integrate the Vendor’s application into a copy of the existing facility InTouch application. The Consultant will complete the navigation, alarming, call-outs section, historical trending, PLC communication, status screens, setpoint screens, and any reporting requirements. This is to be completed prior to the FAT.

#### The Consultant will also update the Plant’s PLC program(s) and Wonderware InTouch application with all related PLC programs and HMI graphics developed by the Consultant and the Vendor.

#### As Halton Region prefers that Vendor packaged equipment does not include PanelView Operator Interface Terminals, even when a Vendor insists that a PanelView is included. The Vendor is required to develop both Wonderware InTouch HMI graphics and PanelView graphics.  The PanelView graphics should be as close to Halton Region’s standards for Wonderware InTouch HMI graphics as possible.

#### When a PanelView is supplied, the Consultant will review the Vendor’s PanelView program and ensure it matches Halton Region’s Wonderware InTouch graphics as closely as possible.  As part of the initial shop drawing submission, the Consultant will check the PanelView graphics with the Wonderware InTouch graphics and ensure that all PanelView functions are included in the InTouch graphics.  Once the Consultant is satisfied with the Vendor’s submission, the Consultant will also forward the Vendor’s PanelView program to Halton Region’s SCADA Group for their review. The testing of the PanelView functionality will also be included in the FAT and SAT.

#### The ONLY exception when a functionality does not need to be added to the InTouch Application is if a specific Vendor controlled equipment setup or settings that must be configured by the Vendor does not require Halton Region to adjust as part of routine operation and maintenance on the equipment.  The Vendor must also provide Halton Region in writing, any PanelView credentials they have installed to access these parameters.

#### The Consultant will be responsible for scheduling software FATs with the Vendor, Halton Region, and any Contractors or other relevant parties to the witnessing of the FAT.

#### The Consultant will attend and document the Vendor’s control panel FAT.  The Consultant will coordinate the FAT date with Halton Region’s SCADA Group to ensure their attendance, as well as any other parties required to be present. The Vendor is responsible for conducting the control panel FAT and preparing the necessary test forms.  The Vendor is required to make any post FAT modifications to the panel.

#### The Vendor is required to bring the PanelView OIT loaded with the PanelView program to the software FAT to be tested as part of the software FAT.

#### The Vendor is required to attend all scheduled software FATs.  Any sub-contractor retained by the Vendor must send a programmer to the FATs as well.

#### The Consultant is responsible for organizing and facilitating the Software SAT. Both the vendor's system and the related plant systems will be tested together at the same time in the same manner that the Software FAT was conducted.

#### As the first phase of the SAT, the Vendor must perform I/O Loop Checks for all of the vendor’s equipment, using Halton Region’s test forms. The Consultant will coordinate with the Halton Region SCADA Group to schedule and document the test results. Prior to the testing, the Vendor must conduct their own internal equipment start-ups and ensure that their equipment is ready for the SAT.

#### The Vendor is required to attend all scheduled software SATs.  Any sub-contractor retained by the Vendor must send a programmer to the SATs as well.

#### All software, such as PLC code and HMI screens, will remain the property of Halton Region.

## Standard Process Narratives and Control Narratives

#### Process Narratives and Control Narratives are two separate documents.

#### Process Narratives are developed by the Consulting Process Engineer.  A Process Narrative is a document that describes how the overall process operates.  A Process Narrative is written at a level that anyone reading the document can understand how the process functions.

#### Control Narratives are developed by the PLC and/or HMI Software Programmer based upon the Process Narrative.  A Control Narrative is a document from which the PLC & HMI Programmer develops the PLC and HMI software.  A Control Narrative is used at the FAT as the “yardstick” to measure that the actual programs meet the project requirements. All sections of the Control Narrative are tested.

## Drawing Order and Organization

#### All drawings related to a PLC control panel shall be grouped together as part of the I&C drawings and be in the following order:

##### Control Panel Layout Drawings

##### Control Panel Power Distribution Drawings

#### Processor and Loop Drawings in order of the Rack/Slot assignment

#### All Control Schematics should be grouped together as part of the Electrical Drawings.

#### All P&ID drawings are to be grouped together as part of the I&C Drawings.

#### All Network Drawings should be grouped together as part of the I&C Drawings and be in the following order:

#### Network Architecture Drawing

#### All drawings related the Network Core should be grouped together in the following order;

#### Network Core Rack Layout

#### Network Core Power Distribution

#### Fiber Panel Port Assignments

#### All drawings related the Network Distribution Enclosure should be organized together for each individual NDE and in the following order:

#### NDE Layout Drawing

#### NDE Power Distribution Drawing

#### NDE Rack Layout and BOM Drawing

#### CAT6 Port Assignment

#### All Wall Mount Work Area Outlet Drawings

#### Any drawings related to the Wide Area Network connection.

## Standard Drawings

#### Halton Region has created a number of standardized drawings to help users understand and apply the SCADA standards. These drawings should be used as base templates for developing the project specific contract drawings. As part of creating the contract drawings, the Consultant must take ownership and responsibility for the design concepts within these drawings.  The SCADA templates are provided for convenience to the designers.

#### The designer is to review the templates and identify any problems with these templates as they relate to the specific project design. Halton Region has invested considerable time into these documents. Should the Consultant have questions on the standard template drawings they should contact Halton Region before modifying the template drawings.

#### Template drawings related to a section have been placed in the section’s Appendix 1B.  The placement of drawings throughout the document is to assist the Consultant in understanding the standards presented in the section.  Drawings presented in one section apply to the standards as a whole.  It is the responsibility of the Consultant to review each section and locate the appropriate drawings.

### Drawing Guidelines

#### All drawings contain instructions and notes.  These should be read in conjunction with these specifications.

#### The P&ID drawings, control schematics, loop drawings, and control panel power schematic drawings all have descriptions of the I/O points, so the same I/O point is shown on several drawings. The Consultant is to make sure the description for any I/O point is the exact same on all the drawings it is shown on.

#### Halton Region has a standard logical order for control circuits.  Consultants are not to modify the logical order in which the drawing is presented.

#### Halton Region’s template control drawings use common modules.  In applications where Halton Region has not published a template control drawing to meet the design requirements, the Consultant is required to:

##### Notify Halton Region through the use of a standards deviation memo.

##### Use as many of the modules from the template drawings as possible to create their application specific control circuit.

##### Adhere to all of Halton Region’s guidelines specified within this section.

#### Halton Region does not approve of typical drawings.  When a consultant is designing an application with four identical circuits, the consultant must produce one drawing for each circuit.

#### When two identical circuits are installed within the same panel, all wire labels and internal components must each have unique numbers.  The first circuit is identified with a leading 1, the second circuit with a leading 2, etc.  As an example, the first relay in circuit 1 will be CR-101, the first relay in circuit 2 will be CR-201, etc.

### Pump Control Schematics

#### Halton Region’s preference is to use 120 VAC as the main control power bus for the motor control circuits.  All power for the control circuit must come from the main switchgear feed to the Motor Control Center (MCC) so that the control power bus is de-energized when:

##### The circuit disconnect is opened.

##### The Emergency stop is pressed.

#### The function of all Local controls and indicators must be clearly labeled at the local control location.

#### Halton Region has standardized that the Emergency stop is placed immediately after the main fuse, and when activated it de-energizes the entire control circuit.

#### Process interlocks should not be hardwired into motor control circuits.  Halton Region has standardized that the PLC software will control these interlocks.

#### Halton Region has standard backup circuits which are published as part of the Wastewater Pumping Station Standards, which are presented in Section 8.  Consultants are required to use this circuit for automatic backup control.

#### VFD Local controls at the MCC or local control station must be capable of operating the VFD without the drive HMI.  The drive HMI should only be used for maintenance activities.

#### When auxiliary equipment such as VFD’s, Reduced Voltage Starters and Motor Protection Relays has an available 4 – 20 mA output, it may be used as the input for Motor current in place of a dedicated Current Transformer (CT).  For specifications, see Motor Power Monitoring Requirements.

#### All motor overloads should be electrically installed so in the event of a trip, only the motor is isolated from the circuit.

### Appropriate Pump Control Selection

#### Halton Region has standard control schematics for pumps that pulse to start and pulse to stop. There are also standard control schematics for maintained run contact. As part of the pre-design activity, the design team (including Regional staff) should examine each pump and its application and determine if the pump should be controlled with a pulse to start and a pulse to stop control schematic or a maintained run contact. When the decision is made, the appropriate control schematic from Appendix 1B will be selected and used to complete the design for the pump control.

### Valve Control

#### Halton Region’s standard is pulse to open and pulse to close for all discrete valves.  The PLC will pulse the valve request, and once received, the valve will seal and continue traveling to the appropriate limit once the PLC out de-energizes.

#### Halton Region does not approve of:

##### Using discrete controls to modulate valve actuators.

##### The use of Open/Close/Stop valves.

##### The use of two open position discrete valves.

#### When a valve or gate is required to modulate to multiple open positions, the Consultant is required to specify a modulating valve actuator.  The PLC software will move the actuator to the appropriate positions.

#### All valves are required to have a lockable field mounted local disconnect switch for maintenance activities in addition to a circuit breaker at the main electrical panel.

### SCADA Monitoring Requirements

#### All motor control circuit hardwired interlocks should have a SCADA input into the PLC and be integrated into the Ready circuit.

#### The consultant is required to determine the appropriate I/O points that are monitored based upon the application.  The minimum requirements are as shown on the drawing.  The final assignment is determined by the consultant based upon:

##### The operation and type of the equipment

##### Hardwired interlocks

#### In applications where a piece of equipment has no automatic operation but is monitored and controlled by the SCADA system, the Consultant is required to use Halton Region's template drawings.

#### All alarm points must be connected in a fail-safe manner (Open on Alarm), so that the alarm will be active on:

##### Alarm condition

##### Loss of power

##### Open circuit

## Halton’s Network Architecture Drawings

#### Halton’s SCADA group owns and maintains a set of Network Architecture drawings. When working on a project, the Consultant is to contact the Region’s SCADA group and request a copy of the appropriate drawing for the project.

#### When preparing the contract drawings, the consultant should be utilizing the Region’s layers and symbols that are part of the network architecture drawings. These symbols and layers should not be modified in any way without permission from the Region.

#### The Region will request an AutoCAD copy of this drawing at the time of Tender for record purposes.

#### Upon Substantial Completion of the project, the Consultant must submit an AutoCAD copy of this drawing to the Region’s SCADA group for record purposes. This submission is to be completed prior to and over and above the submission of record drawings.

## Modifications to Standard Drawings

### Typical P&ID Drawing

#### Consultants are required to create unique Process and Instrumentation Diagram (P&ID) drawings.

#### All PLC I/O is shown in the "PLC I/O" section.

#### The description of the I/O must match the description shown on the Contract loop drawings and all the control schematics.

### Standard Motor Control Drawings

#### On all standard motor control drawings, the Consultant is required to:

##### Update the Pump or Motor number and horsepower information.

##### Indicate all fusing amperages.

##### Update the supply voltage and control transformer information.

##### Update the Hardwired interlock information on line 12.

##### Lines 16 - 28 are the core rungs of the circuit and Consultants should not modify these rungs

##### Indicate the specific PLC Control Panel "XXX" information.

##### Update the door layout arrangement.

##### Remove the motor current input when not required.

##### Update the time preset for all timing relays (when present).

##### At some facilities, the stand-by generator is not sized sufficiently to run all the pumps. When this is the case, the pumps need to be interlocked to prevent all the pumps from being run while the generator is running. This will require that modifications be made to the pump control schematic. This interlock needs to work in all modes of pump control. Use the Pump Interlock Drawings provided with the electrical drawings as a template for how the interlocking is to be done.

### Standard Valve Control Drawings

#### Gate Valve actuator control circuits use the same controls as shown on the valve template drawings.

#### On all standard valve control drawings, the Consultant is required to:

##### Update the Valve or Gate number.

##### Indicate all fusing and breaker amperages.

##### Indicate the specific PLC Control Panel "XXX" information.

##### Update the door layout arrangement.

### Standard Control Panel Layout

#### On all standard Control Panel Layout Drawings, the Consultant is required to:

##### Update the specific control panel lamacoid information.

##### Update the dimensions of the panel based upon Section 3.

##### Update the PLC and I/O terminal block arrangement based upon Section 3.

##### Update the Bill of Materials.

### Control Panel Power Distribution Drawings

#### On all standard control panel power distribution drawings, the Consultant is required to:

##### Update the incoming 120 VAC circuit information.

##### Update all circuit breaker and fusing information and amperages.

### Loop Drawings

#### Halton Region has dynamic rack and slot numbering built into the standard loop drawings. All the consultant has to do is change the rack and slot number at the top portion of the drawing and this information will be transposed into the rack and slot label on all of the wire labels, the drawing name, and it will highlight the respective card in the graphic on the bottom of the drawing indicating I/O module placement.

#### On all standard loop drawings, the Consultant is required to:

#### Update the Rack and Slot number.

#### Update the English language description on all the loops. Note: these descriptions must match the descriptions on the P&ID drawings and the control schematics.

## Appendix 1A – Gatekeeper Protocol

| # | Document Name |
| --- | --- |
| 1 | PLC and HMI Gatekeeper Protocol |
| 3 |  |
| 4 |  |

## Appendix 1B – Standard SCADA Drawings

#### Appendix B is broken down into the following groupings of drawings

#### Control Panels

#### Control Schematics

#### Data Link Files

#### Loop Drawings and P&IDs

#### Network

## Appendix 1C - Standard Process and Control Narratives

| # | Document Name |
| --- | --- |
| 1 | Ferric Chlorine System General Control Narrative |
| 2 |  |
| 3 |  |
| 4 |  |