Consultant to add the following specification section into the Division 16, 16133 - Conduits, Conduit Fastenings and Conduit Fittings specification section and/or other applicable section(s) where conduits are specified.

X.X 	Structured Cabling

.Y 	The following language is to be included by Consultants to the DIVISION 16 specifications in order to provide clarity to Contractors: “All new Structured Cabling  which consists of fibre-optic and copper cabling to be run in minimum 2” galvanized rigid steel (GRS) conduit. Copper cabling includes, but is not limited to, Ethernet, Device Level Ring, DeviceNet, Profibus PA/DP, RS-485 and other communication bus copper cabling standards. GRS conduit is used to provide long-term resistance to corrosion and easier visual identification of Structured Cabling Conduit. GRS conduit provides shielding from Electromagnetic Interference (EMI) in copper signal cabling which can be caused by higher electrical noise levels in the plant, particularly from non-linear load conductors. GRS conduit allows for future wiring changes and mechanical protection to cabling. GRS conduit and its installation methods to comply with the Ontario Electrical Safety Code (OESC) including grounding and bonding requirements.  Cable and conduit must be installed in accordance with DIVISION 16 and DIVISION 17.  If any discrepancies or conflicts occur between DIVISION 17 or any other specification including DIVISION 16 then DIVISION 17 shall take precedence.”