Regional Municipality of Halton

SCADA Standards Manual

Section 4 Structured Cabling

SCADASCADA STANDARDS 2022

Table of Contents

SECTION 4 STRUCTURED CABLING	1

4.1	Intent of this Section	1

4.2	Instructions for Consultant	1

4.3	Design Guidelines	2

4.4	Standard Drawings	2

4.5	Fiber Optic Backbone	2

4.6	Horizontal Cabling System	3

4.7	Structured Cabling	3

4.8	Network Configuration and Redundancy	3

I/O Polling Servers	3

4.9	Network Equipment	3

4.10	WAN	3

4.11	Network and Phone Line Installation Process	4

4.12	Network Connectivity and Phone Lines for Remote Sites with a Building	5

Conduits	5

Back Board	6

NORDX BIX Wiring Block	6

4.13	Network & Phone Line Installation Process for Remote Sites without Building	6

New Panel at a New Location without a Building	6

Upgrade or Retrofit Panel at an Existing Location without a Building	6

Appendix 4A – Division 17 Typical Specifications	8

Appendix 4B – Division 16 Additions for Conduit for Structured Cabling	9

List of Tables

No table of figures entries found.

List of Figures

Figure 4.1	Installation of Network and Phone Lines Process Flow Chart	5

# STRUCTURED CABLING

## Intent of this Section

#### This document provides Halton Region’s standards for structured cabling. The majority of the detail is included in the typical Division 17 specification (refer to Appendix 4A) and the standard drawings (refer to Appendix 1B).

#### The Consultant should contact Halton Region to ensure they have the latest Division 17 specifications.

#### This section also contains instructions on Network and Phone line installation for remote sites.  Consultants completing projects at remote sites should familiarize themselves with the process.

## Instructions for Consultant

#### The Division 17 specifications only apply to water and wastewater plants, and similar locations with major buildings. For the smaller sites, such as sewage pumping stations, the Division 17 specifications do not apply, and should not be used. At these smaller sites, the “structured cabling” only consists of certified patch cables, networking hardware that will be free issued by Halton Region, and terminations that will be performed by the network service supplier. If circumstances dictate that more cabling is required then simple patch panels then the consultant is employ this Division 17 specification.

#### This document is to be read in conjunction with Halton’s Network drawing templates. The Consultant is fully responsible for all aspects of the contract drawings and specifications and this material is supplied only as a reference and to convey Halton’s preferences.

#### The Consultant is to check all cross references to other sections.

#### The Consultant is to verify the following;

#### The list of applicable documents to ensure the most recent release of documents is referenced.

#### The list of certified contractors is still valid and that all contractors listed are certified by CommScope at time of the release of the Tender.

#### That all product catalogue numbers are still current.

#### Remove any sections that are not pertinent or relevant to the job.

#### This standard specification includes parts for both Single Mode and Multi Mode fiber.  Consultant is to remove the format not being supplied and should confirm the format being include during the design process.  Each facility has unique requirements.

#### Review the use of the following sections and decide whether they should be in Division 17 of the spec or would they be better suited in another spec section

#### Fire stop

#### Damages

#### Penetrations of walls floors and ceilings

#### Conduit and ventilated cable tray

#### Grounding and Bonding

#### As a minimum, the following drawings that need to be included with the specifications are;

#### Network Architecture Drawings

#### Network Distribution Enclosures locations

#### Network Distribution Enclosures layout and BOM drawing

#### Network Distribution Enclosures Power Distribution

#### Work Area Outlet locations

#### Patch Panel Demarcation and port assignment drawing

#### Wall mount work area outlet details

#### Horizontal Cabling port assignment

#### Multi-mode Fabre Panel Port Assignement

#### Single-mode Fabre Panel Port Assignment

#### CAT 6 Port Assign

## Design Guidelines

#### The majority of the “design guidelines” are documented in the Division 17 Specification contained in Appendix 4A as well as the standard drawings in Appendix 1B.

#### Networks are designed on the star topology.

#### Network core enclosures already exist at all Water and Wastewater Plants, Landfill and Biosolids facilities.

#### Some projects may require the Consultant to specify changes to the existing network core enclosures.  When changes are required the Consultant must provide a complete set of design drawings and tender specifications.  The design must be completed in accordance with the SCADA standards. The consultant is to go to the site and document the current state before starting the design.

#### A network core enclosure contains:

##### Digital service provider equipment.

##### Appropriate equipment for star topology to all Network Distribution Enclosures (NDE).

##### Provisions for work area outlet connections.

##### Backup Active Directory servers and phone and communication equipment.

##### Other WAN connections.

## Standard Drawings

#### Standard networking drawings for typical installations are contained in the SCADA Standards, Section 1 Appendix 1B. The user should also refer to these drawings when reading this Section.

#### Specific to Wastewater Pumping Stations, standard networking drawings are contained in the SCADA Standards, Section 8.

## Fiber Optic Backbone

#### This backbone will connect the network core to the Network Distribution Enclosure (NDE).

#### The purpose of the local Network Distribution Enclosures (NDE) is to provide a local access switch in strategic locations which will allow work area outlets to be connected to the network. They will contain:

##### Space for network switch.  The network switch is supplied by Halton Region.

##### Fiber to CAT6 media conversion or fibre switches.

## Horizontal Cabling System

#### This is the CAT6 cable that connects all the work area outlets to the Network Distribution Enclosure (NDE) or the cable that connects PLC/Remote I/O racks, or the Device Level Ring (DLR) work area outlets from one panel to another. CAT6 cable used for network communications will be Blue and CAT6 used for DLR will be orange.

#### All field devices will use a patch cable to plug into a work area outlet which will then be connected to the Network Distribution Enclosure. DLR patch cables between racks will be Orange while other network patch cables will be Blue.

#### Install redundant Fiber optic cabling directly between the network core switches and the access switches.

## Structured Cabling

#### All structured cabling will continue to comply with the relevant EIA/TIA 568 Telecommunications Cabling Standard.

#### All new Fiber-optic cabling installations will use tight-buffered non-armored indoor/outdoor rated cable.  50 micron multi-mode Fiber optic cable will be used for all cable runs under 2000 meters. 62.5/125 micron single-mode Fiber will only be used for cabling runs which exceed 2000 meters. Before the design is started, the consultant is to work with the Region and determine if the fiber is to be multi-mode or single-mode.

#### The existing 62.5 micron multi-mode Fiber deployed within Halton Region is functional and there is no need to replace it unless failures occur. However, it should not be expanded.

#### CAT6 copper Ethernet cable will be used for all new installations. The existing CAT5e deployed within Halton Region is functional and there is no need to replace this cable unless failures occur. However, it should not be expanded. CAT6 cable will be installed in grounded steel conduit.  If the cable run is in a corrosive environment CAT6 STP in PVC conduit will be used.

## Network Configuration and Redundancy

### I/O Polling Servers

#### Halton Region utilizes standard server grade machines for the server applications in the network, configured based on the application requirements, and running Microsoft Server OS.  The machines are installed in a primary/secondary configuration.  Consultants should obtain plant specific network architecture drawings for details.

#### The redundant SCADA servers are used for running redundant I/O servers, Local Backup Data Collection and Alarm Distribution.

#### All SCADA servers are installed with redundant Network Interface Cards (NICs).

#### Redundant NICs are connected to Redundant Network Switches.

## Network Equipment

#### All network equipment such as switched routers etc. will be free issued by the Region and programmed by the Region’s IT department.

## WAN

#### All existing Water Treatment and Waste Water Treatment facilities have WAN connections.  All new Water Distribution and Wastewater Collection Facilities require a WAN connection.

#### The Region’s IT department coordinates the installation of WAN connections.

#### When a new connection to the WAN is required for a site, the Region prefers that a fiber option connection be installed. If there is not adequate infrastructure in the area, then the Region prefers a DSL connection. If there is not adequate infrastructure in the area for DSL, then the Region will install a wireless connection to the site.

#### Waste Water pumping stations also have requirements for a Pribusin Alarming circuit.  Refer to Section 8 for details.

## Network and Phone Line Installation Process

#### Halton Region has established a procedure to have network and phone lines installed at remote sites.  Refer to the following figure. The figure identifies what tasks need to be completed during predesign, detailed design and construction. It also identifies which stakeholder- i.e. the Consultant, Halton Region’s Project Manager, IT or the Halton Region SCADA Group leads each activity.

- Installation of Network and Phone Lines Process Flow Chart

## Network Connectivity and Phone Lines for Remote Sites with a Building

### Conduits

#### All buried conduits to have tracer wire installed and wire to be terminated on the grounding lug on the back board

#### Install marker tape over top of buried conduit

#### Install one 3 inch conduit for Bell services (analog phone line, S4T4, LDDS, DSL)

#### Install one 3 inch conduit dedicated to the Fiber cabling

#### Conduits coming into the building must always terminate on an above ground back board.

#### If the conduit enters the building in a basement a sealed NEMA 4 pull boxes will be allowed on the basement wall. Pull Box to be 300 mm 300 mm x 100mm deep.

#### Run conduit to the edge of property line in the direction of nearest utility pole, Bell pedestal or Bell manhole as determined during the Pre-design in consultation with Halton IT and utility supplier(s).

#### Conduit to be brought above ground at the property line; capped and stowed to prevent water from getting in.

#### Conduits must be kept free of water at all times

#### All conduits to have a pull string installed and left after the service medium is installed

#### Conduit depth to be below the frost line to prevent freezing

#### Install 1” conduit from back board to the required locations which could be hydro meter, the PLC panel, Pribusin alarm system or security system ACU.  The location of the conduits will be determined during detailed design.

### Back Board

#### Back board to be 1220 mm x 1220 mm 12mm plywood treated with fire retardant paint.

#### Back Board to be mounted on 2 inch vertically mounted Unistrut

#### No wall penetrations above the board will be permitted.

#### Back board should be installed next to the PLC Cabinet or as close as possible

#### A grounding lug to be installed on the back board

### NORDX BIX Wiring Block

#### The wiring block shall support Category 3, Category 5, Category 5E and Category 6 applications and facilitate cross connection and interconnection using either cross connect wire (voice only) or the appropriate category patch cords.

#### The wiring blocks shall be fire retardant, molded plastic consisting of horizontal index strips for terminating 25 pairs of conductors each.  The index strips shall be marked with five colors on the high teeth, separating the tip and ring of each pair, to establish pair location.

#### A series of fanning strips shall be located on each side of the block for dressing the cable pairs terminated on the adjacent index strips.

#### The wiring block shall accommodate 22- through 26-AWG conductors and shall be able to mount directly on the backboards

#### Clear label holders with the appropriate colour inserts shall be provided with the wiring blocks. The insert labels shall contain vertical lines spaced on the basis of circuit size (3-, 4-, or 5-pair) and shall not interfere with running, tracing or removing jumper wire/patch cords.

## Network & Phone Line Installation Process for Remote Sites without Building

### New Panel at a New Location without a Building

#### The vast majority of sites that will be constructed without a building will be wastewater pumping stations. The design details for wastewater pumping stations can be found in Section 8. For any other sites that do not have a building, the wastewater pumping stations design in Section 8 is to still be referenced and followed in principle and philosophy.

#### The overall installation process is the same as locations with a building.  However, the Consultant must provide a design to accommodate the installation of the new networking equipment.

#### Refer to Section 8 for further details

### Upgrade or Retrofit Panel at an Existing Location without a Building

#### Halton Region’s preference is to replace the entire panel being updated or retrofitted with a new control panel.  When this is performed the Consultant should approach the design as a new panel at a new location. This will enable the new network to be constructed in parallel to the existing.

#### If the panel is not to be replaced, the Consultant must meet with the Halton Region Project Manager, IT and the SCADA group to determine and discuss:

##### The types of data services required,

##### The data service termination point,

##### Where the network equipment will be placed,

##### How the data cables will connect from the network router to the PLC.

## Appendix 4A – Division 17 Typical Specifications

| # | Document Name |
| --- | --- |
| 1 | Division 17 Structured Cabling Systems V4 |
| 2 |  |
| 3 |  |
| 4 |  |

## Appendix 4B – Division 16 Additions for Conduit for Structured Cabling

| # | Document Name |
| --- | --- |
| 1 | Division 16 Additions for Conduit for Structured Cabling v1 |
| 2 |  |
| 3 |  |
| 4 |  |