Regional Municipality of Halton

SCADA Standards Manual

Section 6 HMI Programming

SCADA STANDARDS 2022

Table of Contents

SECTION 6 HMI Programming and Graphics	1

6.1	Introduction	1

6.2	Overall Guidelines	1

6.3	Specific HMI Programming Requirements	1

6.4	Operating System Based Security Levels	2

6.5	Configuring WindowMaker	6

6.6	Alarm Configuration in WindowMaker	9

6.7	Historical Logging Configuration in WindowMaker	10

6.8	Scripts	11

6.9	SQL Access manager	18

6.10	Alarm DB Logger Manager	18

6.11	Tagging/Coding	19

6.12	Device Tag Templates	20

6.13	Standard HMI Graphics	20

6.14	Colours	26

6.15	Process Piping Colours	27

6.16	Standard Symbols	27

6.17	Implementing a Symbol from the Halton Symbols Library	37

6.18	Device Identification Label	38

6.19	Device Alarm Box	39

6.20	Pump Graphic	40

6.21	Discrete Valve Graphic	42

6.22	Modulating Valve Graphic	45

6.23	Weir Plate and Gate	47

6.24	Device with no Auto Control	47

6.25	Analog Display Graphics	48

6.26	Button Bar	55

6.27	Alarm Banner	72

6.28	Screen Hierarchy	75

6.29	Process Control Screens	78

6.30	Hot Link Windows for Remote Stations	80

6.31	Process Current Setpoints	82

6.32	Duty Level Transmitter Control/Selection	91

6.33	Display of Device Automatic Setpoint	92

6.34	Use of Indirect Tags in Pop-Ups	92

6.35	Device Control Pop-Ups	93

6.36	Plant Communication Map	93

6.37	Server, Workstation and Thin Client Window	97

6.38	Logix and SLC Status Window	98

6.39	Rain Gauge Window	102

6.44	Autodialer Verification	102

6.45	Remote Station Pribusin Signals Graphics	108

6.46	Alarm Enable/Disable Control Pop-up	109

6.47	Power Monitor Information Pop-up	111

6.48	Polling Setup	112

6.49	Alarms and Events Strategy	114

6.50	Alarms History	119

6.51	Critical Alarms Notification	119

6.52	Acknowledged Critical Alarm Reminder	128

6.53	Sample PLC Code Related to Critical Alarm Reminder	134

6.54	Alarm History - SQL	134

6.55	InTouch Trends	135

6.56	Historian Trends	144

6.57	OI Server Configuration	150

6.58	Working Alone System – Waste Water	160

List of Tables

Table 6.1	Access Level Security	3

Table 6.2	4

Table 6.3	Alarm DB Logger Configuration Exceptions	19

Table 6.4	HMI Windows	25

Table 6.5	Process Steam Colour Conventions	26

Table 6.6	Device/Status Colour Conventions	27

Table 6.7	Analog Display Fonts	48

Table 6.8	Button Bar Properties	55

Table 6.9	Disabled Analog Alarms Window Properties	64

Table 6.10	Legal Entry Status Window Properties	70

Table 6.11	Alarm Banner Window Properties	72

Table 6.12	Alarm Colour Settings	74

Table 6.13	Window Properties	79

Table 6.14	Process Current Setpoints Window Properties	83

Table 6.15	2Device Duty Select Window Properties	87

Table 6.16	3Device Duty Select Window Properties	88

Table 6.17	4Device Duty Select Window Properties	89

Table 6.18	2Device Duty Select Window Properties	90

Table 6.19	Pump Duty Rotation Window Properties	90

Table 6.20	Duty Transmitter Selection Window Properties	92

Table 6.21	Plant Comm Map Window Properties	94

Table 6.22	Communication " and "X"	96

Table 6.23	Plant Communication Window Properties	99

Table 6.24	Comm Status Window Properties	101

Table 6.25	Auto Dialer Info Window Properties	102

Table 6.26	Dialer Alarms Enable Window Properties	110

Table 6.27	Alarm Group Hierarchy	114

Table 6.28	Alarm and Event Priorities	116

Table 6.29	Type of Alarm	116

Table 6.30	Alarm Summary Window Properties	118

Table 6.31	Critical Alarm Window Properties	126

Table 6.32	Critical Alarms Acknowledge Window Properties	128

Table 6.33	Critical Alarm Reminder Window Properties	133

Table 6.34	InTouch Trend Window Properties	136

Table 6.35	Historian Trend Trend Window Properties	149

Table 6.36	Configuration Set Filenames	151

Table 6.37	Connection and Reply Timeout Settings	152

List of Figures

Figure 6.1	Access Security Level	4

Figure 6.2	InTouch First Log-in Method	4

Figure 6.3	InTouch Log Second Login Method	5

Figure 6.4	InTouch Log on Username and Password Input	5

Figure 6.5	InTouch Log On Username Dropdown Menu	5

Figure 6.6	Window Maker Properties	6

Figure 6.7	Window Viewer General Properties	7

Figure 6.8	Window Viewer Window Configuration Properties	8

Figure 6.9	Window Viewer Home Window Configuration Properties	9

Figure 6.10	Alarm Properties	10

Figure 6.11	Historical Logging Configuration	10

Figure 6.12	Historical Logging Configuration	14

Figure 6.13	Alarm DB Logger Configuration	18

Figure 6.14	Button Bar and Alarm Banner	25

Figure 6.15	Pumps	28

Figure 6.16	Valves	28

Figure 6.17	Diesel Generators	29

Figure 6.18	Automatic Transfer Switches	29

Figure 6.19	Mixers	29

Figure 6.20	Reservoirs/Clear Wells	30

Figure 6.21	Elevated Tanks	30

Figure 6.22	Well Sites (North Halton Water Only)	31

Figure 6.23	Chemical Storage Tanks	31

Figure 6.24	Process Analog Displays	31

Figure 6.25	Traveling Screens	32

Figure 6.26	Hot Water Boiler	32

Figure 6.27	Containment Well	32

Figure 6.28	Gas Compressor	32

Figure 6.29	Waste Gas Burner	32

Figure 6.30	Digester	33

Figure 6.31	Standpipe	33

Figure 6.32	Heat Exchanger	33

Figure 6.33	Secondary Digester (Gas Holding Tank)	33

Figure 6.34	Sludge Hauling Truck	33

Figure 6.35	Round Tank	34

Figure 6.36	Static Mixer	34

Figure 6.37	Par Shall Flume	34

Figure 6.38	Scum Hopper	34

Figure 6.39	Grit Classifier	34

Figure 6.40	Grit Bin	34

Figure 6.41	Sludge Storage Tank (Floating Cover)	35

Figure 6.42	Square Tank	35

Figure 6.43	Wet Well	35

Figure 6.44	Weir Plate and Gate	36

Figure 6.45	Aeration Blower	36

Figure 6.46	Aeration Blower Line Thickness	36

Figure 6.47	Common Header Process Line Connections	36

Figure 6.48	Crossing Process Lines	37

Figure 6.49	Device Control	38

Figure 6.50	Device Identification – Green Label	38

Figure 6.51	Device Identification –Blue Label	38

Figure 6.52	Device Identification – Red Label	39

Figure 6.53	Animation Links Fill Color => Discrete	39

Figure 6.54	Animation Links Fill Miscellaneous => Blink	40

Figure 6.55	Pump Graphic Fill Colour	41

Figure 6.56	Pump Graphic Miscellaneous => Disable	41

Figure 6.57	Pump Graphic Text Block “On”	41

Figure 6.58	Pump Graphic Text Block “Off”	42

Figure 6.59	Discrete Valve Graphic Fill Colour	43

Figure 6.60	Discrete Valve Graphic Fully Opened Tag	43

Figure 6.61	Discrete Valve Graphic Miscellaneous => Disable	44

Figure 6.62	Discrete Valve Graphic “Opened”	44

Figure 6.63	Discrete Valve Graphic “Closed”	44

Figure 6.64	Modulating Valve Graphic Opened Fill Colour	45

Figure 6.65	Modulating Valve Graphic Miscellaneous => Disable	46

Figure 6.66	Modulating Valve Graphic “Opened”	46

Figure 6.67	Modulating Valve Graphic “Closed”	47

Figure 6.68	Analog Display Graphics Value Display => Analog	49

Figure 6.69	Analog Display Graphics Miscellaneous => Visibility	49

Figure 6.70	Analog Display Graphics Value Display => Analog	49

Figure 6.71	Analog Display Graphics Miscellaneous => Alarm Visibility	50

Figure 6.72	Analog Display Graphics Miscellaneous => Unit Visibility	50

Figure 6.73	Analog Display Graphics Miscellaneous => Blink	50

Figure 6.74	Analog Display Graphics HIHI/LOLO Alarms	51

Figure 6.75	Analog Display Graphics Miscellaneous => Visibility	51

Figure 6.76	Analog Display Graphics Miscellaneous => Blink	51

Figure 6.77	Analog Display Graphics Miscellaneous => Visibility	52

Figure 6.78	Analog Display Graphics Miscellaneous => Blink	52

Figure 6.79	Analog Display Graphics Miscellaneous => Line Colour	53

Figure 6.80	Analog Display Graphics Fill Colour => Discrete	53

Figure 6.81	Analog Display Graphics Miscellaneous => Disable	53

Figure 6.82	Disabled Analog Alarms Yellow Dot	54

Figure 6.83	Analog Display Graphics Graphical Display of Analog Value	54

Figure 6.84	Analog Display Graphics Vertical Fill => Analog Value	55

Figure 6.85	Button Bar	55

Figure 6.86	Button Bar Reports’ Button	58

Figure 6.87	Button Bar Available Trends	58

Figure 6.88	Button Bar “Setpoints” Button Security Limitation	60

Figure 6.89	Button Bar Disabled Critical Alarms	62

Figure 6.90	Disabled Analog Alarms Visibility Link	62

Figure 6.91	Disabled Analog Alarms Blinking Link	62

Figure 6.92	Disabled Critical Alarms Window	63

Figure 6.93	Disabled Analog Alarms Alarm Display General Configuration	64

Figure 6.94	Disabled Analog Alarms Alarm Display Message Configuration	65

Figure 6.95	Disabled Analog Alarms Alarm Display Font Settings	65

Figure 6.96	Disabled Analog Alarms Alarm Display Column Management	66

Figure 6.97	Disabled Analog Alarms Alarm Display Colour Configuration	66

Figure 6.98	Button Bar Security Alarm	67

Figure 6.99	Visibility Limitations for Security Alarm Button	67

Figure 6.100	Object Blink Properties for Security Alarm Button	67

Figure 6.101	Action Script for Security Alarm Button	68

Figure 6.102	Legal Entry level Status Window	69

Figure 6.103	Door Location Identifier Building Door	70

Figure 6.104	Legal Entry Status	70

Figure 6.105	Legal Entry Visibility Animation Link	71

Figure 6.106	Entry Alarm Visibility Animation Link	71

Figure 6.107	Access Alarm	71

Figure 6.108	Alarm Banner	72

Figure 6.109	Alarm Banner General Alarm Configuration	73

Figure 6.110	Alarm Banner Configuration Continued	73

Figure 6.111	Display Font	74

Figure 6.112	Alarm Configuration	74

Figure 6.113	Alarm Colour Settings	75

Figure 6.114	Screen Hierarchy	75

Figure 6.115	Filtration Overview Window	77

Figure 6.116	Sub-Process Window	78

Figure 6.117	Process Control Screen	79

Figure 6.118	Example Process Control Screen with Hot Links	81

Figure 6.119	Remote Station Process Control Screen	82

Figure 6.120	Sample Setpoints Window	83

Figure 6.121	Pumping Station Limits Window	85

Figure 6.122	2 Device Duty Select Window	86

Figure 6.123	3 Device Duty Select Window	87

Figure 6.124	4 Device Duty Select Window	88

Figure 6.125	Duty Select Info Popup	89

Figure 6.126	Duty Rotation Window	90

Figure 6.127	Aeration Blower’s Duty Assignment	91

Figure 6.128	Duty Text Split Apart	91

Figure 6.129	Duty Text Miscellaneous Visibility	91

Figure 6.130	Main Process Setpoints Window	91

Figure 6.131	Duty Transmitter Selection Window	92

Figure 6.132	Ferric Pump System	92

Figure 6.133	Plant Comm Map	94

Figure 6.134	Magenta Alarm Box	95

Figure 6.135	Magenta Box Animation Links	95

Figure 6.136	Magenta Alarm Box Animation Links	95

Figure 6.137	Magenta Alarm Box Animation Links	95

Figure 6.138	Visibility Animation Link	96

Figure 6.139	SCADA Server Graphic	96

Figure 6.140	Visibility Animation Link	97

Figure 6.141	Server, Workstation and Thin Clients Window	97

Figure 6.142	SLC Processor Status Summary Page	99

Figure 6.143	Plant Logix PLC Status Button	100

Figure 6.144	PLC to PLC Comm Status	100

Figure 6.145	PLC Comm Status Window	100

Figure 6.146	Logix Processor Status Summary Page	101

Figure 6.147	Auto Dialer Info Window	102

Figure 6.148	Verification System Information Buttons	103

Figure 6.149	Verification System Enable Buttons	103

Figure 6.150	White Text Box Animation Links	103

Figure 6.151	Visibility for the Red “On” Text	103

Figure 6.152	Visibility Animation Links	104

Figure 6.153	Text Status Box	104

Figure 6.154	Visibility Text	104

Figure 6.155	Blink Text	104

Figure 6.156	Discrete Value	105

Figure 6.157	Verification Alarms	105

Figure 6.158	Verification Alarms Animation Link	105

Figure 6.159	Dialer Failure Text Animation Link	106

Figure 6.160	Dialer Failure Text Animation Link	106

Figure 6.161	Verification Alarm Summary	106

Figure 6.162	General Alarm Configuration	106

Figure 6.163	General Message Configuration	107

Figure 6.164	Select Display Font Setup	107

Figure 6.165	Column Management Properties	107

Figure 6.166	Alarm Configuration Color	108

Figure 6.167	Typical Pribusin Alarming System Station	108

Figure 6.168	Dialer Alarms Enable Window	109

Figure 6.169	Dialer Alarms Enable Window	110

Figure 6.170	Alarm Enables	110

Figure 6.171	Dialer Alarm Enable Pop-up	111

Figure 6.172	Polling Node Access Name	113

Figure 6.173	Failover Configuration	114

Figure 6.174	Alarm Summary Window	117

Figure 6.175	ALMSUM	118

Figure 6.176	Script_Trigger Tag Properties	121

Figure 6.177	Time_Delay Tag Properties	122

Figure 6.178	Critical_True Tag Properties	123

Figure 6.179	APPRUNTIME Tag Properties	125

Figure 6.180	Critical Alarm Window	126

Figure 6.181	BXXACKALRMPB_AR Tag Properties	127

Figure 6.182	Animation Links Blink Text	127

Figure 6.183	Critical Alarms Acknowledge Pop-up	128

Figure 6.184	Critical Alarms Acknowledge General Configuration	130

Figure 6.185	BXXACKALMPB_EN Tag Properties	132

Figure 6.186	BXXACKALMDA_GA Tag Properties	132

Figure 6.187	Critical Alarm Reminder Window	133

Figure 6.188	Animation Links Blink Text	134

Figure 6.189	Alarm History - SQL	135

Figure 6.190	InTouch 4 Pen Trend	136

Figure 6.191	InTouch 4 Axis Selection	137

Figure 6.192	InTouch Trend Configuration	138

Figure 6.193	Last Hour Script	139

Figure 6.194	Last 24 Hours Script	140

Figure 6.195	Last 7 Days Script	141

Figure 6.196	‘Print’ Button	142

Figure 6.197	Print Script	142

Figure 6.198	8 Pen Trend	143

Figure 6.199	Historian Trend Plant Trends Menu	145

Figure 6.200	Historian Trend Trend Menu	149

Figure 6.201	aaHistClientTrend1 Control Name	150

Figure 6.202	Adding a New CLX Object	152

Figure 6.203	CLX Object Parameters	153

Figure 6.204	Logix5000_CLX Configuration	154

Figure 6.205	Logix5000_CLX Device Group	154

Figure 6.206	Adding ENB_CPLX Object	155

Figure 6.207	ENB_CPLX Object Parameters	156

Figure 6.208	Logix_CPLX Configuration	157

Figure 6.209	Logix_CPLX Device Group	158

Figure 6.210	Adding SLC500_TCPIP Object	159

Figure 6.211	SLC500_TCPIP Object Parameters	159

Figure 6.212	SLC500_TCPIP Device Group	160

Figure 6.213	Working Alone Main Window	161

Figure 6.214	Working Alone System Enabled Pop-up	161

Figure 6.215	Working Alone Enabled Window Script – On True	162

Figure 6.216	Working Alone Enabled Window Script – While True	162

Figure 6.217	Working Alone Enabled Window Script – On False	162

Figure 6.218	Working Alone Warning Pop-up	163

Figure 6.219	Working Alone Operator Warning Script – On True	163

Figure 6.220	Working Alone Operator Warning Script – While True	163

Figure 6.221	Working Alone Operator Warning Script – On False	164

Figure 6.222	Working Alone Operator Warning Script – While False	164

Figure 6.223	Working Alone System Alarm Pop-up	164

Figure 6.224	Working Alone Operator Alarm Script – While True	165

Figure 6.225	Working Alone Operator Alarm Script – While True	165

Figure 6.226	Working Alone Operator Alarm Script – On False	165

Figure 6.227	Working Alone Operator Alarm Script – While False	166

# HMI Programming and Graphics

## Introduction

#### The section details Halton Region’s Standards for HMI programming. Halton Region has a standard Base Load HMI application.  It is the Programmers’ responsibility to obtain the latest versions of this Base Load HMI application..

#### In most cases, Programmers will add their new HMI graphics and tags into an existing HMI application.  In addition to the newly created HMI graphics, Programmers are also required to update existing screens in the application to reflect the addition of the new process area.

#### When updating the HMI, Programmers are responsible for obtaining Care and Control as per the Gatekeeper Protocol.

#### Halton Region has developed standards for Wastewater Pumping stations (See Section 9).  These standards are specific to Wastewater pumping stations.  Should the Programmer identify a discrepancy between the Wastewater standards and these standards they should inform Halton Region.  Halton Region will review the discrepancy provide direction on how to proceed and update the standards to eliminate the discrepancy.

## Overall Guidelines

#### Programmers must use this section in conjunction with Section 2 Tagname Convention. When Programmers are creating new tags for an existing application, they must follow the latest tagging standards, even if those standards do not conform to the standards within the HMI application.

#### When new equipment is being added to an existing SCADA window, Programmers should place the new graphic in a location that best represents the process location.

## Specific HMI Programming Requirements

#### Halton Region SCADA group has setup a standard configuration for InTouch.  Programmers are not responsible for the installation of InTouch.

#### In situations where a new SCADA View node is being installed as part of a project, the Programmer should request a new thin client from the Project Manager.  The Project Manager will arrange to have the SCADA group and Technology services provide all necessary hardware.

#### Halton Region has created standards for both the PLC and HMI development that are integrated so as to provide a single standardized approach to SCADA system implementation within Halton Region.

#### In order to ensure consistency between the PLC and HMI development, which may from time to time be completed by different Programmers for a given project or as components of different projects, it is imperative that the standards be followed.  If the standards are not followed for the development of the PLC logic, then the HMI standards will not be applicable to the project when the HMI is completed. The same is true for HMI development that is completed independently of the PLC logic.  For this reason, Halton Region insists that these standards are followed by those Programmers wishing to carry out work within Halton Region.

#### Halton Region, through the development of recent HMI applications and the implementation of the guidelines and principles found in the Water, Wastewater and Solid Waste Facilities Design manual, have set out through this document to standardize the development of applications within Halton Region.

#### This standard has been developed to assist Programmers in developing standard applications using Halton Region’s current HMI product – Wonderware InTouch and reporting database Wonderware Historian.

#### The Region will confirm the version of Wonderware InTouch to be used for development.  In order to keep all facilities in good working order the Region reserves the right to apply Service Packs, Patches, Hotfixes, or perform complete software version upgrades at any time.

#### Region owned licenses must be installed on all workstations that run all InTouch applications.

#### Programmers must provide their own InTouch development licenses and development computer.  Development using Halton Region equipment will not be tolerated.

#### At most facilities there are two versions of the InTouch application – the server version and the client version.  The two versions of the application are identical, with the exception that the server version reads data from the PLCs and the client version reads the data from the server version’s tag database.  Programmers are to make and test all changes in the server version before importing their changes to the client version.  The Region has developed an SOP for this process which will be provided to the programmer.

#### Halton Region uses dedicated Primary and Backup OI servers.  These are typically installed on dedicated servers.  SCADA workstations and terminal servers installed in control rooms or key process areas at a facility are set up to be View nodes.

#### Halton Region has a standard configuration for InTouch installation.  This configuration is designed by the SCADA group.

#### Should Programmers be required to modify the configuration of InTouch, Window Viewer, or Window Maker, they must inform Halton Region in writing prior to making the modifications.

#### Halton Region does not use DDE/OPC topics, RSLinx or other OPC servers for data collection.  Only Wonderware DA Server or OI Server drivers are permitted for data collection.  The approved Device Integration server is OI ABCIP.  The DASABTCP and ABTCP drivers are used for legacy device support only.  Should Programmers require use of an additional DA or OI driver they are to submit a request to Halton Region in writing.

#### For a proper and stable data collection system, Halton Region has a compatible Windows, InTouch and OI server configuration.  As a result, the versions of Windows, InTouch and DAS servers are not always the latest available.  It is the responsibility of the Programmer to contact Halton Region to confirm the current supported software versions.

## Operating System Based Security Levels

### Configuring Security

#### Halton Region has standardized on OS based security.  Programmers should not need to update these configuration properties.

#### Halton Region recognizes that security may need to be disabled during development.  Programmers are to ensure that all changes are deployed with OS security enabled.

### Security Levels

#### Each user is assigned to an Active Directory Domain Group by the Regions Technology Services group.

#### Each Active Directory Domain Group is given an access level between 0 and 9999.   This access level determines the level of control that members of that Active Directory Domain Group has on the system. There are eight Active Directory Domain Groups within the SCADA applications.

| Group | Access Level | Name in Security Script |
| --- | --- | --- |
| Administrator | 9999 |  |
| Supervisor | 9100 | PW_SCADA_XXX_SUP |
| Subforeman | 8100 | PW_SCADA_XXX_SUB |
| Operator | 6100 | PW_SCADA_XXX_OPS |
| Supervisor Water | 9100 | PW_SCADA_GLO_SUP_WATER |
| Supervisor Waste | 9100 | PW_SCADA_GLO_SUP_WASTE |
| Operator in Training | 5500 | PW_SCADA_GLO_OIT |
| Technicians | 6100 | PW_SCADA_GLO_TEC |
| Consultant | 9800 | PW_SCADA_GLO_CON |
| Developer | 9999 | PW_SCADA_GLO_DEV |
| View Only | 5500 | PW_SCADA_GLO_VON |

- Access Level Security

#### In the example table above for the Supervisor, Subforeman and Operator groups under Name in Security Script, “XXX” is specific to the facility where the InTouch application is deployed.  Each InTouch application would have the appropriate code for that specific application in the place of BWPP. The programmer should not have to modify these in any way.

#### All HMI applications are developed so that there is no control available in the system until a user logs in.  This is accomplished by locking out several of the navigation buttons on the button bar, as well as device controls until a user with sufficient access rights is logged in.  For more information, refer to the section on “Button Bar”.

#### There are six (6) memory integer tags that have been created in the Base Application to be used as indirect tags when establishing user group access.  This provides a quick and easy mechanism that Halton Region can use to change user access if necessary.  The six (6) access level tags are as follows.  Access Level Tags

| Memory Integer Tag | Tag Description | Access Level |
| --- | --- | --- |
| ACL_SUPER | Supervisor Access Level | 9000 |
| ACL_SUBFOR | Subforeman Access Level | 8100 |
| ACL_OPTR | Operator Access Level | 6000 |
| ACL_PUMP | Pump Access Level | 6000 |
| ACL_VLV | Valve Access Level | 6000 |
| ACL_ANIN | Analog Access Level | 6000 |

#### Based upon the above table, the access rights of a device require that the user whom signs on has at least that level of access.

#### Powerful features within the HMI application such as equipment control or alarm resets limit access to users using the Memory Integer tags shown in Table 6.2. To set the security level of a component, select the Animation Links => Miscellaneous => Disable feature.  The scripting will be similar to the following graphic:

- Access Security Level

#### In this example ACL_SUPER is a memory integer tag set with an initial value of 9000. Each disable should be set to the appropriate level as shown in Table 6.2.

#### Most security privileges are pre-defined in the HMI baseload.  Custom security privileges or exceptions will be determined during the project in consultation with the affected facility and the SCADA group.

### Auto Login into InTouch

#### The following script is run during the start-up of the InTouch application; it logs in the active Windows OS user into the app.

#### {Auto User Login Script}

#### IF $Operator == "None" THEN

#### Result = LogonCurrentUser();

#### ENDIF;

### Manual Login into InTouch

#### To log into InTouch there are two methods.  In the first method the user will left click the Special option from the InTouch Menu, followed by Security, and Log On, shown below.

- InTouch First Log-in Method

#### The second method the user will press the “F2” key. Both methods will result in the following logon being displayed:

- InTouch Log Second Login Method

At this point users will enter their standard Halton Windows domain User Name and Password. For all Halton Region applications the Domain is to be entered as “Halton”, (without quotations).

- InTouch Log on Username and Password Input

#### "Halton" can also be selected from the domain drop down list as shown here:

- InTouch Log On Username Dropdown Menu

#### Selecting anything other than "Halton" in the drop down list as the Domain name will result in a failed Login.

#### Clicking OK will complete the Logon process. The users name will be displayed in the “Button Bar” on the top left corner of the application. A user’s access level is set to allow them to interact with only the equipment and process controls they are permitted to.

#### The user should use the same menu, Special - Security, to log off (selecting the Log Off option instead of Log On), or by pressing F3, when necessary tasks have been completed.

#### All systems are configured to auto-logout of the InTouch application after a period of inactivity.  Continued inactivity will eventually log the user out of the Windows environment. InTouch security has been enabled to ensure only qualified personnel are able to operate equipment.   See the Condition Scripts, under Section 6.8.

#### A user’s InTouch session may remain active if they do not properly log out of Windows. It is the end user’s responsibility to ensure security procedures are observed on all SCADA systems, including but not limited to logging off or locking their session when leaving the terminal unattended.

## Configuring WindowMaker

#### The configuration on WindowMaker is controlled by Halton Region.  The following section provides Programmers with detailed documentation on how InTouch Window Maker is configured.  Programmers should not modify any configurations.

### Configuring WindowMaker

#### To configure WindowMaker, select Special => Configure => WindowMaker.  The following window will be displayed.

- Window Maker Properties

Configuring WindowViewer

#### To configure WindowViewer, select Special => Configure => WindowViewer.  The following three (3) windows will be displayed.

- Window Viewer General Properties

### Configuring WindowViewer (continued)

- Window Viewer Window Configuration Properties

### Configuring WindowViewer (continued)

- Window Viewer Home Window Configuration Properties

#### There are four (4) screens configured as home windows for all SCADA applications.

##### Alarms;

##### Buttons;

##### Critical Alarms; and

##### A “Home” Process Control screen, which varies for each application

## Alarm Configuration in WindowMaker

#### The alarm configuration is controlled by Halton Region.  Programmers should not modify this configuration.

#### To configure Alarms, select the Special => Configure => Alarms.  The following window will be displayed.

- Alarm Properties

#### RTN implies Ack should be unchecked.

## Historical Logging Configuration in WindowMaker

#### The configuration of Historical logging is controlled by Halton Region.  Programmers should not modify this configuration.

#### To configure Historical Logging, select the ‘Special’ menu and select the ‘Configure’ option.  Then select the ‘Historical Logging’ option.  The following window will be displayed.

- Historical Logging Configuration

#### This configures where InTouch stores its local trended data and how long it stores the files for. The logging node will always be the name of the secondary server for the application. The store period is to be 395 days for all applications.

### ActiveX

#### ActiveX Events are used for Historian Trend trending and alarm management.  Request for use of ActiveX controls for any other functions must be submitted to Halton Region in writing.

### Configure Distributed Name Manager

#### Halton Region does not use this feature

### Wizard/ActiveX Installation

#### Programmers should not use this feature

## Scripts

### Application Script

#### There are three types of Applications scripts, On Startup, While Running, and On Shutdown.

#### Halton Region does not use On Shutdown Application scripts.

#### The On Startup Script executes when InTouch starts.

#### The first script gets the Node Name of the Workstation the InTouch Application is installed on.

GetNodeName(COMPNAME,131);

#### The next script identifies if the computer running SCADA is part of the system.

{All Workstations including Plant wide and Remote site}

IF (COMPNAME == "BXXCPU01" OR COMPNAME == "BXXCPU02" OR COMPNAME == "BXXWS01" OR COMPNAME == "BXXWS02"  OR COMPNAME == "BXXWS03" OR COMPNAME == "BXXWS04" OR COMPNAME == "BLAWS01" OR COMPNAME == "BLJWS01" OR COMPNAME == "BLCWS01"  OR COMPNAME == "BLFWS01"  OR COMPNAME == "KIBWS01" OR COMPNAME == "WBSWS01" OR  COMPNAME == "HERWS01" OR COMPNAME == "BASWS01" OR COMPNAME == "BESWS01" OR COMPNAME == "TYSWS01" OR COMPNAME == "ALRWS01") THEN

BXXCOMP = 1;

ELSE

BXXCOMP = 0;

ENDIF;

#### This script identifies if the local workstation or thin client is part of the BXXCOMP group.  The names used within the script changes on an application by application basis.

#### BXXCOMP is a Memory Discrete tag used to identify that a SCADA node is part of a group of SCADA workstations.

#### If Programmers are required to add a new SCADA node to an existing HMI application, they are required to update this script.

#### The next script sets the name of the hot backup alarm pair for distributed alarm queries.  For any new applications the name of the Hot Backup pair shall be determined by Halton Region and set accordingly by the programmer.

SRV_NAME = "Plant\";

#### The next part of the startup script defines the group security assignment for OS log-on, and it defines the InTouch group operation security.  The security script shall include the six (6) global user groups and the three user groups specific to the facility.  An example for Acton Wastewater is shown below.

{Example, Group security assignment for OS log in}
c = AddPermission( "Halton", "PW_SCADA_AWWT_SUP", 9100 );
c = AddPermission( "Halton", "PW_SCADA_AWWT_SUB", 8100 );
c = AddPermission( "Halton", "PW_SCADA_AWWT_OPS", 6100 );

c = AddPermission( "Halton", "PW_SCADA_GLO_SUP_WASTE", 9100 ); 
c = AddPermission( "Halton", "PW_SCADA_GLO_DEV", 9999 ); 
c = AddPermission( "Halton", "PW_SCADA_GLO_VON", 5500 ); 
c = AddPermission( "Halton", "PW_SCADA_GLO_CON", 9100 ); 
c = AddPermission( "Halton", "PW_SCADA_GLO_TEC", 6100 );

c = AddPermission( "Halton", "PW_SCADA_GLO_OIT", 5500 );

#### The next portion of the startup script sets the device security levels for InTouch

{InTouch group operation security}

ACL_PUMP = 6000;

ACL_ANIN = 6000;

ACL_VLV = 6000;

ACL_OPTR = 6000;

ACL_SUBFOR=8100;

ACL_SUPER = 9000;

#### This script is controlled by Halton Region.  Programmers should not modify this script.  The script sets the security permission levels for pumps, valves, etc.  These tags are used by device control pop-ups and setpoint windows to prevent unauthorized operation of equipment or changing of setpoints.

#### The next part of the script auto logs in the current user, if they are not already logged in

{Auto User Login Script}

IF $Operator == "None" THEN

Result = LogonCurrentUser();

ENDIF;

#### The last part of the startup script runs the heartbeat Quickfunction InTouchHeartbeat().  A heartbeat shall exist for all IO servers.  Heartbeats may exist for legacy workstations and Thin Clients but are not required unless implemented for some Work Alone monitoring systems.

{Set InTouch Heartbeats}

CALL InTouchHeartbeat();

#### The workstation names and tags used in the InTouchHeartbeat quickfunction will change on an application by application basis.  The intent of the script is to clear the heartbeat alarm in the plant’s Autodialer PLC.  InTouch will display a HMI communication Heartbeat Alarm when communications are lost.

#### If Programmers are required to add a new SCADA node to an existing HMI application, they are required to update this script.

{Set Heartbeat Signal to IO Servers and any Thin Clients/Workstations}

IF COMPNAME == "BXXCPU01" THEN

BXXCPU01AO_HB = -1;

ENDIF;

IF COMPNAME == "BXXCPU02" THEN

BXXCPU02AO_HB = -1;

ENDIF;

IF COMPNAME == "BXXWS01" THEN

BXXWS01AO_HB = -1;

ENDIF;

### While Running

#### The While Running script is configured to run once every 10,000 mS.  These scripts execute once every 10 Seconds.

#### The first part of the script increments the application runtime.

APPRUNTIME = APPRUNTIME + 1;

#### This tag is used by the Condition Scripts.

#### The next script is the global UnAck for all alarms in the HMI application.  This code exists in legacy applications and should not be used in any new InTouch Applications.

Burloak.UnAck = BURLOAK-GU;

#### The next three action scripts call the quick functions, shown below:

{Acks alarms across the WAN}

CALL GroupUnack( );

{Call Heartbeat Script}

CALL InTouchHeartbeat();

{Opens the Critical Alarm Object on Monitoring Nodes}

CALL CriticalAlarmObject( );

{Checks for any entry/exit or access alarms in the system}

CALL SecurityAlert();

#### The GroupUnack Quickfunction is a legacy application script that is not to be used in any new InTouch Applications.

#### Any new quick functions should be called after the Security Alarm.  A comment describing the operation of the quick function should be included above the call.

#### When an integrator is required to add a new quick function they are required to notify Halton Region.

### Key Scripts

#### Key scripts are used to assign the function key to run a specific script each time the key is pressed.  Key Scripts are controlled by Halton Region.  Programmers should not change the key scripts or add new key scripts.

#### The F1 Key is programmed to show a process overview Window that Operations requires frequent quick access to.  The name of the Window will vary on an Application by Application basis.

#### The F2 key is programmed to run the following script:

SendKeys"%(SYL)";

#### This sends the command to logon to InTouch.

#### The F3 key is programmed to run the following script:

SendKeys"%(SYO)";

#### This sends the command to logoff InTouch.

### Condition Scripts

#### Conditions scripts execute when the condition is true.

#### The following figure shows all condition scripts that are part of the base application.

- Historical Logging Configuration

#### Condition Script “ $Hour == 3 AND $Minute == 0” runs the following script:

IF COMPNAME == "BXXCPU01" THEN

CALL PLCDateTimeSync( );

ENDIF;

##### This script calls the PLC Set date and time quick function.  Programmers are required to update this script whenever a PLC is added or removed from an InTouch Application.

#### Condition Script “$InactivityTimeout OR ($Operator == "None") runs the following script:

ShowHome;

##### This script will show the home windows, when a user logs out or they are logged out due to inactivity.

#### Condition Script “((COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB) )  AND Critical_Alarm_Counter==2”

##### This script is used for the critical alarm reminder.  This will be discussed further under Critical the critical alarm reminder.

#### Condition Script “((COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB) ) AND Ack_Critical_Alarm>0”

##### This script is used for critical alarming. This will be discussed further under Critical Alarms

#### Condition Script “((COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB)) AND (Burloak.UnAck OR Burloak.Alarm)”

##### This script is used for critical alarming. This will be discussed further under Critical Alarms

#### Condition Script “(COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB)”

##### This script is used for the critical alarm reminder.  This will be discussed further under Critical the critical alarm reminder.

#### Condition Script “BXXCOMP==1 AND BXXACKALMDA_GA==1”

##### This script is used for the critical alarm reminder.  This will be discussed further under Critical the critical alarm reminder.

#### Condition Scripts ANIN_UNITSBTNPUSH==1 ,“CLOSEBTNPUSH == 1” “OPENBTNPUSH == 1”, PMP_UNITSBTNPUSH==1, “STARTBTNPUSH ==1”, and “STOPBTNPUSH ==1”   are used by device control pop-ups and do not need to be modified by programmers.

#### Condition Script “Critical_True > 0 AND BXXCOMP”

##### This script is used for critical alarming. This will be discussed further under Critical Alarms

#### Condition Script “Critical_True >= 1 AND APPRUNTIME > 3”

##### This script is used for critical alarming. This will be discussed further under Critical Alarms

#### Condition Script “Critical_True >=1 AND BXXCOMP”

##### This script is used for critical alarming. This will be discussed further under Critical Alarms

#### Condition Script “Script_Trigger ==1”

##### This script is used for critical alarming. This will be discussed further under Critical Alarms

#### Condition Script “Script_Trigger2 ==1”

##### This script is used for critical alarming. This will be discussed further under Critical Alarms

##### script is used by the device control pop-ups.  Programmers do not need to modify this script.

#### Condition Script “Time_Delay > 0”

##### This script is used for critical alarming. This will be discussed further under Critical Alarms

#### Condition Scripts “Unused1 ==1”,“Unused2 ==1”, “Unused3 ==1” and “Unused4 ==1” are used to hide functionality for certain devices.  In all instances, if the tag is true it is immediately set false.

#### Condition Script “UnusedAnalog1 <> 0” and “UnusedAnalog2 <> 0.”  Are used for InTouch Trending.  If either tag is not equal to zero, it is set to zero.  New InTouch applications will only use Historian Trend trending and these two scripts can be removed.

#### PLC-HMI Communication Alarms BXXPLC1001DI_CN

##### This Condition script provides a template for implementing communication alarms between the HMI and PLC.  In order to implement this script, two tags are required; BXXPLC1001DI_CN, which is an IO Discrete Tag that monitors the $SYS$Status tag of the PLC driver, and alarm tag BXXPLC1001DA_CN, which is an IO discrete tag using the IO server pair as the access name (BXXCPU01_1) and using the tagname as the item name.

##### The “While False” script will attempt to reinitialize the Topic, and will also set the alarm tag.

{If there is a loss of communication to the access name, then restart}

{The Access name to try and reestablish communications}

IF COMPNAME == "BXXCPU01" OR COMPNAME == "BXXCPU02" THEN

IOReinitAccessName("BXX",0);

{Set the Alarm Tag}

BXXRT01001DA_CN=0;

ENDIF;

##### The execution interval for local PLCs is 30000 Msec (30 seconds) and 300000 Msec (5 minutes) for remote PLCs.  Programmers may be asked to implement different intervals depending on the criticality of the system and strength of the network connection.

##### The “On True” and “While True” scripts are identical in clearing the alarm tag.  The “While True” script shall execute every 10000 Msec.

{Clear The Alarm}

IF COMPNAME == "BXXCPU01" OR COMPNAME == "BXXCPU02" THEN

BXXRT01001DA_CN=1;

ENDIF;

##### All instances of “BXX” in the sample script are to be replaced with names appropriate to the InTouch Application and PLC.

### Data Change

#### Data Change scripts only run when data changes.

#### Data Change Script “SQL-DATABASE-SELECTED”

##### This is used as part of the SQL alarm database window.  It will be discussed under the SQL alarm database section.

#### Data Change Script “SQL-DEFINED-QUERY”

##### This is used as part of the SQL alarm database.  It will be discussed under the SQL alarm database section.

### Quick Functions

#### Quick functions are programmed scripts that run when called and can be called from anywhere in the InTouch scripting system.  Quickfunctions are intended to be used when a lengthly piece of code is to be reused repeatedly within the application, to simplify deployment and streamline changes.  If a programmer wishes to develop a Quickfunction for work they are performing they should contact the Halton Region SCADA group.  .

#### CloseAnalogPopUps, CloseGenPopUps, ClosePumpPopUps, Close ValvePopUps

##### These Quickfunctions are used to close all pop-ups of similar device types to prevent indirect tagging conflicts.  Only one pop-up for a device type may be open at a time, even if the device uses a pop-up developed for an earlier version of the standards

##### These Quickfunctions must be updated any time a new device pop-up is released.  The list of pop-up window names may need to be revised on a per-application basis to remove any pop-ups that were never deployed to that application or include additional customized pop-ups that are not part of the standard build.

#### Quick Function CriticalAlarmObject

##### This calls the critical alarm object.  This will be discussed further under Critical Alarms.

#### Quick Function PLCTimeDateSync synchronizes all facility PLC clocks with the server time.  A sample script for a ControLogix PLC is shown below.  The script for a SLC is similar, bud does to require a pushbutton command as the clock registers can be written to directly.

{ Chemical PLC }

BLCRPU100AO_YY = $Year;

BLCRPU100AO_MM = $Month;

BLCRPU100AO_DY = $Day;

BLCRPU100AO_HS = $Hour;

BLCRPU100AO_MS = $Minute;

BLCRPU100AO_SN = $Second;

BLCRPU100 PB_SU = 1;

##### This script is called by the Condition script “$Hour == 3 AND $Minute == 0.” and can also be triggered manually from the PLC status pages.

##### Programmers are required modify this Quickfunction whenever a PLC is added or removed from a facility.

#### Quick Function SecurityAlert (Water Sites)

##### The security alarm quick function is used to indicate an Illegal Entry alarm on the main Process Overview.

##### Any new Illegal Entry alarm tag must be added to the script.  An example of the script is shown below:

{Burlington Security Alert}

IF (ALRSTN100DA_SA OR BASSTN100DA_SA OR BESSTN100DA_SA OR BRSSTN100DA_SA OR BWASTN100DA_SA OR BWJSTN100DA_SA OR GLMSTN100DA_SA OR HERSTN100DA_SA OR KIBSTN100DA_SA OR MFSSTN100DA_SA OR PRMSTN100DA_SA OR TYSSTN100DA_SA OR WBSSTN100DA_SA OR WDSSTN100DA_SA OR BCVSTN100DA_SA) THEN

BXXSTN000DA_SA = 1;

ELSE

BXXSTN000DA_SA = 0;

ENDIF;

IF (ALRSTN100DA_AC OR BASSTN100DA_AC OR BESSTN100DA_AC OR BRSSTN100DA_AC OR GLMSTN100DA_AC OR HERSTN100DA_AC OR KIBSTN100DA_AC OR MFSSTN100DA_AC OR PRMSTN100DA_AC OR TYSSTN100DA_AC OR WBSSTN100DA_AC OR WDSSTN100DA_AC OR BCVSTN100DA_AC) THEN

BXXSTN000DA_AC = 1;

ELSE

BXXSTN000DA_AC = 0;

ENDIF;

##### This script is specific to each HMI application.  The tags used by the script are the security tags for each HMI application.

## SQL Access manager

#### .1 Halton Region does not use this feature.

## Alarm DB Logger Manager

- The Alarm DB Logger is to be configured and running on both I/O servers at all facilities in order to ensure the database is always available as there will always be a primary database and a backup database. At facilities where critical alarms are being logged to the respective historian server, this is always done by xxxCPU01. The window Alarm History-SQL display will always query the database on xxxCPU02.

- The logger is to be configured the same as shown in Figure 6.13 for all the servers with a few exceptions that are detailed in Table 6.3 below.

- Alarm DB Logger Configuration

The fields that need to be changed depending on the server are the “Server Name”, and the “To Priority” and they should be changed based on the table below.

| #### SCADA Server Name | #### InTouch Application | #### Logged to Server | #### To Priority |
| --- | --- | --- | --- |
| ASYCPU01 | Acton Wastewater | ASYCPU01 | 999 |
| ASYCPU02 | Acton Wastewater | ASYCPU02 | 999 |
| BFYCPU01 | Biosolids Facility | BFYCPU01 | 999 |
| BFYCPU02 | Biosolids Facility | BFYCPU02 | 999 |
| BWYCPU01 | Burlington Water | SCADA1 | 99 |
| BWYCPU02 | Burlington Water | BWYCPU02 | 999 |
| BLXCPU01 | Burloak Water | BLXCPU01 | 999 |
| BLXCPU02 | Burloak Water | SCADA1 | 99 |
| GSYCPU01 | Georgetown Wastewater | GSYCPU01 | 999 |
| GSYCPU02 | Georgetown Wastewater | GSYCPU02 | 999 |
| MI1CPU02 | Landfill Site | MI1CPU02 | 999 |
| MI1CPU01 | Landfill Site | MI1CPU01 | 999 |
| MHYCPU01 | Mid-Halton Wastewater | MHYCPU01 | 999 |
| MHYCPU02 | Mid-Halton Wastewater | MHYCPU02 | 999 |
| GWYCPU01 | North Water System | GWYCPU01 | 999 |
| MWYCPU01 | North Water System | SCADA1 | 99 |
| OWYCPU01 | Oakville Water | SCADA1 | 99 |
| OWYCPU02 | Oakville Water | OWYCPU02 | 999 |
| BSYCPU01 | Skyway Wastewater | BSYCPU01 | 999 |
| BSYCPU02 | Skyway Wastewater | BSYCPU02 | 999 |
| SEYCPU01 | South East Wastewater | SEYCPU01 | 999 |
| SEYCPU02 | South East Wastewater | SEYCPU02 | 999 |
| SWYCPU01 | South West Wastewater | SWYCPU01 | 999 |
| SWYCPU02 | South West Wastewater | SWYCPU02 | 999 |
| WCYCPU02 | Wastewater Collections | WCYCPU02 | 999 |
| WCYCPU01 | Wastewater Collections | WCYCPU01 | 999 |
| WDYCPU01 | Water Distribution | SCADA1 | 99 |
| WDYCPU02 | Water Distribution | WDYCPU02 | 999 |

- Alarm DB Logger Configuration Exceptions

#### The Alarm DB Logger utility should not have to be modified by external programmers. If modifications are required, the SCADA gatekeeper should be consulted before any changes are made.

### Alarm DB Purge-Archive

#### The Alarm DB Purge/Archive Utility is a separate executable used to remove old alarms and events from the SQL database.

#### The Alarm DB Purge/Archive Utility is not used and is to be left off.

### Alarm Hot Backup Manager

#### The Alarm Hot Backup Manager is used to synchronize alarming between two redundant polling nodes.

#### The Hot Backup is configured by the SCADA group and does not need to be changed by the programmer.

#### If an additional Hot Backup pair is required at a facility, the programmer is required to make a request to the Region in writing to make the change.

## Tagging/Coding

#### The development of tagnames for Halton Region’s HMI applications is to be based on the latest version of the Halton Region’s Tagname Convention, as presented in Section 2 of the SCADA standards.

#### In the development of an application there may be missing tags not covered in the tagname convention.   To create a new tagname fragment, contact the SCADA Group for approval prior to continuing development.

#### Tagnames are assigned to an alarm group in Level 5+ of the alarm control hierarchy.  Refer to Alarms and Events Strategy for more details.

### Database Development

#### When developing the database, ensure that all tagnames are in CAPITAL letters.

#### Each direct tagname must be fifteen to eighteen characters long depending on whether or not fragment 7 is used.  Tagnames must adhere to the fragment structure as defined in Section 2.  Indirect tags must be ten characters long and adhere to the coding standards.

#### All tags are to have a description.  The Alarm Comment for a Tag shall match its Description.  Tag descriptions will have the First Letter of Each Word Capitalized and all others will be lower case.  The exception to this rule is indirect tags.  Tag descriptions and alarm comments will be a maximum of 49 characters long.  Abbreviations may be used to meet the 49-character limit as long as the purpose of the tag can be easily determined.

#### All tags are to be set to Retentive Value.

#### All integer and real tags are to have a deadband of 0.

#### Logged integer and real tags should have a LogDeadband applied to control growth of the lgh trend file.  The tag template files are pre-programmed with LogDeadbands for standard devices.  As a general guideline, for real time process values this setting should be 1% of the full engineering span (MaxEU-MinEU) of the device.  For any tag performing a counting/accumulation function (Totalizers, Runtime Hours, etc.) the value should be 1.  The SCADA group will make final determination of any settings based on actual process conditions and expected operating tolerances.  If the tag is not logged the LogDeadband is 0.

#### No Tag property fields are to be left blank unless the property has been disabled by some other aspect of the tag configuration.  The exception is Engineering Units if the associated engineering value is dimensionless.

## Device Tag Templates

#### The HMI Template for common devices and ACP functions are provided in Appendix 6A.  Programmers are expected to configure all devices using the appropriate template.

#### The provided programming template worksheets are designed to simplify the amount of configuration by the programmer.  Third party programs may also provide similar functionality.  Regardless of how the tags are created programmers are responsible for ensuring that all tags are in compliance with the Regions tagging standard, that all required device tags are configured correctly and that all optional tags not required for the application are not imported into the InTouch application.

## Standard HMI Graphics

#### Standardized graphics are of critical importance.  Each HMI application should have the same look and feel.

#### Standard application resolution is 1024 pixels by 768 pixels.  Halton Region does permit users to dynamically change resolution.  Due to changes in InTouch operation it is now possible to open Windowmaker at higher monitor resolutions without impacting the native resolution.  Windows will open at their programmed location and programmed pixel size, leaving the rest of the monitor area blank.

#### Halton Region has developed a standardized nomenclature for the creation of HMI windows.  The following is a list of standard windows and the general functionality associated with each window.  Detailed descriptions of the window configuration can be found in other sections of this document.

#### Screens marked as “Legacy” are only present for backwards compatibility with previous versions of the standards and should not be used for new development

| Window Name or Type | Occurrence | Legacy | Function |
| --- | --- | --- | --- |
| 2Device Duty Select | Single | No | Device Assignment for Two Duty Systems |
| 3Device Duty Select | Single | No | Device Assignment for Three Duty Systems |
| 4Device Duty Select | Single | No | Device Assignment for Four Duty Systems |
| About | Single | No | Displays Computer Name and InTouch Version |
| Historian Trend Plant Trend Menu | Single | No | List of all available Historian Trend Trends for the plant. |
| Historian Trend Remote Trend Menu | Single | Yes | List of all available Historian Trend Trends for remote stations |
| Historian Trend Trend | Single | No | Displays graphical trend of Historian Trend Data |
| Historian Trend Trends Menu | Single | Yes | Menu to select Plant or Remote Historian Trend Trends. |
| Advanced Analog | Single | Yes | Analog specific information and control |
| Advanced Analog Units | Single | Yes | Analog specific information and control |
| Advanced Analog v5_0 | Single | No | Analog specific information and control |
| Advanced Analog W/Override | Single | Yes | Analog specific information and control. Also allows the value to be simulated |
| Advanced Analog W/Override_Logix | Single | Yes | Analog specific information and control. Also allows the value to be simulated |
| Advanced Analog_Logix | Single | Yes | Analog specific information and control. |
| Advanced Chemical Pump v1_0 | Single | No | Chemical pump specific information and control |
| Advanced Motor Dual FB v1_0 | Single | No | Motor specific information and control |
| Advanced Motor V1_0 | Single | No | Motor specific information and control |
| Advanced Valve V1_0 | Single | No | Valve Specific information and control |
| Alarm History | Single | No | Display historical Alarms and events |
| Alarm History – SQL | Single | No | Display historical Alarms and events from the SQLExpress database. |
| Alarm Summary | Single | No | Display and acknowledge alarms |
| Alarms | Single | No | Alarm Banner that displays all Alarms and Events |
| Alarms Menu | Single | No | Filter alarms and events to be displayed |
| Analog Device Control | Single | Yes | Analog specific information and control |
| Analog Device Control V5_0 | Single | No | Analog specific information and control |
| Analog Device Control_Logix | Single | Yes | Analog specific information and control |
| Analog Device Control_Units | Single | Yes | Analog specific information and control |
| ATS Control | Single | Yes | ATS specific information and control |
| ATS Control_Logix | Single | Yes | ATS specific information and control |
| Buttons | Single | No | Button Bar used for navigation |
| BXX RT01 Comm Status | Multiple | No | Used to display status of peer-to-peer messaging for a PLC |
| Chemical Pump Control W/Stroke_Logix | Single | Yes | Device specific information and control, including stroke |
| Chemical Pump Control W/Stroke_Units | Single | Yes | Device specific information and control, including stroke |
| Chemical Pump Control | Single | Yes | Device specific information and control |
| Chemical Pump Control v1_0 | Single | No | Device specific information and control, including stroke |
| Chemical Pump Control W/Stroke | Single | Yes | Device specific information and control, including stroke |
| Chemical Pump Control _Logix | Single | Yes | Device specific information and control, including stroke |
| Chemical Pump Control _Units | Single | Yes | Device specific information and control, including stroke |
| Critical Alarm Notice | Single | No | Critical Alarm Notification |
| Critical Alarm Reminder | Single | No | Critical Alarm Reminder Notification |
| Critical Alarm Summary | Single | No | Critical Alarm Summary Page |
| Critical Alarms | Single | No | Critical Alarm object |
| Critical Alarms Acknowledge | Single | No | Critical Alarm object |
| Disabled Critical Alarms | Single | No | Displays a list of disabled critical alarms |
| Duty Rotation | Single | No | Used to set duty rotation mode |
| Duty Select Info Popup | Single | No | Provides help information for duty selection |
| Duty Wet Well | Single | No | Used for setting duty in two transmitter systems |
| Generator v1_0 | Single | No | Generator and ATS Specific Information and Control |
| InTouch Trends | Single | Yes | InTouch Trending Display |
| Legal Entry Status | Single | No | Displays security legal entry status |
| Logix Processor Status | Multiple | No | Displays Logix PLC Diagnostics |
| Modulating Valve Control | Single | Yes | Device specific information and control |
| Modulating Valve Control_Logix | Single | Yes | Device specific information and control |
| Motor Control Dual Feedback v1_0 | Single | No | Motor specific information and control |
| Motor Control v1_0 | Single | No | Motor specific information and control |
| Options Menu | Single | No | Navigation of application options |
| Plant Comm Map | Multiple | No | Display of Plant LAN communications. More than one screen may be needed depending on facility size |
| Plant Trends | Single | Yes | List of all available InTouch trends for the plant |
| Power Monitor v1_0 | Single | No | Displays Power Monitor Information |
| Process Current Setpoints | Multiple | No | Display of auto setpoints |
| Process Setpoints Entry | Multiple | No | Entry of Auto Setpoints |
| Pump Control | Single | Yes | Pump specific information and control |
| Pump Control_Logix | Single | Yes | Pump specific information and control |
| Pump Control_Units | Single | Yes | Pump specific information and control |
| Pumping Station Alarms Page 1 | Multiple | No | Dialer alarms. This windows is intended specifically for Wastewater pump station applications but may be used as a template for any facility with an autodailer |
| Pumping Station Alarms Page 2 | Multiple | No | Dialer alarms. This windows is intended specifically for Wastewater pump station applications but may be used as a template for any facility with an autodailer |
| Pumping Station Alarms Page 3 | Multiple | No | Dialer alarms. This windows is intended specifically for Wastewater pump station applications but may be used as a template for any facility with an autodailer |
| Pumping Station Limits | Multiple | No | Wastewater Pump Station Duty Start/Stop Setpoint Entry |
| Pumping Station Overview | Multiple | No | Wastewater Pump Station Process Overview Screen |
| Pumping Station Setpoints | Multiple | No | Wastewater Pump Station Setpoints Screen |
| Remote Trends | Single | Yes | List of all available InTouch trends for remote stations |
| Server, Workstation, Thin Client | Single | No | List and status of all Servers, Workstations, and Thin Clients associated with an InTouch Application |
| SLC Processor Status | Multiple | Yes | Displays SLC PLC diagnostic Information |
| SPS Overflow Report v1_0 | Multiple | No | Used for Bypass Overflow Reporting |
| Symbols Library – Analog I | Single | No | Sample objects for use on screens |
| Symbols Library – Analog II | Single | No | Sample objects for use on screens |
| Symbols Library – Misc I | Single | No | Sample objects for use on screens |
| Symbols Library – Motors I | Single | No | Sample objects for use on screens |
| Symbols Library – Motors II | Single | No | Sample objects for use on screens |
| Symbols Library – Networking I | Single | No | Sample objects for use on screens |
| Symbols Library – Power I | Single | No | Sample objects for use on screens |
| Symbols Library – Valves I | Single | No | Sample objects for use on screens |
| Symbols Library – Wastewater I | Single | No | Sample objects for use on screens |
| Transmitter 3 Duty | Single | No | Duty assignment for 3 duty transmitter systems |
| Transmitter 4 Duty | Single | No | Duty assignment for 4 duty transmitter systems |
| Trends Menu | Single | Yes | First Submenu for InTouch Trending |
| Trends Selection | Single | No | Selection of InTouch or Historian Trend Trends. |
| Valve Control | Single | Yes | Device specific information and control |
| Valve Control v4_0 | Single | No | Valve specific information and control |
| Valve Control_Logix | Single | Yes | Valve specific information and control |
| Weather Station v1_0 | Single | No | Displays Rain Gauge Information |

- HMI Windows

#### The Button Bar and the Alarm Banner are always displayed and are critical to the proper operation of the HMI Application.  Located between these two (2) windows on the screen is a Process Control window. A process control window shall be visible at all times.  These three (3) windows occupy the entire screen at standard resolution.  Other windows that may appear at the same time are pop-up windows or overlay windows that are displayed on top of the three (3) main windows.   The following diagram depicts this layout.

- Button Bar and Alarm Banner

## Colours

#### The following tables document the colour standards used in Halton Region’s SCADA systems.  Any deviation from these standards, or the use of additional colours not identified in the following tables must be approved by Halton Region prior to proceeding with development of the HMI graphics.

#### If a colour is discussed that does not appear in these tables, the RBG value will be provided in brackets following the colour name.

#### Process Stream (Piping/Vessel Contents) Colour Conventions

| Element | Colour Name | Red | RBG Blue | Green |
| --- | --- | --- | --- | --- |
| Potable Water | Cyan | 0 | 255 | 255 |
| Raw Water | Dark Blue | 0 | 255 | 0 |
| Air | Light Blue | 200 | 255 | 255 |
| Chlorine (Liquid) Chlorine (Gas) Aluminum Sulphate Ammonia Polymer Sulphur Dioxide Fluoride Ferric Chloride Natural Gas Digester Gas | Chemicals: Orange Steam/Gases: Yellow With cross-hatched background | 255 255 | 0 0 | 130 255 |
| WTP/WWTP Sludges WTP Backwash Waste WWTP RAS/WAS WTP Settled Backwash WWTP Supernatant | Brown | 132 | 0 | 0 |

- Process Steam Colour Conventions

#### Device/Status Colour Conventions

| Device/Status | Colour Name | Red | RBG Blue |  | Green |  |
| --- | --- | --- | --- | --- | --- | --- |
| Pump/Motor |  |  |  |  |  |  |
| Running | Red (with text) | 255 |  | 0 |  | 0 |
| Off | Green (with text) | 0 |  | 0 |  | 255 |
| Unacknowledged Alarm | Flashing Magenta | 255 |  | 255 |  | 0 |
| Acknowledged Alarm | Solid Magenta | 255 |  | 255 |  | 0 |
| Valve |  |  |  |  |  |  |
| Opened | Red (with text) | 255 |  | 0 |  | 0 |
| Transition (Discrete) | Half Red/Half Green |  |  |  |  |  |
| Closed | Green (with text) | 0 |  | 0 |  | 255 |
| Modulating | Percentage open is displayed beside the valve. Valve colour is Green <= 5% open and Red > 5% open. | 0 255 |  | 0 0 |  | 255 0 |
| Isolating/Device Not controllable from SCADA | Grey | 128 |  | 128 |  | 128 |
| Unacknowledged Alarm | Flashing Magenta | 255 |  | 255 |  | 0 |
| Acknowledged Alarm | Solid Magenta | 255 |  | 255 |  | 0 |
| Yellow Box Alarm | Solid Yellow | 255 |  | 0 |  | 255 |
| Miscellaneous |  |  |  |  |  |  |
| HIHI/LOLO Alarm | Flashing Magenta | 255 |  | 255 |  | 0 |
| HI/LO Alarm | Flashing Yellow | 255 |  | 0 |  | 255 |
| Analog Alarm Box | Grey Fill Black Border | 198 0 |  | 198 0 |  | 195 0 |
| Background | Process – White Control – Black | 255 0 |  | 255 0 |  | 255 0 |
| Text | Description: White on Pop-Up & Black on Process Screen | 255 0 |  | 255 0 |  | 255 0 |

- Device/Status Colour Conventions

## Process Piping Colours

#### Line Colours should use those specified in the process stream convention.

## Standard Symbols

#### Halton Region adheres to ISA standards for two-dimensional representations of devices unless specifically identified otherwise.

#### Halton Region does not use pictures, three dimensional symbols, or device symbols which show how the device physically appears in the field.  The intent is to have the HMI match the P & ID process flow drawings, so that anyone looking at the HMI can understand the system operation.

#### In the event that a Programmer in the development of an HMI application must create a new symbol, or wishes to modify an existing symbol, the symbol must be submitted to Halton Region’s SCADA group for approval before commencing development.

#### Programmers are permitted to modify action scripts to suit the device configuration as outlined in the PLC UDT Programming Guides.

#### Halton Region has adopted a number of graphical symbols through the implementation of SCADA systems in several of Halton Region’s water and wastewater systems.  Standard graphical symbols appear on the “Symbols Library” screens in the InTouch Baseload.

#### Most of these symbols have the appropriate scripts attached to change the colours of the device given the device state, visibility links, alarm state, and pop-up control.  Devices that represent static objects without any animations or controls are indicated as such.

#### Programmers developing applications for Halton Region should refer to the most recent libraries.

#### Most symbols are available in a variety of sizes.  Choose a device size appropriate to the complexity and detail of the process screen.

#### Programmers are not to resize any symbols.  If any of the available sizes are insufficient for the application the programmer shall contact the Halton Region SCADA group for guidance.

#### Halton Region has final approval of the placement of all graphical objects and reserves the right to request objects be moved if their placement is deemed inappropriate.

### Pumps

- Pumps

### Valves

- Valves

#### Solenoid valves are shown as uncontrolled valves

### Diesel Generators

- Diesel Generators

#### The above diesel generator is shown with a fuel tank graphic.

#### When a generator has an external fuel tank, the tank should be shown with a process line connection to the generator.  When the generator has a skid-mounted fuel tank, it should be displayed beneath the generator.

#### A fuel tank graphic is not required if the tank level is not available for connection to SCADA.

### Automatic Transfer Switches

- Automatic Transfer Switches

### U.V. Reactors

#### These symbols are typically developed by the UV vendor.

### Mixers

- Mixers

#### The size of mixer graphic uses should be consistent in each HMI application.

#### In cases where a process has mixers of different capacities, using a larger mixer graphic to indicate the larger horsepower is acceptable.

### Reservoirs/Clear wells

- Reservoirs/Clear Wells

#### The text box indicates the location and capacity of the reservoir

#### Below the text box the level will be displayed.

#### The above cyan cell fills based upon the level

### Elevated Tanks

- Elevated Tanks

#### The cyan text within the tank will fill proportionally to the tank’s level

### Well Sites (North Halton Water Only)

- Well Sites (North Halton Water Only)

#### The well graphic is only required to fill if the well in monitored for level.

### Chemical Storage Tanks

- Chemical Storage Tanks

#### Chemical tanks and chlorine tonners fill based upon level or weight.

#### If the tank is not monitored for level, the tank should still be shown to indicate where the pump or chlorinator draw their chemical feed from.  Programmers should simply disable the animation fill graphic.

#### If the chemical is not already assigned a colour, Programmers should contact the SCADA group.

### Process Analog Displays

- Process Analog Displays

#### Process analog displays use a standard analog device control.  See Analog Device Control for more information.

#### It is acceptable to group multiple analog inputs for a process area or subsection of a process area together in a black display box, as shown above.  The white description text should be set so that the device purpose or function can be readily identified.

#### It is also acceptable practice to place the analog display at the location where it is in the process.  As an example placing a motor current under a blower is acceptable.

#### Analog inputs can be shown on multiple Windows if required by operations.

### Traveling Screens

- Traveling Screens

### Hot Water Boiler

- Hot Water Boiler

### Containment Well

- Containment Well

### Gas Compressor

- Gas Compressor

### Waste Gas Burner

- Waste Gas Burner

### Digester

- Digester

#### Digesters monitored for level can fill in the rectangular portion of the graphic.

### Wastewater Standpipe

- Standpipe

### Heat Exchanger

- Heat Exchanger

### Secondary Digester (Gas Holding Tank)

- Secondary Digester (Gas Holding Tank)

### Sludge Hauling Truck

- Sludge Hauling Truck

#### Sludge tank huller trucks are shown on locations where sludge is hauled away.

### Round Tank

- Round Tank

### Static Mixer

- Static Mixer

### Parshall Flume

- Par Shall Flume

### Scum Hopper

- Scum Hopper

### Grit Classifier

- Grit Classifier

### Grit Bin

- Grit Bin

### Sludge Storage Tank (Floating Cover)

- Sludge Storage Tank (Floating Cover)

### Square Tank

- Square Tank

### Wet Well

- Wet Well

#### The current level is displayed below the wet well.

#### The green box will fill and empty based upon the level

#### Wastewater pumping stations have a more detailed level of HMI standards for wet wells and sewage lift pumps.

### Weir Plate and Gate

- Weir Plate and Gate

### Aeration Blower

- Aeration Blower

#### Aeration blowers use the same graphic as pumps. In this example the graphic has been rotated.

### Line Thickness

#### The thickness of the line depends upon the size of the graphic connecting to the device.

- Aeration Blower Line Thickness

#### This is the recommended size for most process lines. The line is 3 pixels high. Examples include, Wastewater pumping, Raw/Finished water, RAS/WAS.

### Process Line Connections

#### When process lines are shown as connected, it indicates a common header.

- Common Header Process Line Connections

#### When process lines must cross, but there is no connection between the two lines, one (1) of the lines must stop prior to connecting to the other process and then continue on the other side.  An example is shown below (cyan lines).

- Crossing Process Lines

#### Programmers should consistently break the same process line.

## Implementing a Symbol from the Halton Symbols Library

#### A Programmer can implement a library symbol in an HMI application through modifications to the tagnames associated with the library symbol.  This can be accomplished by following these steps.

##### Open the appropriate Symbols Library window;

##### With the mouse, highlight a complete symbol by drawing a box around the symbol with the mouse;

##### Copy and paste the symbol to the process control window; with the complete symbol still selected, perform a Substitute tags operation to update the placeholder tags with the device tags.

##### Open the InTouch action script for the pop-up and verify that all configuration options are correct for the intended operation of the device.

## Device Identification Label

#### For all devices depicted by a symbol, there must be an identification label below the symbol.  The label is defined using Fragment Three of the Halton Region SCADA and Equipment Coding Standards.    An example of a device identification label is “LLP1” for Low Lift Pump One (1).

- Device Control

#### This label is also used to inform the operator of the control mode that the device is currently in by changing the colour of the label as follows:

##### Local Mode – Label is displayed in GREEN;

##### Plant Manual Mode – Label is displayed in BLUE; and,

##### Plant Auto Mode – Label is displayed in RED .

#### This can be accomplished by having three (3) lines of text superimposed on one another, each with one of the three (3) above characteristics.  The following screens are found by right clicking on the text and choosing Animation Links => Miscellaneous => Visibility.

#### The green label will only be visible when the device is not in Remote mode.

- Device Identification – Green Label

To avoid confusion; do not use the Visible State “Off” radio button.  Use the ‘NOT’ operator in the expression as is displayed above.

#### The blue label is only visible when the device is in Plant Manual mode.

- Device Identification –Blue Label

#### The red label is only visible when the device is in Plant Auto mode.

- Device Identification – Red Label

#### All identification labels are to be in capital letters.  The font type is MS Sans Serif, Bold 8 point.

## Device Alarm Box

#### All devices depicted by a graphic symbol that have an alarm group, also display an “alarm box” to offer the operator a visual indication that an alarm exists for the device.

#### A device alarm is displayed using a square “alarm box” in the middle of the device graphic.  When the device is in alarm the “alarm box” will indicate an alarm by turning magenta and flashing.  When the alarm is acknowledged through the HMI, the “alarm box” will stop flashing and will become solid magenta, while the alarm continues to exist.  Once the alarm condition has been cleared in the field, and has been acknowledged in the HMI, the “alarm box” will return to white signifying that there are no alarms related to the device.

### Animation Links

#### There are two (2) animation links that are used for a device alarm box:

##### Fill Colour => Discrete; and,

##### Miscellaneous => Blink.

### Fill Color => Discrete

- Animation Links Fill Color => Discrete

### Miscellaneous => Blink

- Animation Links Fill Miscellaneous => Blink

## Pump Graphic

This section of the standard addresses the proper graphical representation of a pump (both fixed and variable speed) within Halton Region’s HMI applications.  Note that all other electromechanical type devices (with the exception of Generators) should be configured using this standard.  Examples of other devices include, but are not limited to, mixers, blowers, traveling screens, grit classifiers, and bar screens.

### Animation Links

#### There are three (3) animation links that are used for a pump:

##### Fill Colour => Discrete;

##### Miscellaneous => Disable; and,

##### Touch Pushbuttons => Action => On Key Up.

### Fill Color => Discrete

#### A pump graphic on a process screen that is controllable by the operator is displayed using the following convention:

##### PUMP RUNNING	- RED

##### PUMP OFF	- GREEN

#### Fill Color is used to change the pump red to signify that the pump is running, or green to signify that the pump is stopped.  A discrete status tag will exist for all on/off devices with a value of 1 signifying the device is running and a value of 0 signifying the device is stopped.  An example of this is displayed in the figure below.

- Pump Graphic Fill Colour

### Miscellaneous => Disable

#### The Miscellaneous => Disable setting is used to set a security level on the device so that a user must log in with a user name that has the proper privileges to control the device.  A memory integer tag ‘ACL_PUMP’ with the description ‘Pump Access Level’ is used to set the security level of a device.

- Pump Graphic Miscellaneous => Disable

#### All on/off devices that use the same device control such as mixers, should use the same ACL_PUMP tag and all of the associated indirect tags.

#### Touch Pushbuttons => Action => On Key Up Action Script maps tags to the pump pop-up.  Consult the UDDT programming guide for details on configuring the action script for various device types.

### Status in Text Form

#### The pump graphic is accompanied by a text block located beside the graphic to indicate the state of the device.  When the pump is running, the word “On” appears in red, and when the pump is off, the word “Off” appears in green.  These two (2) lines of text are controlled using visibility links.  The text block “On” is only visible when the status tag of the device = 1 as displayed in the figure below.

- Pump Graphic Text Block “On”

#### The text block “Off” is only visible when the status tag of the device = 0 as displayed in the figure below.

- Pump Graphic Text Block “Off”

#### The font for these text blocks is System, Bold 10 point.

To avoid confusion; do not use the Visible State “Off” radio button.  Use the ‘NOT’ operator in the expression as is displayed above.

### Flow Capacity Label

#### The rated flow capacity of each pump may be displayed directly below the device state indication in black text if required.  The font to use for this line of text is System, Bold 10 point.

### Pump Identification Label

#### The device identification label should appear immediately below the device.

### Device Alarm Box

#### A device alarm box is necessary for all pumps and other on/off type devices that are controlled by the HMI system and have an alarm group defined for the device.

## Discrete Valve Graphic

The graphic principles for a controllable fixed position valve are very similar to that of a pump.  Pump On is synonymous with Valve Open and Pump Off is synonymous with Valve Closed.

### Animation Links

There are three (3) animation links that are used for a valve:

##### Fill Colour => Discrete;

##### Miscellaneous => Disable; and,

##### Touch Pushbuttons => Action => On Key Up.

### Fill Color => Discrete

A valve graphic on a process screen that is controllable by the operator is displayed using the following convention:

##### VALVE OPENED			- RED

##### VALVE CLOSED			- GREEN

##### VALVE IN TRANSITION	- RED/GREEN.

#### Fill Color is used to change the valve colour red to signify that the valve is open, or green to signify that the valve is closed.  One or two discrete status tags will exist for all fixed valves.  If only one tag is used, then a value of 1 will signify that the valve is open and a value of 0 will signify that the valve is closed.  The more common system uses two discrete tags; one to signal that the valve is fully open and one to signal that the valve is fully closed.  In this case the left half of the valve symbol will use the fully closed tag.  An example of this is displayed in the figure below.

- Discrete Valve Graphic Fill Colour

#### The right half of the valve will use the fully opened tag.  An example of this is displayed in the figure below.   Note how the colours are reversed.

- Discrete Valve Graphic Fully Opened Tag

#### A valve in transition will be neither fully closed nor fully opened.  In situations such as this the valve will display both colours indicating a transition in progress.

#### The opening direction of a valve on the HMI is based upon process flow.  The side closest to the pump or source of flow should open first.  This example was for a valve that opens left to right.  Valves that open right to left will be reversed.

### Miscellaneous => Disable

#### The Miscellaneous => Disable setting is used to set a security level on the valve so that a user must log in with a user name and password that has the proper privileges to control the valve.  A memory integer tag ‘ACL_VLV’ with the description ‘Valve Access Level’ is used to set the security level of a device.

#### Since the valve itself is small, a box is drawn around the valve graphic and the Miscellaneous => Disable setting as well as the Touch Pushbuttons settings are attached to this box.  Above this box is displayed in light grey for clarity.  When used in an application the box should be invisible.

- Discrete Valve Graphic Miscellaneous => Disable

#### Note in the above example the user access level must be greater than ACL_VLV which equals 5000 in order to control the valve.

#### Touch Pushbuttons => Action => On Key Up Action Script maps tags to the pump pop-up.  Consult the UDDT programming guide for details on configuring the action script for various device types.

#### The valve graphic is accompanied by a text block located below the graphic to indicate the state of the device.  When the valve is open, the word “Opened” appears in red, and when the valve is closed, the word “Closed” appears in green.  These two (2) lines of text are controlled using visibility links.  The text block “Opened” is only visible when the valve open status tag equals 1 (ON) as displayed in the figure below.

- Discrete Valve Graphic “Opened”

#### The text block “Closed” is only visible when the valve closed status tag equals 1 (ON) as displayed in the figure below.

- Discrete Valve Graphic “Closed”

#### The font for these text blocks is System, Bold 10 point.

### Valve Identification Label

#### The device identification label should appear immediately below the device.

### Valve Alarm Box

#### An alarm box is necessary for all valves that are controlled by the HMI system and have an alarm group defined for the device.

## Modulating Valve Graphic

The modulating valve graphic is very similar to the fixed valve graphic.  The only difference is that the modulating valve is not considered open (red) until its valve position is greater than 5% open.

### Animation Links:

#### There are three (3) animation links that are used for a valve:

##### Fill Colour => Discrete;

##### Miscellaneous => Disable; and,

##### Touch Pushbuttons => Action => On Key Up.

### Fill Color => Discrete

#### A modulating valve graphic on a process screen that is controllable by the operator is displayed using the following convention:

##### VALVE OPENED	(>5%)		RED

#### This is set by using two memory integer tags of

##### VLVMV_OD

#### These tags have an initial value of 5.  The values of these tags are controlled by Halton Region.  Programmers should not update these tags.

#### Fill Color is used to change the valve colour red to signify that the valve is greater than 5% open, or green to signify that the valve is less than or equal to 5% open, using the analog position current value feedback.  If the position feedback value is greater than 5% this signifies that the valve is open.  If the position feedback tag is less than or equal to 5%, the modulating valve is considered closed.

#### There is only one position feedback tag, thus both sides of the valve use the same Animation Links => Fill Colour => Discrete, shown below:

- Modulating Valve Graphic Opened Fill Colour

### Miscellaneous => Disable

#### The Miscellaneous => Disable setting is used to set a security level on the valve so that a user must log in with a user name and password that has the proper privileges to control the valve.  A memory integer tag ‘ACL_VLV’ with the description ‘Valve Access Level’ is used to set the security level of a device.

#### Since the valve itself is small, a box is drawn around the valve graphic and the Miscellaneous => Disable setting as well as the Touch Pushbuttons settings are attached to this box.  This box is displayed in light blue for clarity.  When used in an application the box should be invisible.

- Modulating Valve Graphic Miscellaneous => Disable

#### Touch Pushbuttons => Action => On Key Up Action Script maps tags to the pump pop-up.  Consult the UDDT programming guide for details on configuring the action script for various device types.

### Status in Text Form

#### The valve graphic is accompanied by a text block located below the graphic to indicate the state of the device.  When the valve is open, the word “Opened” appears in red, and when the valve is closed, the word “Closed” appears in green.  As with the valve fill colour, these two (2) lines of text are controlled using visibility links.  The text block “Opened” is only visible when the current valve position status tag > 5% as displayed in the figure below.

- Modulating Valve Graphic “Opened”

#### The text block “Closed” is only visible when the current valve position status tag < 5% as displayed in the figure below.  Again VLVMV_OD is an indirect tag that is set to 5%.

- Modulating Valve Graphic “Closed”

#### The font for these text blocks is System, Bold 10 point.

### Valve Identification Label

#### The device identification label should appear immediately below the device.

### Valve Alarm Box

#### A valve alarm box is necessary for all valves that are controlled by the HMI system and have an alarm group defined for the device.  For a modulating valve the alarm box is represented by a half circle to distinguish it from a fixed valve.

### Position Feedback Text

#### The modulating valve has a black numeric feedback display of the current position.  This text block is located directly below the opened/closed status label.  The font to use for this text block is MS Sans Serif, Bold 12 point.

## Weir Plate and Gate

Weir Plates and gates use the exact same scripts and animation as discrete and modulating vales.  See Sections 6.22 and 6.23 for details.

#### Weir Plates and gates can be either modulating or discrete.  Programmers are required to apply the correct valve control animation links.

#### Weir gates use an Animation Links => Percent Fill => Vertical, based upon the position feedback value.

#### Gates use Opened and Closed graphics for the “Green” potions.

## Device with no Auto Control

#### In some cases, devices are connected to SCADA and either are monitored for status, or have no PLT-AUTO operation.

#### A device that is monitored for status only does not have any of the Touch Pushbuttons => Action => On Key Up scripts.  It has all of the animation fills, an example of a monitored only device is a singer valve located in front of a high lift pump.  The valve is monitored for opened and closed status, but SCADA cannot control the valve.  This valve would turn Red and Green based upon the opened and closed status.

#### The device control label for a device with no SCADA control is shown in Black text.  If local controls for the device are available, the device control label is shown in Green text.  It also has no device alarm box.

### Devices with no PLT-AUTO Scripting

#### A device that has no PLT-AUTO control is one that operations can operate in PLT-MAN as required.  An example is an aeration tank mixer.  Operations will start and stop the mixer as required.

#### If a device does not have PLT-AUTO code the Action Script shall be modified to map a null string to the PLT-MAN request pushbutton and PLT-AUTO status indirect tags. .

## Analog Display Graphics

Halton Region’s standard for the display of analog values consists of both a numeric display, and where appropriate, a graphical display.  (The graphical display is typically used to display the level of a fluid or gas in a container.)  If this a calculated value, then “CALC” needs to appear beside the graphic and in the tag description. The numeric display has seven (7) different components as identified below:

##### Normal analog value text block (black ###);

##### HI / LO Alarm value text block (yellow ###);

##### HIHI / LOLO Alarm value text block (magenta ###);

##### Off Scan text block (magenta ???);

##### Engineering unit text block (black); and,

##### Analog alarm box.

##### Disabled Analog Alarms Yellow Dot

#### The first four (4) components are “stacked” on top of one another since only one is visible at any time.  The black engineering units’ text block displayed above is the “mg/L” text.  This sits on top of the analog alarm box.  The final component is the disabled analog alarms yellow dot.

#### The colours and font sizes for the five (5) text blocks are as follows:

### Analog Display Fonts

| State | Font | Colour | R/B/G | Border | Background |
| --- | --- | --- | --- | --- | --- |
| Normal | 10 pt. MS Sans Serif Bold | Black | 0/0/0 | None | Screen Colour |
| HI / LO |  | Yellow | 255/0/255 | Black | Grey |
| HIHI / LOLO |  | Magenta | 255/255/0 | Black | Grey |
| Off Scan |  | Magenta | 255/255/0 | None | Screen Colour |
| Eng. Units |  | Black | 0/0/0 | None | Screen Colour |

- Analog Display Fonts

### Animation Links for the Normal Analog Value Text Block

#### There are two (2) animation links that are used for the normal analog value text block:

##### Value Display => Analog

##### Miscellaneous => Visibility

### Value Display => Analog

#### The Value Display => Analog is the tag which represents the current value of the analog signal to be displayed in this text block.  This is displayed in the following figure.

- Analog Display Graphics Value Display => Analog

### Miscellaneous => Visibility

#### The Miscellaneous => Visibility setting is used by the application to determine when the normal value text block is to be visible.  If the analog signal is on scan and there are no HI, HIHI, LO, LOLO or Signal Error alarms, this block of text will be visible.  An example of this is displayed in the figure below.

- Analog Display Graphics Miscellaneous => Visibility

### Animation Links for the HI / LO Analog Value Text Block

#### There are three (3) animation links that are used for the HI / LO analog value text block:

##### Value Display => Analog;

##### Miscellaneous => Visibility; and,

##### Miscellaneous => Blink.

### Value Display => Analog

#### The Value Display => Analog is the tag which represents the current value of the analog signal to be displayed in this text block.  This is displayed in the following figure.

- Analog Display Graphics Value Display => Analog

### Miscellaneous => Alarm Visibility

#### The Miscellaneous => Visibility setting is used by the application to determine when the HI / LO analog text block is to be visible.  If the analog signal is on scan and a HI or LO alarm exists but no HIHI, LOLO or signal error alarms, this block of text will be visible.  An example of this is displayed in the figure below.

- Analog Display Graphics Miscellaneous => Alarm Visibility

### Miscellaneous => Unit Visibility

#### .10 The Miscellaneous => Visibility setting is used by the application to determine when the Engineering Unit is to be visible.  If the PLC tag value is 2 then 2 engineering units will display. If there is a 3 in the PLC tag then 3 engineering units will display. An example of this is displayed in the figure below.

- Analog Display Graphics Miscellaneous => Unit Visibility

### Miscellaneous => Blink

#### The Miscellaneous => Blink setting is used by the application to determine when the HI / LO analog text block is to blink.  If the analog signal is on scan and there is a HI or LO alarm but no HIHI or LOLO alarms, and there is an unacknowledged alarm for this analog alarm group, this block of text will blink.  An example of this is displayed in the figure below.

- Analog Display Graphics Miscellaneous => Blink

### Animation Links for the HIHI / LOLO Analog Value Text Block

#### There are three (3) animation links that are used for the HIHI / LOLO analog value text block:

##### Value Display => Analog;

##### Miscellaneous => Visibility; and,

##### Miscellaneous => Blink.

### HIHI/LOLO Alarms

#### The Value Display => Analog is the tag which represents the current value of the analog signal block.  This is displayed in the following figure.

- Analog Display Graphics HIHI/LOLO Alarms

#### The Miscellaneous => Visibility setting is used by the application to determine when the normal analog text block is to be visible.  If the analog signal is on scan and there is a HIHI or LOLO alarm and not a Signal Error alarm, this block of text will be visible.  An example of this is displayed in the figure below.

- Analog Display Graphics Miscellaneous => Visibility

#### The Miscellaneous => Blink setting is used by the application to determine when the normal analog text block is to blink.  If the analog signal is on scan, there is not a signal error and there is a HIHI or LOLO alarm, and there is an unacknowledged alarm for this analog alarm group, this block of text will blink.  An example of this is displayed in the figure below.

- Analog Display Graphics Miscellaneous => Blink

#### There are two (2) animation links that are used for the Off Scan text block:

##### Miscellaneous => Visibility; and,

##### Miscellaneous => Blink.

#### The Miscellaneous => Visibility setting is used by the application to determine when the Off Scan text block is to be visible.  If the analog signal is not on scan, this block of text will be visible.  An example of this is displayed in the figure below.  The Off Scan text block, as depicted by a series of question marks, is used to inform the Operator that the analog device is not communicating or is out of range/calibration.

- Analog Display Graphics Miscellaneous => Visibility

#### The Miscellaneous => Blink setting is used by the application to determine when the Off Scan text block is to blink.  If the analog signal is off scan, or has a Signal Error and there is an unacknowledged alarm for this analog alarm group, this string of question marks will blink.  An example of this is displayed in the figure below.

- Analog Display Graphics Miscellaneous => Blink

### Engineering Unit Text Block

#### There are no animation links associated with the Engineering Unit text block.  It is used to display the engineering unit associated with the analog device.

### Animation Links for the Analog Alarm Box

#### There are four (4) animation links that are used for the analog alarm box:

##### Line Color => Discrete;

##### Fill Color => Discrete;

##### Miscellaneous => Disable; and,

##### Touch Pushbuttons => Action => On Key Up.

### Line Color => Discrete

#### The Line Color => Discrete link is used to turn the analog alarm box black and thus visible if there is an alarm in the analog alarm group.  Therefore, when the device is in alarm a box will appear around the analog value.  An example of this setting is displayed in the following figure.

- Analog Display Graphics Miscellaneous => Line Colour

### Fill Color => Discrete

#### The Fill Color => Discrete link is used to turn the analog alarm box fill grey and thus visible if there is an alarm in the analog alarm group.  For instance, when the device is in alarm a grey background will appear behind the analog value.  An example of this setting is displayed in the following figure.

- Analog Display Graphics Fill Colour => Discrete

### Miscellaneous => Disable

#### The Miscellaneous => Disable setting is used to set a security level on the analog device so that a user must log in with a user name and password that has the proper privileges to control the device.  A memory integer tag ‘ACL_ANIN’ with the description ‘Analog Access Level’ is used to set the security level of the device.

- Analog Display Graphics Miscellaneous => Disable

### Touch Pushbuttons => Action => On Key Up

#### Touch Pushbuttons => Action => On Key Up Action Script maps tags to the pump pop-up.  Consult the UDDT programming guide for details on configuring the action script for various device types.

### Disabled Analog Alarms Yellow Dot

#### A yellow dot located beside the analog display graphic is to indicate that at least one of the alarm parameters has been disabled.  The alarm group of the disabled analog will also appear on the “Disabled Alarms” alarm summary page.

- Disabled Analog Alarms Yellow Dot

### Graphical Display of Analog Value

#### For analog values that represent “level” in a reservoir, standpipe, wet well, or storage tank, a graphical display is created to indicate the current level.  This graphical display is used to show how full the vessel is based upon the level.  A text string is placed near the vessel, indicating which analog value is being displayed.  The text sting is System, Bold, 10 Point Font and Black in colour.

#### An example of a graphical display is the level of fluid in a tank such as the Alum tank displayed below.  The fluid level in the tank varies from 0 to 100% depicting the current value that is displayed in the text box located above it.

- Analog Display Graphics Graphical Display of Analog Value

#### Set the animation link Percent => Fill for the box that represents the fluid to the following.

- Analog Display Graphics Vertical Fill => Analog Value

#### The background colour will be the same colour as the window, white.

## Button Bar

#### Halton Region has a standard screen layout.  The “Button Bar” identified in the layout is used for navigation and the selection of options.  The button bar is part of the base application.  The button bar window is displayed in the graphic below.

- Button Bar

#### The properties of the Button Bar window are as follows:

| Window Properties | R/B/G |
| --- | --- |
| Window Colour | Blue (0/255/0) |
| Window Type | Overlay |
| Frame Style | Single |
| Title Bar | No |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | -1 0 1028 38 |
| Window Scripts | None |

- Button Bar Properties

#### The following subsections describe each button or display window on the button bar in greater detail.

### Login Name Display

#### On the far left side of the button bar is a small black window that displays the name of the user currently logged into the HMI application.  The box is 114 pixels wide by 29 pixels high.  The box has black fill with a thin grey border.

#### In the center of the black box is a white text block.  The Animation Link => Value Display => String for the login name display is ‘$Operator’.

### ‘Exit’ Button

#### The size of the ‘Exit’ button is 58 pixels wide by 30 pixels high.

#### The ‘Exit’ button is used to close all control pop-up type windows.  Typically, it should not be used to close process control windows.  Depending on the HMI application being developed, the Programmer may elect to use the ‘Exit’ button to close other miscellaneous type windows.  Programmers wishing to close miscellaneous windows with the Exit button should notify Halton Region before proceeding.

#### The following windows must be closed when the ‘Exit’ button is selected:

##### "Alarms Menu";

##### "Alarm History";

##### "Alarm Summary";

##### "InTouch Trends";

##### "SCADA Node Status";

##### "Burlington Runtimes";

##### "Distribution System";

#### The Burlington Runtimes and Distribution System close commands are examples of how the windows closed will change on an application by application basis.  The intent of the exit button is to close all windows but the five configured “Home” windows.

#### The ‘Exit’ button is also used to open the Alarms Banner window.  This ensures that the Alarms Banner is reopened in the event that it is accidentally closed.

#### An example of the Animation Links => Touch Pushbuttons => Action => On Key Up script for the ‘Exit’ button is shown below:

Hide "Alarms Menu";

Hide "Alarm History";

Hide "Alarm Summary";

Hide "InTouch Trends";

Hide "SCADA Node Status";

Hide "Burlington Runtimes";

Show "Distribution System";

Show "Alarms";

### ‘Alarms’ Button

#### The ‘Alarms’ button is 75 pixels wide by 30 pixels high.

#### The ‘Alarms’ button is used to open the “Alarms Menu” window.  From this menu the user can select the priority and group of alarms to be displayed.    The user can the group of alarms to be displayed by selecting one of the alarm group buttons.  The “Alarms Summary” window will open, and display the alarms associated with the selected alarm group.  Users can also press the “critical” alarms button to display a summary of all critical alarms for the entire application.

#### For a more in-depth discussion of the “Alarms Summary” window and the “Alarms Menu” window, refer to Alarms and Events Strategy.

#### An example of the Animation Links => Touch Pushbuttons => Action => On Key Up script for the ‘Alarms’ button is displayed below:

BUTT_NUM=1;

ALRM_MIN = 1;

ALRM_MAX = 999;

ALRMCRIT = 0;

Hide "Alarm Summary";

Hide "Alarm History";

Hide "Critical Alarm Summary";

Show "Alarms Menu";

Show "Alarms";

‘History’ Button

#### The ‘History’ button is 75 pixels wide by 30 pixels high.

#### Selecting the ‘History’ button will open the “Alarms Menu” window.  The user can select the group of alarms and events to be displayed by selecting one of the alarm group buttons.  The “Alarms History” window will open, and display the alarms associated with the selected alarm group.

#### For a more in-depth discussion of the “Alarms Summary” window and the “Alarms Menu” window, refer to Alarms and Events Strategy.

#### An example of the Animation Links => Touch Pushbuttons => Action => On Key Up script for the ‘History’ button is shown below:

BUTT_NUM=2;

ALRM_MIN = 1;

ALRM_MAX = 999;

Hide "Alarm Summary";

Hide "Alarm History";

Hide "Critical Alarm Summary";

Show "Alarms Menu";

Show "Alarms";

#### BUTT_NUM is used by the alarms menu to determine if the operator wishes to see the Alarm History or the Event History.

### ‘Process’ Button

#### The ‘Process’ button is 72 pixels wide by 30 pixels high.

#### Selecting on the ‘Process’ button will open the main process overview window for a given SCADA system.  In the case of the Mid Halton Wastewater Treatment Plant, the Animation Links => Touch Pushbuttons => Action => On Key Up script for the ‘Process’ button would be:

##### Show “Mid Halton Process Overview”;

### ‘Systems’ Button

#### The ‘Systems’ button is 71 pixels wide by 30 pixels high.

#### The ‘Systems’ button is designed to open the main distribution /collection system window.  This window will display an overview of the entire treatment / collection / distribution system including all of the remote locations.  From this window it will then be possible to navigate into each of the plant and remote screens by clicking on the various location symbols.

#### An example of the Animation Links => Touch Pushbuttons => Action => On Key Up script for the ‘System’ button would be:

##### Show "Distribution System";

### Reports’ Button

#### The ‘Reports’ button is 67 pixels wide by 30 pixels high.

#### Each plant has its own style of reports. So, when updating the reports, the same style and content as the existing report should be used for any expansions.

### ‘Trends’ Button

#### The ‘Trends’ button is 67 pixels wide by 30 pixels high.

#### The “Trends” button is used to open a smaller pop-up type window, which offers the operator to choose either InTouch trends or Historian Trend trends. The selection of either will bring up additional sub-menus that provide a list of available trends.

#### The following graphic displays a sample trend selection menu pop-up window.

- Button Bar Reports’ Button

#### Selection InTouch trends will bring up a sub menu of the available InTouch trends.

- Button Bar Available Trends

#### Selecting Raw Water will bring up a further sub-menu with the available Raw Water Trends.

#### An example of the Animation Links => Touch Pushbuttons => Action => On Key Up script for the ‘Trends’ button would be:

##### Hide "InTouch Trends";

##### Hide "InTouch Trends II";

##### Show "Trends Selection";

#### For an in-depth discussion on the scripting associated with a specific trends button, refer to InTouch Trends.

### ‘Options’ Button

#### The ‘Options’ button is 63 pixels wide by 30 pixels high.

#### The ‘Options’ button is similar to the ‘Trends’ button.  Selecting the ‘Options’ button will open a pop-up type window displaying additional buttons.  The options available will be system dependent, but should include as a minimum, where available, the following information.

##### Autodialer Alarm Enabling window(s);

##### Communication Map;

##### Workstation Comm Status

##### PLC Status;

##### About;

#### The ‘Options’ button does not have any security attached to it, however, the Autodialer Alarm Enabling does.

### ‘Setpoints’ Button

#### The ‘Setpoints’ button is 73 pixels wide by 30 pixels high.

#### The ‘Setpoints’ button is used to open the setpoint screen associated with the process control window that is currently being displayed.  Each process control window has its own unique window number.  Selection of the ‘Setpoints’ button will display the setpoint window associated with the currently displayed process control window number.  The value used by each window should match the indexing number that InTouch applied to the window. The ww_wdws.NDX file located in the application folder contains this information.

#### A partial example of the Animation Links => Touch Pushbuttons => Action => On Key Up script for the ‘Setpoints’ button is as follows.

IF WINDOW == 100 THEN

Show "Oakville Alum Pumps Setpoints";

ENDIF;

IF WINDOW == 101 THEN

Show "Oakville Ammoniators Setpoints";

ENDIF;

IF WINDOW == 102 THEN

Show "Oakville Chlorinators Setpoints";

ENDIF;

IF WINDOW == 106 THEN

IF FILT_NUM == 1 THEN

FILARAI_CV.Name = OWFFG01ARAI_CV.Name;

FILARAO_CT.Name = OWFFG01ARAO_CT.Name;

FILARPB_SU.Name = OWFFG01ARPB_SU.Name;

FILARDA_EE.Name = OWFFG01ARDA_EE.Name;

FILBWAI_AS.Name = OWFFG01BWAI_AS.Name;

FILBWAO_AS.Name = OWFFG01BWAO_AS.Name;

FILBWAI_FL.Name = OWFFG01BWAI_FL.Name;

FILBWAO_FL.Name = OWFFG01BWAO_FL.Name;

FILBWAI_FH.Name = OWFFG01BWAI_FH.Name;

FILBWAO_FH.Name = OWFFG01BWAO_FH.Name;

FILBWAI_HF.Name = OWFFG01BWAI_HF.Name;

FILBWAO_HF.Name = OWFFG01BWAO_HF.Name;

FILBWAI_HG.Name = OWFFG01BWAI_HG.Name;

FILBWAO_HG.Name = OWFFG01BWAO_HG.Name;

FILBWAI_SB.Name = OWFFG01BWAI_SB.Name;

FILBWAO_SB.Name = OWFFG01BWAO_SB.Name;

FILBWAI_SY.Name = OWFFG01BWAI_SY.Name;

FILBWAO_SY.Name = OWFFG01BWAO_SY.Name;

FILBWAO_TS.Name = OWFFG01BWAO_TS.Name;

FILBWAI_TS.Name = OWFFG01BWAI_TS.Name;

FILBWPB_SU.Name = OWFFG01BWPB_SU.Name;

FILBWDA_EE.Name = OWFFG01BWDA_EE.Name;

ENDIF;

Show "Oakville Filter Setpoints";

ENDIF;

IF WINDOW == 107 THEN

Show "Oakville Filter OV Setpoints";

ENDIF;

#### Programmers adding new windows with setpoints to the SCADA system are required to modify this button.  The Programmer should insert their setpoints window in the appropriate numerical order.  In the above example if the next window was “108” it would go after the “IF WINDOW ==107” condition.  If the Window was 103, it would go between 102 and 106.

#### The “Setpoints” button has a level of security attached to it.  An example of the Animation Links => Miscellaneous => Disabled script for the “Setpoints” button is displayed in the figure below.

- Button Bar “Setpoints” Button Security Limitation

#### For a complete list of access level tags and their numerical access value, see the security levels chart in Section 6.4.

### ‘Previous’ and ‘Next’ Arrows

#### The ‘Previous’ Arrow button is 41 pixels wide by 30 pixels high.  The ‘Next’ Arrow button is 43 pixels wide by 30 pixels high.

#### The ‘Previous’ and ‘Next’ arrows are navigation buttons.  The selection of ‘Previous’ will display the process control window associated with the process area which immediately precedes the process area currently on display.  The selection of ‘Next’ will display the process control window associated with the process area which immediately follows the process area currently on display.

#### A partial example of the Animation Links => Touch Pushbuttons => Action => On Key Up script for the ‘Previous’ button is as follows:

IF WINDOW == 112 THEN

Show "Oakville Ammonia System";

ENDIF;

IF WINDOW == 101 THEN

Show "Oakville Sulphur Dioxide System";

ENDIF;

IF WINDOW == 117 THEN

Show "Oakville Fluoride System";

ENDIF;

IF WINDOW == 108 THEN

Show "Oakville Polymer System";

ENDIF;

IF WINDOW == 111 THEN

Show "Oakville Alum System";

ENDIF;

IF WINDOW == 100 THEN

Show "Oakville Chlorine System";

ENDIF;

IF WINDOW == 102 THEN

Show "Oakville High Lift";

ENDIF;

IF WINDOW == 109 THEN

Show "Oakville Filtration Overview";

ENDIF;

IF WINDOW == 107 THEN

Show "Oakville Low Lift/Flocculation";

ENDIF;

#### Programmers adding new windows are required to modify these two buttons to include their windows.  The Order the windows are scrolled though are by process.  Programmers should insert their new window at the appropriate process location.  In the above example if the new window was required between the Alum and the Chlorine system, that is where Programmers should insert their window.  This applies even if the Window numbers are out of numerical sequence as shown in the above example.

#### To insert a window for the “Previous” button, use the following procedure

#### Determine the window number of the window that will precede the new window.

#### Locate this number in the action script.  Insert a new IF statement immediately above the preceding window IF statement for the new window.  Modify the Show action to open the window currently being opened by preceding window.

#### Modify the IF statement for the preceding window to open the new window.

#### To insert a window for the “Next” button, use the following procedure

##### Determine the window number of the window that will precede the new window.

##### Locate this number in the action script.  Insert a new IF statement immediately below the preceding window IF statement for the new window.  Modify the Show action to open the window currently being opened by the preceding window.

##### Modify the IF statement for the preceding window to open the new window.

#### The value used by each window should match the indexing number that InTouch applied to the window. The ww_wdws.NDX file located in the application folder contains this information. Use this number to identify the window in the “On show” script and the number in the “Next” and “Previous” button scripts.

#### The intent of the next and previous arrows is to allow an operator to scroll through the process in  a logical order.

### Disabled Critical Alarms

#### The disabled critical alarms is part of the button bar, located beside the date and time, shown below:

- Button Bar Disabled Critical Alarms

#### The Grey box is 30 Pixels high and 123 pixels wide.

#### Red box behind the Grey box is 35 Pixels high and 130 pixels wide.

#### The “Disabled” and “Critical Alarms” are text stings that are System, Bold, 10 Point Font and Black in colour.  They have no animation links

#### The Red box has the following animation links:

##### Miscellaneous Visibility

##### Miscellaneous Blink

#### The animation links are shown below:

- Disabled Analog Alarms Visibility Link

- Disabled Analog Alarms Blinking Link

#### The alarm groups used are application specific and changed application by application.  The Red box becomes visible if the workstation is a Burlcomp and an alarm in the “Disabled_Alarms” group is in alarm.  The Red Box will blink so long as the “Disabled_Alarms” alarm group is in alarm.

#### The Grey Box in front of the Red box only has one Animation Links => Touch Pushbuttons => Action, the script is shown below:

IF BURLCOMP THEN

ALRM_AGRP = "DISABLED_ALARMS";

ENDIF;

Show "Disabled Critical Alarms";

#### The script shows assigns the “DISABLED_ALARMS” group to the “ALARM_AGRP” memory message tag and shows the Disabled Critical Alarms window when the button is pressed.  The window is shown below:

- Disabled Critical Alarms Window

#### The properties of the window are:

| Window Properties | R/B/G |
| --- | --- |
| Window Colour | White (255/255/255) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | -2 40 1028 720 |
| Window Scripts | On Show |

- Disabled Analog Alarms Window Properties

#### Note:  The window colour is white.  The window contains an InTouch Alarm Viewer Control Wizard, which has a Black background.

#### The On Show windows script is as follows:

ALRM_AGRP = SRV_NAME + "Disabled_Alarms";

almQuery("DISABLEDALM", ALRM_AGRP,1,999,"ALL","SUMM");

#### This script will query all alarms in the “Disbled_Alarms” alarm group, and display them on the alarm viewer.

#### The Window contains one key graphics which are:

##### Alarm Display

### Alarm Display

#### The alarm display is a standard alarm display.  The General configuration is shown below:

- Disabled Analog Alarms Alarm Display General Configuration

#### The General Message configuration is shown below:

- Disabled Analog Alarms Alarm Display Message Configuration

#### The Select Display Font properties are shown below:

- Disabled Analog Alarms Alarm Display Font Settings

#### The column management properties are shown below:

- Disabled Analog Alarms Alarm Display Column Management

#### The Colour configuration is shown below.

- Disabled Analog Alarms Alarm Display Colour Configuration

### Security Alarm

#### The security alarm box is specific to Water Treatment and Water Distribution HMI applications.  Wastewater Treatment and Wastewater Collection HMI applications do not utilize this button.

#### The security alarm box is a symbol that sits above the clock and date box in the button bar, shown below:

- Button Bar Security Alarm

#### The box is 36 Pixels High and 77 Pixels wide with a Black fill and Magenta boarder.  The “Security” and “Alarm!” text is MS Sans Serif, Bold, 8 Point and White text.  The Symbol has the following animation links:

##### Miscellaneous Visibility

##### Miscellaneous Blink

##### Touch Pushbuttons Action

#### The animation links are shown below:

- Visibility Limitations for Security Alarm Button

- Object Blink Properties for Security Alarm Button

- Action Script for Security Alarm Button

#### The script will show the “Security Alarm” symbol when any illegal entry is detected.  In the above examples, there are only two alarms.  The scripts must be modified for each Illegal entry alarm in the system.  The action script will display the Legal Entry Status window.

#### The button and scripts are customized for each specific HMI application.

### Water Treatment and Distribution Legal Entry Status Window

#### Legal Entry status is handled differently at Water, Wastewater, Water Distribution and Wastewater Collection facilities.

#### The following figure is a typical Legal Entry Status window for Water and Water Distribution Facilities.

- Legal Entry level Status Window

#### The properties of the Window are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height |  |
| Window Scripts | None |

- Legal Entry Status Window Properties

#### The X,Y location and window height and width are application specific.

#### The number of locations presented in the window are application specific.

#### Each Window has four key items.  These are:

##### Door Location

##### Legal Entry

##### Entry Alarm

##### Access Alarm (Application Specific)

#### The Door location identifies the location of the door.  Water Distribution facilities that have multiple doors , but only have one input to the PLC from the security panel for Legal Entry and Entry alarm.

- Door Location Identifier Building Door

#### The string is System, Bold, 10 Point Font, White text.  It has no animation links.

### Legal Entry and Entry Alarms

#### The Legal Entry and Entry Alarms are digital inputs from the GE security panel that monitors the door(s).  The evaluation of Legal Entry Status and Entry alarm is generated within the security panel.  Below is the graphic display.

- Legal Entry Status

#### The text strings are, System, Bold and 10 point font.  The “Yes” is Red and the “No” is Lime in colour.

#### `

#### Each has one Animation Links => Miscellaneous => Visibility, shown below:

- Legal Entry Visibility Animation Link

#### The Red “Open” text is displayed when the tag is true.  The “Closed” text uses a similar Animation Links => Miscellaneous => Visibility.

### Entry Alarm

#### The Entry alarm text Displays a Lime “OK” and an “ALARM” in magenta.  Each work has an Animation Links => Miscellaneous => Visibility limitation:

- Entry Alarm Visibility Animation Link

#### The "OK" text uses a similar Animation Links => Miscellaneous => Visibility.

#### Programmers adding new door security inputs are required to update appropriate window, based upon their system configuration.

### Access Alarm

#### Access alarms are only applicable to Water Distribution applications.  This alarm is generated by the local PLC, not the GE security panel.  The Access Alarm is generated by a timer that monitor's the Legal Entry status.  Programmers should contact Halton Region for more information.

- Access Alarm

#### The access alarm text is similar to the Open and Close shown above.  The only difference being it displays a Line "OK" and an "ALARM" in magenta.

### Wastewater Treatment Legal Entry Status

#### Wastewater Treatment Facilities do not utilize a standard SCADA security window.

### Wastewater Collection Legal Entry Status

#### Wastewater Pumping Stations have specific security requirements.  Refer to section 8 – Wastewater Pumping stations for more details.

### Time and Date Displays

#### On the far right side of the button bar there are two (2) small black windows that display the current time and date.  The first box is the Time box which is 87 pixels wide by 16 pixels high.  The second box is the Date box which is 88 pixels wide by 19 pixels high.  The boxes have black fill with a thin grey border.

#### Placed in the center of each black box is a white text block.  The expression Animation Link => Value Display => String for the Time display is the tagname $TimeString. The expression Animation Link => Value Display => String for the Date display is $DateString.

#### $TimeString and $DateString obtain their values directly from the local workstation’s system time and date settings.

## Alarm Banner

#### The Alarm Banner is a small window called “Alarms” located at the bottom of the screen and is the full width of the screen.  It has no title bar and is always opens the alarm banner constantly displays the alarms and events that are occurring in the SCADA system.  The alarm banner is shown in the figure below:

- Alarm Banner

#### The properties of this window are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | White (255/255/255) |
| Window Type | Overlay |
| Frame Style | Single |
| Title Bar | No |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | -1 660 1028 102 |
| Window Scripts | None |

- Alarm Banner Window Properties

#### The alarm display is created by using a Wonderware wizard called ‘Dist. Alarm Display.’  The display has been stretched to cover the complete width and height of the window.  The proper settings for the alarm banner are displayed in the figure above.  The Alarm Query Group should be the highest alarm group in the alarm hierarchy below the $System alarm hot backup group.

- Alarm Banner General Alarm Configuration

#### The alarm Query should query all alarms for the application.

### Alarm Banner Configuration continued.

- Alarm Banner Configuration Continued

#### Above is shown the general configuration.  In addition the Display Font and Colum management parameters need to be set.

- Display Font

- Alarm Configuration

#### The RBG colour standards for the alarm settings are as follows:

| Alarm Colour Settings | RBG |
| --- | --- |
| UnAck ALM Colour | Magenta (255/0/255) |
| Ack ALM Colour | White (255/255/255) |
| RTN Colour | Cyan (0/255/255) |
| EVT Colour | Yellow (255/255/0) |

- Alarm Colour Settings

#### Alarm Banner Colour Settings

- Alarm Colour Settings

## Screen Hierarchy

#### The screen hierarchy is configured as outlined in the following flow chart:

- Screen Hierarchy

### Navigation

#### Navigation within Halton Region’s HMI applications has been standardized as detailed in this section.  The primary method of navigating through the process control windows is achieved through the configuration of the ‘Previous’ and ‘Next’ Arrows on the button bar.  Each successive click of the ‘Next’ Arrow will open the next process control window in order of the actual process.  Once the last process control window has been reached, the next mouse click will open the first process control screen.  Each successive click of the ‘Previous’ Arrow opens the process control windows in reverse order to the actual process.  Once the first process control window has been reached, the next mouse click will open the last process control screen.

#### If the SCADA application is for a water purification plant and associated distribution system, a suggested order in which the main control screens open, based on the Next/Previous Arrows, is as follows:

##### Plant Process Overview;

##### Low Lift;

##### Flocculation;

##### Filtration Overview;

##### High Lift;

##### Distribution System;

##### Waste System;

##### Chlorine System;

##### Other Chemical Systems;

##### Other Miscellaneous Systems; and,

##### Plant Process Overview.

#### If the SCADA application is for a wastewater plant and associated collection system, a suggested order in which the main control screens should open is as follows:

##### Plant Process Overview;

##### Inlet Works;

##### Primary Clarifier;

##### Aeration;

##### Final Clarifier;

##### Tertiary Treatment;

##### Chemical Systems;

##### Digesters & Sludge Recirculation;

##### Sludge Storage and Transfer;

##### Effluent Water System;

##### Other Miscellaneous Systems; and,

#### When a process control screen requires additional screens to provide sufficient detail and control, sub-process screens may be opened from the main process control screen.  An example of this is a water purification plant filtration process.  The ‘Filtration Overview’ process control window in a water purification system displays information on all of the filters as an overview to the filtration process.  Each of the individual filters is controlled in a sub-process control window by selecting the filter from the ‘Filtration Overview’ window.  An example of this is the ‘Burlington Filtration Overview’ window displayed below.

- Filtration Overview Window

#### The process control screen is programmed to allow these sub-process windows to open.  In this example there is a square box around each filter that will open the specific filter control window when selected. The Animation Links => Touch Pushbuttons => Action => On Key Up scripting for this box is as follows.

FILT_NUM = 13;

Show "Burlington Filter Control";

#### In the above screen picture note the box that appears around Filter 13 when the mouse is placed over the box.  Selecting this box opens the sub-process window displayed below.

- Sub-Process Window

#### Once in a sub-process control window, a button is required to close the sub-process control window and reopen the main process control window.  In the example displayed above there is a button in the top right corner labeled ‘Filtration Overview’ that performs this function.  The Animation Links => Touch Pushbuttons => Action => On Key Up scripting for this button is as follows.

Show "Burlington Filtration Overview";

## Process Control Screens

#### Process control screens are the windows that cover the majority of the screen and fit below the Button Bar at the top of the screen and above the Alarm Banner at the bottom of the screen.  These windows display all of the major processes and / or devices required to control the process.  To move from one process control screen to the next and back, the ‘Next’ and ‘Previous’ arrows on the Button Bar are used.

#### The windows closely resemble the actual physical layout of the system.  An example of a process control screen is the “Low Lift” window from the Burloak Water Treatment plant, displayed below.

### Process Control Screen

- Process Control Screen

#### The window properties for a typical process control screen are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | White (255/255/255) |
| Window Type | Replace |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | Yes |
| Dimensions: X Location Y Location Width Height | 0 40 1028 630 |
| Window Scripts | On Show |

- Window Properties

#### Window Script On Show:

WINDOW = 101;

#### Each window has a unique number that is assigned during development. The value used by each window should match the indexing number that InTouch applied to the window. The ww_wdws.NDX file located in the application folder contains this information. The window number is assigned in the “On Show” window script.   ‘WINDOW’ is a memory integer tag.  Each time another process control screen is opened, the tag ‘WINDOW’ is given a new value, allowing the ‘Next’ and ‘Previous’ Arrows on the Button Bar to keep track of which windows to open next.

## Hot Link Windows for Remote Stations

#### Water distribution and wastewater collection have dedicated HMI applications for each system.

#### Process control screens for remote stations in a SCADA system may or may not be accessible through the ‘Previous’ and ‘Next’ Arrows.  In some SCADA systems there are too many remote sites with process control screens to make them easily accessible from the button bar.  In this case these screens are only available through a Process Overview screen.

#### Process overview screens may already be made accessible through the ‘Process’ button or the ‘System’ button on the button bar.  However, all process overview screens must be accessible through the use of the ‘Previous’ and ‘Next’ Arrows.

#### On the process overview screen, all of the remote SCADA sites and the major plant sites are graphically depicted.  Highlighting any one of these sites with the mouse must bring up a highlight box that when selected will open the process overview screen for that process area. An example of the Animation Links => Touch Pushbuttons => Action => On Key Up scripting for this button is as follows.

Show "Bailie Pumping Station";

#### Another method of navigation that can be used to access a process control screen from another process control screen is the use of buttons or ‘hot links’ as part of the graphics.  By clicking one of these hot links the process control screen for the station will open.  The Animation Links => Touch Pushbutton => Action => On Key Up script for the ‘Ninth Line’ button is as follows.

Show "Ninth Line SPS";

The main navigation Window is shown below:

- Example Process Control Screen with Hot Links

#### An example of a remote station Process Control screen is shown below:

- Remote Station Process Control Screen

## Process Current Setpoints

#### The process current setpoints pop-up provides information and control for the process duty equipment.  Process setpoint windows are specific to each process application.

#### The name of the window should clearly identify which process setpoints are contained in the window.  As an example, the Raw Sewage Pump Setpoints window would be called “RSP Current Setpoints.”

#### An example of the process current setpoints window is shown below:

- Sample Setpoints Window

#### The default window properties are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 169 56 620 260 |
| Window Scripts | None |

- Process Current Setpoints Window Properties

#### The final dimensions and X,Y location is depended upon the amount of information displayed.  The window should be mid screen and not cover the button bar or alarm banner.

#### As a minimum process setpoint windows should show:

##### All adjustable setpoints, such as current start/stop values, duty assignments, and flow setpoints

##### Other information relevant to automatic operation

#### All Analog Entry Fields shall be configured as follows:

##### An appropriate “Msg to User” value shall be entered indicating what setpoint is being displayed

##### “Keypad?” Is to be selected as Yes

##### The “Minimum” and “Maximum” values are to use the .MinEU and .MaxEU dotfield properties for the setpoint tag.

##### Formatting is “Text String”

#### Each coloured rectangle shall link to a setpoints entry screen.  A typical entry screen is shown in Figure 6.122.  A secondary data entry screen is required if setpoint entry must be validated against other values in the PLC.  If values may be changed directly, the rectangle colour shall be grey data entry may be performed on this screen.    The requirements for the setpoints entry screen are as follows

##### Two columns are required – a “Current” value and an “Entry” value.  The “Current” value is the live setpoint controlling the system, while the “Entry” value is a pending setpoint held in an entry tag.

##### The columns are to be spanned by a rectangle the same colour as the one clicked on the setpoints entry screen.

##### Minimum and maximum allowable values for a setpoint are to be programmed into the User Input script.  Any additional data validation requirements are to be performed in the PLC.

##### The “Update” button will apply all “Entry” Values to the “Current” fields if all data validation requirements are met.  If they are not met, the “Entry Error” message will display.  This message will only clear when valid “Entry” values are applied to the “Current” values.

##### The “Info” button may be optionally used to display a pop-up that describes validation rules or provides more information on the setpoints.

### Duty Rotation Setpoints

#### Halton Region has standardized duty rotation template for devices and transmitters.

#### The “Pumping Station Setpoints” screen in the InTouch Baseload allows for a maximum four device duty rotation and/or four transmitter duty rotation.  This screen to be unique for each duty rotation system.  The programmer is responsible for making appropriate modifications for three device and two device duty rotations.

#### Duty Device Start/Stop setpoints and Speed Control settings are modified on the “Pumping Station Limits” Screen in the InTouch Baseload.  This screen is unique for each duty rotation system and the programmer is responsible for making appropriate modifications specific to the application.

- Pumping Station Limits Window

### Duty Select

#### 2Device Duty Select, 3Device Duty Select, and 4Device Duty Select  windows are available in the InTouch Baseload.  These screens are common to all duty rotation systems and are not to be modified by the Programmer.  These popups are highly customizable through the blue bar action script on the main setpoints screen.

##### Do not delete any part of this script.  If a value is not to be used set it to null or zero.

##### Set the device names as defined for the application

##### Set the duty descriptions as defined for the application

##### Set Duty Assignment Button Visibility.  If a duty assignment option is not available for a device it should be set to 0.

##### If the Info button is to be used, set the visibility parameter for the Info button and add applicable information to the line entries.

##### Map the Setpoint Entry Tags

##### Map the Current Entry Tags

##### Map the Setpoint Update button and Entry Error Button

##### Call the appropriate device duty screen

#### Duty selection for Two (2) device applications is performed using the following entry window:

- 2 Device Duty Select Window

#### The window properties are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 363 225 320 237 |
| Window Scripts | None |

- 2Device Duty Select Window Properties

#### Duty selection for Three (3) device applications is performed using the following entry window:

- 3 Device Duty Select Window

#### The window properties are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 330 200 385 290 |
| Window Scripts | None |

- 3Device Duty Select Window Properties

#### Duty selection for Four (4) device applications is performed using the following entry window:

- 4 Device Duty Select Window

#### The window properties are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 297 175 451 343 |
| Window Scripts | None |

- 4Device Duty Select Window Properties

### Duty Select Info Popup

#### Specific duty selection criteria or general information is presented to the Operator using the following window:

- Duty Select Info Popup

#### The window properties are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 0 36 320 237 |
| Window Scripts | None |

- 2Device Duty Select Window Properties

### Device Duty Rotation

#### Halton Region has standardized on four duty rotation methods

##### Disabled – No duty rotation occurs

##### All Pumps Stopped – Duty Assignments rotate when all pumps stop

##### Daily Timed Interval – Duty Assignments rotate at the set number of days at the set clock time

##### Hourly Timed Interval – Duty Assignments rotate at the set hourly interval

#### The “Duty Rotation” popup window allows operations to adjust the duty rotation of their equipment.  Halton Region has developed a standard Window to control the three modes of duty rotation.  This window is not to be modified by Programmers.  This window is opened from the yellow bar on the Pumping Station Setpoints Window.  Programmers are to modify the Action Script appropriate to their system.

#### Duty rotation mode selection is performed using the following entry window:

- Duty Rotation Window

#### The window properties are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 300 217 410 281 |
| Window Scripts | None |

- Pump Duty Rotation Window Properties

### Display of Pump Duties

#### The duty position of each device needs to be shown on the process control window.  Duties can be shown above or beside the equipment depending upon the available space.

#### Below is an example showing an aeration blower’s duty assignment.

- Aeration Blower’s Duty Assignment

#### The duty text is layered on top of each other and is visible based upon the duty assignment.

#### The text split apart appears as follows:

- Duty Text Split Apart

#### The font is System, Bold 10 Point.  The text colour is Black.

#### Each Duty position text has the following animation links:

##### Miscellaneous Visibility.

#### Under the Animation Links => Miscellaneous => Visibility, the following condition is used:

- Duty Text Miscellaneous Visibility

#### The “Duty 1” text is visible if the duty blower is 1.  The Duties 2 and 3 have similar scripts except the Duty tag changes.  For Blower #2, the “==1” becomes “==2.”

## Duty Level Transmitter Control/Selection

#### In applications where process equipment can operate to supply or draw from more than one duty location, the SCADA system is required to indicate which duty tank is in service.  Examples include Chemical Storage Tanks, Digesters and Sewage Wet Wells.  Halton Region has standards on Level Transmitter Duty rotation.  There are pre-configured screens for 2 Duty, 3 Duty, and 4 Duty transmitter rotation.  The application specific source code can be found in Section 5.

#### The main process setpoints window shows the current duty transmitter.

- Main Process Setpoints Window

#### The green bar is used to indicate that clicking on it will active an automatic setpoints sub pop-up.  This action script should be modified with the appropriate device names, tags, and showing the appropriate duty assignment screen.

### Duty Transmitter Selection Window

#### There are three duty transmitter windows in the application; “Transmitter 2 Duty”, “Transmitter 3 Duty” and “Transmitter 4 Duty”.  These windows are not to be modified by programmers.

- Duty Transmitter Selection Window

#### The Windows all have the following properties.

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 223 84 363 201 |
| Window Scripts | None |

- Duty Transmitter Selection Window Properties

## Display of Device Automatic Setpoint

#### In situations where the PLC calculates an Automatic setpoint based upon operator entered parameters, these setpoints can be displayed on SCADA, at the request of operations.  Typically this is used for PID applications where a PID loop setpoint is calculated and then compared to a process variable feedback.

#### The following is an example from a Ferric pump.

- Ferric Pump System

#### The Ferric Pump Automatic Setpoint is shown in Red Text, below the Ferric flow meter.  The Ferric Flow is a standard analog device control, and the Red SP is an animation link => Value Display => Analog that shows the current flow setpoint.  This allows operations at a glance to know if their equipment is operating correctly.

## Use of Indirect Tags in Pop-Ups

#### Halton Region has standardized on the use of indirect tagging as a means to conserve the resources necessary to develop and run HMI applications.  The use of indirect tagging also facilitates troubleshooting.  Indirect tagging is used wherever possible, and in particular for the device control pop-up windows and similar sub-process screens.

#### Indirect tagging is to be used when there is a requirement for multiple windows that have a similar appearance and function.  As an example, each pump requires a control window and each pump has similar controls and feedback.  The use of indirect tags with the control pop-up will thus minimize the number of windows required within an application.  The control window will have a similar appearance for each pump, and differ only based upon the unique properties associated with the device.

#### Indirect tagging requires the creation of an indirect tag for each variable in a shared window.  When a shared window is opened, the indirect tags are set equal to the device specific tags for the device being selected.

## Device Control Pop-Ups

#### Device control pop-ups are small pop-up windows used to operate controllable devices such as pumps, valves, mixers, digesters, bar screens, chlorinators, and many other controllable devices within the SCADA system.  Each HMI application will have several main device control pop-ups such as a pump control pop-up, a fixed valve control pop-up, a modulating valve control pop-up and a chemical pump control pop-up.  Programmers should only use pop-ups approved for the current release of the standards.  Consult the UDDT Programming guides for more details on approved pop-ups for this release of the standards.

#### All pop-ups created for Standards Version 4 have versioning control implemented into their name.  Minor revisions shall incorporate bug fixes or features that do not require major modifications to the window layouts.  Major revisions are reserved for future Standards releases or significant changes that break backwards compatibility.

#### Applications should only contain the latest version of a major revision pop-up.

#### The use of indirect tags in a device control pop-up window is required by Halton Region’s standards.

#### Halton Region is responsible for the creation and management of all pop-ups.  Any changes requested by Programmers are to be submitted in writing for review.

## Plant Communication Map

#### Halton Region has established a Standard Map Layout to Display Plant Communications.  This window displays the network connections on the communication LAN.  The Window is titled, “Plant Comm Map” and is shown below:

- Plant Comm Map

#### The Window properties are:

| Window Properties |  |
| --- | --- |
| Window Colour | White (255/255/255) |
| Window Type | Replace |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 0 40 1028 630 |
| Window Scripts | Yes |

- Plant Comm Map Window Properties

#### Halton Region has standardized on the following colours for communication lines:

##### Orange Lines indicate Fiber Optic Communications

##### Blue lines indicate Ethernet.

##### Purple lines indicate Serial or DSL Communications.

#### The intent of the Window is to provide a high level display the communication network that can be used for troubleshooting by SCADA staff.

#### In situations where there is too much information to display on one window, the use of multiple windows is acceptable.  The SCADA servers located in the Network Closet must be shown on all Comm Windows.

#### Each PLC has a Magenta Alarm box, shown behind the PLC.

- Magenta Alarm Box

#### The Magenta Alarm Box indicates when the PLC has a fault alarm in the BXXRT01_PLC alarm group.

#### The box is 41 Pixels High and 67 Pixels Wide with a Magenta Fill and Black boarder line.  The box has two Animation Links which are:

##### Miscellaneous Visibility

##### Miscellaneous Blink

#### The Animation Links are shown below:

- Magenta Box Animation Links

- Magenta Alarm Box Animation Links

- Magenta Alarm Box Animation Links

#### Beside each PLC there is also a " and "X", shown below:

- Communication " and "X"

#### These are used to indicate if DAS server communications to the PLC are active.

#### All PLCs are to have a pair of tags (BXXPLC001DA_CN and BXXPLC1001DI_CN) that implement network communications alarming.

#### The "" shall be visible when BXXPLC001DA_CN is true:

- Visibility Animation Link

#### The "X" shall be visible when "NOT BXXPLC001DA_CN" is true.

#### SCADA View nodes, Thin Clients, and Terminal Servers are shown on the window, but there are no animation links associated with the computers.

#### SCADA Servers use a similar Magenta box and "", "X", shown below:

- SCADA Server Graphic

#### The Magenta alarm box indicates if there is a heartbeat alarm between the Server and the facility dialer/admin PLC, or if there is a problem with the connection to the dialer/admin PLC access name in the OI server.

#### All Servers are to have one tag (BXXCPU0XDA_HB) that alarms on failure of the heartbeat between the polling node and the dialer/admin PLC.

#### The Box is 38 Pixels High and 66 Pixels wide.  It has the same animation links as the PLC magenta box, using the DA Server status tag and the PLC heartbeat tag.

- Visibility Animation Link

#### The "" and "X" are used to indicate a Heartbeat alarm from the SCADA server to the Autodialer PLC.  Refer to Section 5 for details on how to Program the Heartbeat alarm.

#### Halton Region has created a standard Symbol library specific to Network communications.  The window is titled "Symbols Library – Networking".  These symbols are used for all of Halton Region's SCADA applications.

## Server, Workstation and Thin Client Window

#### Halton Region has established a standard window for server, workstation and thin client summarization and status.  Programmers adding a new SCADA node or thin client to an existing HMI application must update this window.

#### An example of the Server, Workstation and Thin Client Window is shown below:

- Server, Workstation and Thin Clients Window

#### There are six items which must be displayed for each SCADA server or workstation, these are:

##### System Name

##### Current Time (CPU01 and Workstations Only)

##### Application Number (CPU01 and Workstations Only)

##### View Active Status

##### I.P. Address

##### Location

#### There are three items which must be displayed for each thin client, these are:

##### Client name

##### Location

##### I.P. Address

### Server and Workstation Properties

#### The server time indicates the local time.  For the IO server pair, the time is provided by CPU01 or CPU02, depending on which server is currently the primary.  The time is not shown for the terminal server.

#### The Application Number is a text sting which looks at the, “$ApplicationVersion” on the local workstation.  For the IO server pair, the application version is provided by CPU01 or CPU02, depending on which server is currently the primary.  The application version is not shown for the terminal server.

#### The “View Active” for Polling nodes monitors the status of the Heartbeat alarm from the Plant’s Autodialer PLC.  Refer to Section 5 for details on how to Program the Heartbeat alarm.  The Text string is shown below:

#### Each server and workstation uses their associated heartbeat alarm tag.  When the tag is, off it will display “OK” in Green text.  When the tag is on, it will display “DOWN” in Magenta text.   The “DOWN” will blink invisible.

#### The workstations monitor the same heartbeat alarm, but instead show "Online" and "Offline".  When View is not running on a SCADA workstation, it is not considered an alarm.  As such, the text does not have the text colour change or alarm blink animation links.

#### I.P. Address is static text used to assist in the troubleshooting of SCADA problems.

#### Location is the location is static text used to assist in the troubleshooting of SCADA problems.

## Logix and SLC Status Window

#### Halton Region has standardized on two displays for Allen Bradley SLC and Allen Bradley Logix based processors.

### SLC Processor Status Summary

#### Below is the SLC Processor Status Summary:

- SLC Processor Status Summary Page

#### The Window properties are:

| Window Properties |  |
| --- | --- |
| Window Colour | White (255/255/255) |
| Window Type | Pop-up |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 0 40 1028 620 |
| Window Scripts | Yes |

- Plant Communication Window Properties

#### All SLCs associated with the Application are presented on this window.

#### If a PLC is added to this screen, an existing column should be copied and positioned appropriately.  Perform the necessary tag and string substitutions to update for the new system.  If the new PLC communicates with other PLCs via Peer-to-Peer messaging, then manual configuration of the COMM status row is required as described below.

#### For larger install counts where there are more PLCs then will fit on one window, a capital letter "I" should be appended to the window name, and a second identical window should be created continuing the PLCs.  Appropriate navigation is to be added to all additional windows to allow users to cycle back and forth between the screens.

### Workstation Comm. Status

#### This button opens the “Server, Workstation, Thin Client” window.

### Plant Logix PLC Status

- Plant Logix PLC Status Button

#### This button will open the plant Logix Processor Status Page.  If there is more than one Logix status page the button should be modified to navigate to the first page in the series.

### Time/Date Sync Button

#### The Time/Date Sync Button calls the PLCTimeDateSync() Quickfunction when pressed.  Security access is restricted to operators and above.

### PLC to PLC Comm Status

#### This feature is only required if the listed PLC reads data from other PLCs.  The communication button brings up a second window which monitors PLC to PLC communication alarms. As an example, the SWSRT01 PLC reads SWERT01 for a message.  When the heartbeat alarm for SWERT01 times out in SWSRT01  the alarm will become true.

- PLC to PLC Comm Status

#### The” Normal” text label has visibility animation.  The expression is a NOT AND of all heartbeat alarms in the PLC.

#### The “Alarm” text label has visibility animation.  The expression is an AND of all heartbeat alarms in the PLC.

#### The magenta box has visibility and blink animation.  The expression for both is the same AND statement used for the “Alarm” label.

#### Finally, there is an Animation Link => Action Script to open up the communication summary window “BXXRT01 Comm Status”.  This window must be duplicated for each PLC with peer-to-peer messaging.  Each row entry represents communication to a single target PLC.  The animations on the comm status labels shall be updated to point to the appropriate heartbeat alarm.

- PLC Comm Status Window

#### The Window properties are:

| Window Properties |  |
| --- | --- |
| Window Colour | White (255/255/255) |
| Window Type | Pop-up |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 197 149 540 364 |
| Window Scripts | No |

- Comm Status Window Properties

#### These windows are application specific.  The size and X/Y Location and size may require adjustment depending upon the number of communication alarms presented in the window.

### Logix Processor Status Summary

#### Below is the Logix Processor Status Summary:

- Logix Processor Status Summary Page

#### The window has the same general functions and layout as the SLC Processor Status Summary page.

## Rain Gauge Window

#### Consult the Weather Station UDDT Programming Guide for more information in implementing the rain gauge window in an application.

## Autodialer Verification

#### Halton Region has a standardized pop-up for the Autodialer Verification System.  Information on how the Verification System is programmed is located in Section 7, Supplemental SCADA Programming.

#### The Auto Dialer Info Window is as follows:

- Auto Dialer Info Window

#### The Window has the following properties:

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 112 96 505 321 |
| Window Scripts | On Show |

- Auto Dialer Info Window Properties

#### The On Show Window Script is used to query the autodialer alarm group.  The example below shows the script for Oakville Southwest WWTP:

almQuery( "ALD_VS", "southwest\SWYALD0VS", 844, 845, "All", "Hist" );

#### The window has the following three (3) key features:

##### Verification System Information and Control

##### Verification Alarms

##### Verification Alarm Summary

### Verification System Information and Control

#### The Verification System Information consists of three Buttons and a visible text string, shown below:

- Verification System Information Buttons

#### The Verification System enable button consists of a white box and two text strings, as shown below:

- Verification System Enable Buttons

#### The White Text box has the following Animation Links => Touch Pushbuttons => Discrete Value:

- White Text Box Animation Links

#### Each time the white boxed is “Clicked,” the Verification System Enable bit is toggled on or off, depending upon its current state.

#### The Red and Green text have similar visibility limitations.  The Animation Links => Miscellaneous => Visibility for the Red “On” text is as follows:

- Visibility for the Red “On” Text

#### The Red “On” text is visible when the enable tag is on.  The Green off text uses the same tag with a visibility of “Off.”

#### The System Test Running string is Times New Roman, Bold, Ten Point Font, and White in Colour.

#### It has the following Animation Links.

##### Miscellaneous Visibility.

#### The Animation Links => Miscellaneous => Visibility is shown below:

- Visibility Animation Links

#### The text sting is only visible when the test mode is active.

#### The Last Test Status box consists of a white box that is 20 Pixels High and 61 Pixels wide.  It has no animation links.  Inside the box is two text strings, shown below with the box.

- Text Status Box

#### The Red “Passed” and Magenta “Failed” text are System, Bold and 10 Point Font in size.  The “Red” passed has one Animation Links => Miscellaneous => Visibility, and the Magenta, “Failed” has two which are Visibility and Blink.  Both use the same tag.  The Animation Links => Miscellaneous => Visibility, followed by the => Blink for the Magenta “Failed” is shown below:

- Visibility Text

- Blink Text

#### Based upon the Visibility and Blink we can see that “Failed” is visible and blinks, when the tag is not true, or off.  The Red “Passed” text is visible when the tag is true.

#### The Verification System Alarm Reset Box is a text button that is 23 Pixels High and 60 Pixels wide.  The “Reset” text is System, Bold, 10 Point, and Black in Colour.

#### The button has one Animation Links => Touch PushButtons => Discrete Value, which is shown below.

- Discrete Value

#### The tag is set true, when the box is pressed.

### Verification Alarms

#### The verification alarms consist of a Cell, and Two Magenta Text Strings shown below:

- Verification Alarms

#### The Cell consists of the white “System Dialer Alarm Active –“ and “No Test Occurring” text strings which are:  Times New Roman, Bold, 10 Point Font, and White in Colour.

#### Both have the same animation link which is, Animation Links => Miscellaneous => Visibility; shown below:

- Verification Alarms Animation Link

#### Both text strings are visible when the tag is true.

#### The Magenta text is three separate strings, of “Dialer Failure,” “System Failed!” and “Phone Line Failed.”  The Dialer Failure is Times New Roman, Bold, 14 Point Font, and Fuchsia in Colour.  The other two strings have identical properties, except they are 16 Point Font.

#### Each string has two Animation links which are:

##### Visibility

##### Blink

#### The Animation Links for the Dialer Failure text is shown below:

- Dialer Failure Text Animation Link

- Dialer Failure Text Animation Link

#### The text sting is visible and blinks when the alarm is active.  The other two strings have identical animation links using different tags.

### Verification Alarm Summary

#### The verification Alarm summary is an InTouch Alarm summary at the bottom of the window.  It is 116 Pixels High and 497 Pixels Wide.  The summary is shown below:

- Verification Alarm Summary

#### The General Alarm configuration is shown below:

- General Alarm Configuration

#### The general message configuration is shown below:

- General Message Configuration

#### The Select Display Font setup is shown below:

- Select Display Font Setup

#### The Column Management Properties are shown below:

- Column Management Properties

#### The Alarm Configuration Color Properties are shown below:

- Alarm Configuration Color

## Remote Station Pribusin Signals Graphics

#### Halton Region has established a standard for Remote Sewage Pumping stations that do not have a PLC installed, but do have the Wet Well Level and High Level Float alarm tied back to the Plant’s SCADA system.

#### This system is referred to as the Pribusin Alarming System, and is used to monitor all remote Sewage Pumping Stations.

#### A typical station is shown below:

- Typical Pribusin Alarming System Station

#### Programmers shall not modify this graphic except as directed below.  To deploy this graphic, make the following changes:

##### Perform a string substitution to update the Station Name and Station ID

##### Perform a Tag Substitution to update tags

##### Modify the Action Script for the Four White Boxes to open the first dialer page for the station

## Alarm Enable/Disable Control Pop-up

#### Halton Region has standardized on an interface for enabling and disabling Autodialer alarms.  Details on programming the Autodialer can be found in the Section 7, Supplemental SCADA Programming.

#### Halton Region has standardized on two windows for Autodialer enablement. The first is used to monitor and disable all channels.  The second windows provide individual alarm enable/disable control for the channel.

#### The Autodialer control windows exist in all Halton Region HMI applications.   Should Programmers require more information about the properties of the Window they should contact Halton Region.

#### Autodialer Channels have already been assigned for all remote stations and existing process PLCs.  If Programmers are required to create a new Channel, they should contact Halton Region in writing for direction.

### Dialer Alarms Enable Window

#### Halton Region has standardized on a layout and structure for the alarms and graphic displays.  In situations where Programmers are required to update an existing window, they should contact Halton Region for direction.  Should Programmers be required to create a new window, they are required to use the standard windows shown below.

#### The standard page layout is shown below:

- Dialer Alarms Enable Window

#### The properties of the Windows are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Black (0/0/0) |
| Window Type | Popup |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | -1 40 1028 620 |
| Window Scripts | None |

- Dialer Alarms Enable Window Properties

#### The standard layout accommodates forty-eight (48) dialer alarms per page, spread across two (2) columns.  The remaining space is reserved for channel status and control.

#### Alarms are to be organized and grouped in a logical manner.  The exact layout shall be agreed upon by the plant.  Typical guidelines are as follows

##### The alarms that are considered to be most important to the operation of the system should appear first. Typically, but not always, these are compliance critical and critical alarms.

##### Alarms associated with the same device or instrument should be grouped together

##### Avoid spanning alarms associated with the same device or instrument across multiple columns or multiple pages

#### Each window shall have a “Next,” and/or “Previous” button to facilitate navigation of alarm pages for the same channel.  Programmers are responsible for programming these buttons to ensure correct navigation flow of the dialer alarm pages An “X” button shall be provided to close the current pop-up:

- Dialer Alarms Enable Window

### Dialer Alarm Object

#### Two Dialer Alarm Objects are provided on the “Symbols Library – Misc I” screen in the InTouch baseload.  Note that they have been placed on a black background so that all components are readily visible.  The “Standard Alarm Object” is for typical single point alarming.  The “Virtual Alarm” object is intended for use with pumps and valves as collection of the fail to actuate/uncommanded actuation alarms. More generally this object can be used to control dialouts of a group of up to four alarms with a common alarm and dialer control.

- Alarm Enables

#### The Dialer alarm object consists of four key items, which are;

##### Alarm description text string.

##### The Raw Alarm Control

##### The Dialer Alarm Control

##### The Alarm Status

#### The Raw Alarm Control is restricted to Subforeman Access and higher.

#### The Dialer Alarm Control is restricted to Operator Access and Higher.

#### Pressing the Dialer Alarm Control brings up a secondary pop-up called “Dialer Alarm Enable”.  On this screen the alarm are two controls to disable the dialer alarm.  One control requires Operator Access or Higher and the second control requires Supervisor Access or Higher.  Users may also enter a reason as to why the alarm has been disabled.  Programmers shall not modify this screen.

#### If the Supervisor Dialer Disable control is set, in addition to the Dialer Alarm Control showing “Off”, the background rectangle will also be coloured yellow.

#### Programmers shall perform a Substitute Tags operation to update the tags specific to the object.  Programmers shall then perform a Strings Operation to update the alarm text.

- Dialer Alarm Enable Pop-up

## Power Monitor Information Pop-up

Halton Region has developed a standard window for displaying information from a Rockwell Automation 5000 series power monitor.  Consult the Power Monitor UDDT Programming Guide for more details

## Polling Setup

### Access Names

#### There is to be one (1) access name for each field controller in the SCADA system. The access name is used to access all information.

#### If data from a PLC is required in multiple InTouch Applications, it shall be accessed via remote references to the InTouch Application where the access name is configured.

#### Access names at facilities with process areas use a naming convention with four characters.  The first three (3) characters use fragment 1 and 2 of Halton Region’s Tagname Convention.  The fourth character is the number of the field controller at each particular site.

#### An example would be BWA1.  This is the first PLC in the Low Lift area at the Burlington Water Plant.

#### Access names for existing Water Distribution facilities use a naming convention with four characters.  These topics have been created by Halton Region and Programmers should not need to modify them.  Programmers should contact Halton Region in writing if more information is required.

#### Halton Region will provide Programmers with the four-character topic definitions for new Water Distribution facilities.

#### Topic definitions of wastewater collection facilities use a naming convention with three characters.  The three (3) characters use the fragment 1 and 2 of Halton Region’s Tagname Convention.  An example of the topic is A01.

### Polling Setup

#### A polling node is a workstation that runs an I/O driver to communicate to one or more field controllers.  All other workstations in a SCADA system communicate with the polling node to gain access to the same information.  Field controllers are only polled by one IO server at any given time, in one application.

#### For each HMI system there is one primary polling node and a backup polling node.  The primary and secondary polling nodes are dedicated rack mount servers.

#### If the main polling node fails, the backup polling node will automatically begin polling.  Once the main polling node has recovered it will automatically start polling again and the backup polling node will stop polling.  This changeover occurs automatically without operator intervention.

### Switching to the Backup Polling Node

#### This is performed when setting up the Access names.

#### Under Special => Access Names a backup polling node is assigned, as shown below.

- Polling Node Access Name

#### Switching between primary and backup is determined by Wonderware, using the built in feature.

- Failover Configuration

#### The failback dead band is set for 5 seconds, meaning that the primary node must be active for five (5) seconds before SCADA will switch back.

## Alarms and Events Strategy

#### Halton Region has standardized on an alarms and events strategy used in all Regional SCADA systems.

### Alarm Grouping

#### The alarm grouping hierarchy has six levels.  These levels, from the highest level down, are as identified in the following table.

### Alarm Group Hierarchy

| Hierarchy Level | Level Description | Example of Alarm Group |
| --- | --- | --- |
| Level 1 | $System | All Alarms |
| Level 2 | Process | Water or Wastewater |
| Level 3 | Regional Division | South Halton and North District |
| Level 4 | Municipal Division | East, West, Georgetown, Acton, Milton, etc. |
| Level 5 | Field Controller | PLCs and RPUs |
| Level 6 | Field Device | Valves, Pumps, Analogs, etc. |
| Level 7 | Field Device Secondary Instrument | Speed Feedback |

- Alarm Group Hierarchy

#### Each alarm group is a member (child) of the alarm group directly above it (parent).  If an alarm group in Levels 1 through 5 is selected, all alarms directly below that group will also be selected.  For example, if the alarm group “Acton” on Level 4 is selected, then all of the field controller alarm groups below it in Level 5 and all of the field device alarm groups in Level 6 will be selected at the same time.

#### Every alarm and event tag that references a specific device must be assigned to a logical alarm group in Level 6.  If the tag is a stray tag such as a communication alarm for a PLC or a temperature alarm for a remote pumping station with one PLC in it; the tag should be assigned to an alarm group in Level 5 to reflect that it belongs to a particular PLC.

#### The grouping hierarchy takes into consideration all of the water and wastewater elements currently identified in Halton Region’s water and wastewater systems.

### Alarm Group Naming Convention (Levels 5, and 6)

#### Alarm group naming for alarm levels 1, 2, 3, and 4 are decided upon by Halton Region.  For a description of these alarm groups contact Halton Region’s SCADA group.

#### Level 5 alarm groups are the field controller names.  Adhering to Halton Region’s tagname convention, a level 5 alarm group tag is configured using the first three (3) fragments.  As an example, the alarm group for a field controller in the Chemical Department of the Oakville WPP would consist of fragment 1 = ‘OW’ (Oakville WPP), fragment 2 = ‘C’ (Chemical Dept.), and fragment 3 = ‘RT01’ (Remote Terminal Unit 1).  All combined the tag will be:

OWCRT01.

#### Level 6 alarm groups are the device names.  Adhering to Halton Region’s tagname convention, a level 6 alarm group tag is configured using the first four (4) fragments.  As an example, the alarm group for Alum Pump 1 in the Chemical Department of the Oakville WPP would consist of fragment 1 = ‘OW’ (Oakville WPP), fragment 2 = ‘C’ (Chemical Dept.), fragment 3 = ‘AFP1’ (Alum Feed Pump 1), and fragment 4 = ‘VF’ (Variable Frequency Drive).  All combined the tag will be:

OWC_AFP1_VF.

#### Devices may exist at Level 7 or higher if they are primarily associated with a Level 6 device.  For example, the speed feedback analog input for a pump will be a Level 7 child object to a Level 6 pump.

### Alarm Priorities

#### Alarms and Events have individually assigned numerical priority values. The values for each can range from 1 to 999 with 1 being the most critical. When a tag is configured for use as an Alarm it will be logged in the alarm database.

#### When a signal is configured for use as an Event it should not be configured for use as an Alarm thereby making the priority level associated with Alarm logging redundant.  Therefore, each tag that requires logging must be configured as an Alarm or an Event, but not both.

#### A priority level has been assigned to each signal that is identified as an Alarm or Event. Priority levels differ between Water and Wastewater systems.

### Alarm and Event Priorities

| System | Category | Type | Priority Range | Example |
| --- | --- | --- | --- | --- |
| Wastewater | Critical Alarm | Alarm | 1 – 10 | Fire Alarm |
|  | Equipment Critical Alarm | Alarm | 11-99 | Pump Fail to Start Wet Well HIHI Level |
|  | Non Critical Alarm | Alarm | 100-199 | Standby Pump Fail |
|  | Advisory Alarm | Alarm | 200-299 | Wet Well High Level |
|  | Warning Alarm | Alarm | 300-399 | Alum Day Tank Low Level |
|  | Status Event | Event | 700 | Valve Open/Close Status |
|  | Pushbutton Event (Discrete) | Event | 600 | Valve Request to Open/Close |
|  | Setpoint Entry Event (Analog) | Event | 900 | Valve Manual Position Setpoint |
| Water | Critical Alarm - Compliance | Alarm | 1 – 50 | Fire Alarm |
|  | Critical Alarm - Non-Compliance | Alarm | 50-99 | Pump Fail to Start Reservoir LOLO Level |
|  | Non Critical Alarm | Alarm | 200-999 | Standby Pump Fail |
|  | Status Event | Event | 200-999 | Valve Open/Close Status |
|  | Pushbutton Event (Discrete) | Event | 200-999 | Valve Request to Open/Close |
|  | Setpoint Entry Event (Analog) | Event | 200-999 | Valve Manual Position Setpoint |

- Alarm and Event Priorities

#### For a list of alarms/events and the priority level that has been assigned to each alarm/event, refer to Section 2, Tagname Convention.  Within Appendix A of Section 2 is an Excel file that includes all of the currently defined tags and priorities. If an alarm / event / tag is not identified in the tagname convention, the Programmer must contact Halton Region’s SCADA group before continuing.

#### Alarm Colours for all alarm displays are as follows:

| Type of Alarm | Colour | Wonderware Colour (RBG) |  |  |
| --- | --- | --- | --- | --- |
| Unacknowledged and in Alarm (UnAck ALM) | MAGENTA | 255 | 0 | 255 |
| Acknowledged and in Alarm (Ack ALM) | WHITE | 255 | 255 | 255 |
| Unacknowledged and Returned to Normal (UnAck RTN) | BLUE | 0 | 255 | 255 |

- Type of Alarm

#### Alarms are only to be acknowledged using predefined Wonderware functions that interact with the distributed alarm object (e.g. AlmAckAll).  Generally speaking, this is any function that is prefaced with the characters “Alm”.  Direct acknowledgement of alarms or alarm groups using “Ack” or related functions that do not interact with the distributed alarm group is not permitted.

### Alarm Displays

#### Alarms are displayed in four (4) different locations:

##### Alarm Banner;

##### Device Alarms in Control Pop-ups;

##### Alarms Summary; and,

##### Alarms History.

### Device Alarms in Control Pop-ups

#### All device control pop-up windows and analog control pop-up windows have an alarm display at the bottom of the window which displays all of the current active alarms associated with the particular device alarm group.

### Alarm Summary

#### The Alarm Summary window displays alarms in a full size window.  (It does not display any events.)  An example of the Alarm Summary screen is displayed in the figure below:

### Alarm Summary Window

- Alarm Summary Window

#### The properties for this window are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Blue (0/255/255) |
| Window Type | Replace |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | -1 40 1026 720 |
| Window Scripts | On Show, On Hide |

- Alarm Summary Window Properties

#### Window Script On Show:

almQuery("ALMSUM", ALRM_GRP,1,998,"ALL","SUMM");

#### Window script On Hide.

IF ALRMCRIT==1 THEN

ALRM_MIN=1;

ALRM_MAX=999;

ENDIF;

ALRMCRIT=0;

#### ALMSUM is a memory discrete tag.   ALRM_GRP is an indirect message.  Alrm_GRP is used to filter alarms, by Levels 1 – 5, based upon the scripting of the button calling the alarm summary.

- ALMSUM

#### The programmer shall modify the button text to indicate the description appropriate to the alarm level, and will modify the button action script to query the appropriate alarm level from the Distributed Alarm Manager.  For example, selecting Chemical 1 PLC has the following script.

ALRM_GRP= "PLANT\BWCRT01";

IF BUTT_NUM == 1 THEN

Show "Alarm Summary";

ENDIF;

IF BUTT_NUM == 2 THEN

Show "Alarm History";

ENDIF;

Hide "Alarms Menu";

#### The script assigns ALRM_GRP the alarms from BWCRT01 which is a level 5 alarm within the distributed alarm group “Plant”, which points to both BWYCPU01 and BWYCPU02 using the Alarm Hot Backup Manager.

#### The script then filters between the alarm history and alarm summary.

#### The Alarm Summary screen is not to be modified by Programmers.

## Alarms History

#### The Alarms History window displays all alarms and events with the selected group and priority level.  In addition, the window has a similar appearance to the Alarms Summary window.  There is no functionality to acknowledge alarms from this screen.

## Critical Alarms Notification

#### Critical Alarms are identified as alarms where the failure to immediately respond to the alarm condition could adversely affect water quality or result in equipment damage or injury.  Producing a special ‘Critical Alarm Notice’ requires that all unacknowledged alarms from the main alarm group be filtered, or searched, for alarms assigned to a critical alarm priority.

#### The Critical Alarms involves the Critical Alarm Object and six (6) steps:

##### Critical Alarm Object

##### Step 1, the examination of unacknowledged alarms for critical alarms priorities;

##### Step 2, updating the critical alarm object

##### Step 3, adding a short time delay for critical alarming

##### Step 4, retrieve the number of critical alarms currently present

##### Step 5, provide auditable notification that a critical alarm is present

##### Step 6, active the critical alarm notice

### Critical Alarm Object Quick Function

#### The following conditions are part of the scripting for the “Critical Alarm Object” quick function:

{Call Critical Alarm Object}

IF (COMPNAME == "BXXCPU01" OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB)) AND NOT Critical_Open THEN

Show "Critical Alarms";

ENDIF;

#### This quick function is used to display (open) a window called “Critical Alarms’ based on the condition that the workstation is named either BXXCPU01 or BXXCPU02 and both servers have a heartbeat alarm.

#### The workstation names change by an application by application basis.  The “BXXCPU01” workstation is always the main alarm providing node at the plant.  The “BXXCPU02” workstation is always the backup alarm providing node at the plant.  These two names are used throughout the remainder of this section as examples.

#### The Critical_Open tags’ value is determined from the ‘Critical Alarms’ window script (explained further in the document body). Its value is set to one (1) when the Critical Alarms window is open and reset to zero (0) when the window is closed.

#### This quick function ensures that the ‘Critical Alarms’ window is always open and thus able to provide the Critical alarming function with the InTouch application.

#### The critical alarms window has a window size of 1x1 pixels and opens at position (0,0).

### Associated Critical Alarms Condition Scripts

#### The Critical Alarming method is performed by a series of condition scripts, explained in Steps. All scripts are described in detail. The following list outlines all the condition scripts involved.

##### Step 1:  ((COMPNAME == “BXXCPU01”) OR (COMPNAME == “BXXCPU02” AND BXXCPU01DA_HB)) AND (Burloak.UnAck OR Burloak.Alarm)

##### Step 2:  Script_Trigger ==1

##### Step 3:  Time_Delay > 0

##### Step 4:  Script_Trigger2 ==1

##### Step 5, Part A:  Critical_True > 0 AND BXXCOMP

##### Step 5, Part B:  Critical_True >= 1 AND APPRUNTIME > 3

##### Step 5, Part C:  Critical_True >=1 AND BXXCOMP

### Step 1

#### The first step is to initiate the Critical Alarms examination process for the presence of unacknowledged alarms.

#### This is accomplished with the following condition script

((COMPNAME == “BXXCPU01”) OR (COMPNAME == “BXXCPU02” AND

BXXCPU01DA_HB)) AND (Burloak.UnAck OR Burloak.Alarm)

#### The condition requires the computer name to be either BXXCPU01 or BXXCPU02 if BXXCPU01 has a heartbeat alarm.  There must also be an unacknowledged alarm in the main alarm group or an alarm active in the main alarm group.  The programmer is to update this script trigger with the appropriate Level 1 or Level 2 alarm group for the application.

#### The alarm group “Burloak” is used throughout the remainder of this section as an example.

#### This condition script is comprised of four (4) condition types. These are:

##### On True

##### While True

##### On False

##### While False

#### When the condition first becomes true, the “On True” condition type triggers the following script:

Script_Trigger = 1;

#### The following screen shots show the tag properties of the “Script_Trigger” tag.

- Script_Trigger Tag Properties

#### The “Script_Trigger” tag is used as a flag to drive the scripting in Step 2.

#### While the condition is true the “While True” condition is examined every 10000Msec. It executes the following script:

Script_Trigger = 1;

#### Providing that the condition remains ‘True’ the variable (Script_Trigger) is continued to be set to one (1).

#### Once the condition is no longer true, the “On False”’ script reset “Script_Trigger” to zero (0), using the following script.

Script_Trigger = 0;

#### While the condition is false, the “While False” condition is examined every 10000 Msec.  The ‘While False’ Condition script is shown below

Script_Trigger = 0;

#### This condition type continues to keep “Script_Trigger” false.

#### The intent of Step 1 is to set the value of Script trigger to either 1 or 0.  “Script_Trigger” is used to drive all of the scripting in Step 2.

### Step 2

#### The second step in the Critical Alarms examination process is to update the critical alarming object ‘CriticalAlarms’. The following scripts are used.

Script_Trigger ==1

#### This script uses three condition types which are:

##### On False

##### On True

##### While True

#### This On true condition type runs one of the following scripts depending on the type of system:

Wastewater

almQuery( "CriticalAlarms", "Plant Remote", 1, 9, "Unack", "Summ" );

Time_Delay = 1;

Water

almQuery( "CriticalAlarms", "Plant Remote", 1, 99, "Unack", "Summ" );

Time_Delay = 1;

#### The script updates the critical alarm object ‘CriticalAlarms’ with all unacknowledged alarms present in the both hot backup pair name “Plant” and “ Remote” between priorities one (1) to nine (9) or ninety-nine (99) with a query type of ‘Summ’ (Summary). Then set the variable ‘Time_Delay’ to one (1).

#### The “Plant Remote” will change in an application by application basis.  This is the main alarm group for the HMI application.

#### The tag Time_Delay is defined as shown in the figure below.

- Time_Delay Tag Properties

#### The “While True” condition type is examined every 200000 Msec.  The script is as follows:

#### Providing that the condition remains ‘True’ the alarm query will execute and update the alarm object and the variable Time_Delay will be set to one (1).

#### When the condition changes to false, the ‘On False’ condition type executes.  The script is shown below:

Time_Delay = 1;

#### The variable Time_Delay is set to one (1).

#### The intent of Step 2 is to set the value of Time_Delay to 1 and perform an alarm query on the critical alarm object.

### Step 3

#### The third step introduces a time delay using this condition script.

Time_Delay > 0

#### This condition script on executes once every 1000 Msec, when the condition is true.  The script is shown below:

IF Time_Delay > 0 AND Time_Delay < 2 THEN

Time_Delay = Time_Delay + 1;

ELSE

Time_Delay = 0;

Script_Trigger2 = 1;

ENDIF;

#### Once the time delay has expired the script will set Script_Trigger2 to one (1).

#### The purpose of this script and the intent of Step 3 is to introduce a minor delay in the Critical Alarms process to allow certain functions to complete. If this delay is not introduced, particularly in large systems, the count of critical unacknowledged alarms will be inaccurate.

### Step 4

#### Step four involves the condition script as follows.

Script_Trigger2 ==1

#### Condition script will execute only when the condition is true. The script it executes is shown below:

GetPropertyI("CriticalAlarms.NumAlarms", Critical_True);

Script_Trigger2 =0;

#### The GetPropertyl function is used to retrieve the number of critical alarms currently present within the ‘CriticalAlarms’ alarm object. The integer value returned is put into a memory variable name ‘Critical_True’. The ‘Script_Trigger2’ variable is then reset to zero (0).

#### The figure below shows the properties of the ‘Critical_True’ tag.

- Critical_True Tag Properties

#### The intent of Step 4 is to retrieve the number of critical alarms currently present and to set Script_Trigger2 false.  Step 3 will set Script_Trigger2 true after the short delay.

### Step 5

#### Step five (5) involves three (3) condition scripts. They are:

##### Critical_True > 0 AND BXXCOMP

##### Critical_True >= 1 AND APPRUNTIME > 3

##### Critical_True >=1 AND BXXCOMP

#### Part A of Step 5 involves the following condition script:

Critical_True > 0 AND BXXCOMP

#### This condition is true when “Critical_True” is greater than 0, and the local workstation is part of the BXXCOMP group.

#### BXXCOMP is set in the Application => On Startup Script.  This tag identifies that the computer is part of the BXX Plant Group. The group name changes in an application by application basis.

#### This script’s main purpose is to display the Critical Alarm pop-up window when a critical alarm occurs.  It has three Condition types.  These are:

##### On False

##### On True

##### While True

#### Once the script condition (Critical_True >0 and BXXCOMP) is true, the following script is executed:

Show "Critical Alarm Notice";

#### This script shows the ‘Critical Alarm Notice’ pop-up window.

#### When the Condition type changes to ‘While True’ the following script is executed.  The ‘While True’ condition forces the notice to reappear every 40000Msec (40 seconds) until all the critical alarms are acknowledged by the operator.  The script is shown below:

Show "Critical Alarm Notice";

#### Once the ‘Critical Alarm Notice’ pop-up window is shown it may be hidden from other screens being opened such as a process screen.  This ensures that the notice cannot be ignored, by re-opening the pop-up.

#### Once the Condition Type changes to ‘False’ the following script is executed:

Hide "Critical Alarm Notice";

#### This closes the ‘Critical Alarm Notice’ once the tag Critical_True is not greater than zero (0).

#### The intent of Step 5, Part A is to open up the Critical Alarm Notice Pop-up.  The pop-up is discussed further in the body of the document.

#### Part B of Step 5 involves the following condition script:

Critical_True >= 1 AND APPRUNTIME > 3

#### The APPRUNTIME tag properties are shown below:

- APPRUNTIME Tag Properties

#### The value of APPRUNTIME is increased by 1 once every 10000 Msec by the Application => While Running Script.  The intent is to provide a 30 second delay before the Critical Alarm horn software activates.  This allows the HMI application to start up and provides operations enough time to acknowledge any alarms to prevent nuisance operation of the alarm horn.

#### The condition script is used to control plant wide alarm horns. It has four Conditions Types which are:

##### On False

##### On True

##### While True

##### While False

#### The On True and While True conditions activate the alarm horns that are located throughout the plant by setting a tag that writes to the alarm horn activate signal in the target PLC.  The Programmer is to customize this on a per-application basis.

#### The tags and process areas used in the script are application specific.  Each plant has its own set of alarm horns located in key process areas.

#### Once the critical alarm condition is no longer true then the ‘On False’ and ‘While False’ Condition Type set the alarm horns to zero.  The Programmer is to customize this on a per-application basis.

#### The intent of Step 5, Part C is to play an alarm sound at the operations workstation to notify the operator an alarm is prsent.

#### Part C of Step 5 involves the following condition script:

Critical_True >=1 AND OAKCOMP

#### This script has two conditions types:

##### On True

##### While True.

#### The on true condition is shown below.  The programmer is to customize the script based on the actual location of the .wav file.:

PlaySound("c:\FS2000\InTouch\Southwtr\ding.wav", 0 );

#### This condition type is used to turn ON the PC speaker and play a sound file called ‘ding.wav’. It is used to alert the operator at an InTouch node that a Critical alarm is present.

#### The ‘While True’ Condition Type executes every 2317 MSec and is shown below.

PlaySound("c:\FS2000\InTouch\Southwtr\ding.wav", 0 );

#### Step 6 involves generating a visual notice for operations to see that a critical alarm is present.

#### The ‘Critical Alarm Notice’ pop-up window is shown below This window is a pop-up used to notify operations that a critical alarm is present.

- Critical Alarm Window

#### The properties of this window are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Magenta (255/0/255) |
| Window Type | Pop-up |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | 1 81 264 116 |
| Window Scripts | None |

- Critical Alarm Window Properties

#### The purpose of this window is to immediately draw the attention of the operator that there is a life-threatening critical alarm present in the system.

#### The text “CRITICAL ALARM” is MS Sans Serif, Bold, 18 Point font, and Black in colour.  It has two Animation Links.  The first Animation Links => Touch Pushbuttons => Action, runs the following script:

BXXACKALMPB_AR=1;

ALRM_MIN = 1;

ALRM_MAX = 10;

ALRMCRIT = 1;

Show "Critical Alarm Summary";

HideSelf;

#### The properties of the tag BXXACKALMPB_AR are shown below:

- BXXACKALMPB_AR Tag Properties

#### This tag is pointed at the Plant Autodialer PLC.  Once operations click on the text, the critical alarm reminder tag in the Autodialer PLC is set true.  This causes the notification display flag to clear, thus ending the display of the critical alarm pop-up.

#### The remaining actions performed are an alarm query and the opening up the Critical Alarm summary.  From this summary, operations can identify the new critical alarm.

#### The “CRITIAL ALARM” text also has an Animation Links => Miscellaneous => Blink animation shown below:

- Animation Links Blink Text

#### This causes the text to blink invisible when a critical alarm is present.

#### The intent of the step 6 is to open the Critical Alarm Notification pop-up to provide a visual notification to the operator and identify that a life-threatening critical alarm is present.

## Acknowledged Critical Alarm Reminder

#### If there is an acknowledged critical alarm for 15 minutes the Critical Alarm Reminder pop-up will appear. This is to prevent operations from forgetting to deal with a potentially life dangerous situation. This is accomplished through the use of

##### Step 1:  Critical Alarms Acknowledge Window

##### Step 2 Part A:  (COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB)

##### Step 2, Part B:  ((COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB) )  AND Critical_Alarm_Counter==2

##### Step 2, Part C:  ((COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB) ) AND Ack_Critical_Alarm>0

##### Step 2, Part D:  BXXCOMP==1  AND BXXACKALMDA_GA==1

##### Step 3:  Critical Alarm Reminder Pop-up

### Step 1

#### The same method used for querying critical alarms is used to query acknowledged critical alarms. The InTouch Window viewer has the “Critical Alarms Acknowledge” window configured as a home window.

#### The Window is only 1 Pixel by 1 Pixel, so an expanded display of the window is shown below.

- Critical Alarms Acknowledge Pop-up

#### The Properties of this window are:

| Window Properties |  |
| --- | --- |
| Window Colour | White (255/255/255) |
| Window Type | Pop-up |
| Frame Style | Single |
| Title Bar | No |
| Size Controls | NO |
| Dimensions: X Location Y Location Width Height | 0 0 1 1 |
| Window Scripts | Yes |

- Critical Alarms Acknowledge Window Properties

#### The window has three condition type scripts which are:

##### On Show

##### While Showing

##### On Hide

#### The On Show condition type runs the following script:

Critical_Open = 1;

#### This sets the critical open tag true.  Critical_Open is used as a flag to notify InTouch that the window is opened or closed.

#### The “While Showing” condition type executes every 2000 Msec.  This condition runs the following script:

almQuery("AckCriticalAlarms", "Plant Remote",1,10,"Ack","SUMM");

#### The condition type runs a script that updates the acknowledged critical alarms with all acknowledged alarms present in the both hot backup pair name “Plant” and “Remote” between priorities one and ten.

#### The “On Hide” condition type runs the following script:

Critical_Open = 0;

#### This sets the critical open tag off.  Critical_Open is used as a flag to notify InTouch that the window is opened or closed.

#### The Window itself contains a distributed alarm screen called ACKCriticalAlarms.  The same method used for querying critical alarms is used to query acknowledged critical alarms. The general configuration of the distributed alarms is shown below:

- Critical Alarms Acknowledge General Configuration

### Step 2

#### Part A of step 2 uses the following condition script:

(COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB)

#### The condition is true if the workstation name is BXXCPU01 or BXXCPU02 and both servers have a heartbeat alarm.

#### This script uses two condition types; they are:

##### On True

##### While True

#### The “On True” condition type executes the following script:

almQuery( "AckCriticalAlarms", "Plant Remote", 1, 9, "Ack", "Summ" );

#### When the condition becomes true the script will run a query of all of the acknowledged critical alarms.

#### While the condition is true the “While True” script is operated every 30000 Msec

{query acknowledge critical alarm in every 30 seconds and update the counter}

almQuery( "AckCriticalAlarms", "Plant Remote", 1, 9, "Ack", "Summ" );

Critical_Alarm_Counter=Critical_Alarm_Counter +1;

IF Critical_Alarm_Counter >=3 THEN

Critical_Alarm_Counter=0;

ENDIF;

#### The purpose of Step 2, part A is to query for acknowledged critical alarms every 30 seconds. This is accomplished by updating the critical alarm object “AckCriticalAlarms” with all acknowledged alarms present in the alarm groups found in Alarm Hot Backup Manager with a priority between 1 and 10.

#### Part B of Step 2 is to run the next condition script, shown below:

((COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB) ) AND Critical_Alarm_Counter==2

#### The above condition script runs if the workstation name is BXXCPU01 or BXXCPU02 and both servers have a heartbeat alarm.  The Critical Alarm Counter must also equal 2.  The script has two condition types which are

##### On True

##### While True

#### The “On True” condition type runs the following script:

GetPropertyI("AckCriticalAlarms.NumAlarms", Ack_Critical_Alarm);

#### This script gets the acknowledged critical alarm number via a memory integer tag “Critical_Ack_Alarm”

#### The “While True” condition type executes while the condition is true, every 5000 MSec.  The script is shown below:

{query acknowledged critical alarm number in every 5 seconds}

GetPropertyI("AckCriticalAlarms.NumAlarms", Ack_Critical_Alarm);

#### The intent of Step 2 Part B is to get the acknowledged critical alarm number via a memory integer tag “Critical_Ack_Alarm” while the condition is true every 5 seconds:

#### Step 2 Part C run the following condition script:

((COMPNAME == "BXXCPU01") OR (COMPNAME == "BXXCPU02" AND BXXCPU01DA_HB) )  AND Ack_Critical_Alarm>0

#### This script executes if the workstation name is BXXCPU01 or if the workstation name is BXXCPU02 and both servers have a heartbeat alarm.  The Ack_Critical_Alarm Counter must also be greater than Zero.  The script uses the condition types of

##### On False

##### On True

##### While True

#### The “On True” condition type script is as follows:

BXXACKALMPB_EN=1;

#### This sets the acknowledged critical alarm tag to true.  The BXXACKALMPB_EN tag properties are shown below:

- BXXACKALMPB_EN Tag Properties

#### This tag writes to the acknowledged critical alarm tag in the plant Autodialer PLC.

#### The “While True” condition type runs every 30000 Msec while the condition is true.  The script is shown below:

BXXACKALMPB_EN=1;

#### Both the “On True” and “While True” condition type scripts start a 15-minute timer in the PLC. If the acknowledged critical alarm isn’t cleared in 15 minutes, the PLC will set the acknowledged critical alarm tag BXXACKALMDA_GA to 1.  This sets the final script true.

#### The intent of Step 2 Part C is to start the 15-minute timer in the Autodialer PLC.

#### Step 2 Part D uses the following condition script:

BXXCOMP==1 AND BXXACKALMDA_GA==1

#### This condition script is true is the workstation is a BXX Computer and the BXXACKALMDA_GA tag is true.  The properties of the tag are shown below:

- BXXACKALMDA_GA Tag Properties

#### This tag resides in the Plant Autodialer PLC and is used to flag SCADA that the critical alarm has remained after the 15-minute timer has elapsed.

#### This script has the three condition types of On False, On True and While True.

#### The “On True” script is as follows:

Show "Critical Alarm Reminder";

#### The “While True” script runs every 30000 Msec while the condition is true.  The script is as follows:

Show "Critical Alarm Reminder";

#### Both the “On True” and “While True” scripts show the Critical Alarm Reminder pop-up.

#### The “On False” script is as follows:

Hide "Critical Alarm Reminder";

#### This script hides the Critical Alarm Reminder pop-up when the condition is no longer true.

#### The intent of Step 2 part 2 is to display and hide the Critical Alarm reminder pop-up.

#### Step 3 of the Acknowledged Critical Reminder is the ‘Critical Alarm Reminder’ pop-up window.  The Window is shown below:

- Critical Alarm Reminder Window

#### The Properties of this window are:

| Window Properties |  |
| --- | --- |
| Window Colour | Yellow (255/255/0) |
| Window Type | Pop-up |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | Yes |
| Dimensions: X Location Y Location Width Height | 324 160 400 116 |
| Window Scripts | No |

- Critical Alarm Reminder Window Properties

#### The purpose of this pop-up is to remind the operator there is an acknowledged critical alarm presented in the system.

#### The text ‘Critical Alarm Reminder’ text is MS Sans Serif, Bold, 18 Point font and Black in Colour.  It has two animation links.  The first Animation Links => Touch Pushbuttons => Action, runs the following script:

BXXACKALMPB_AR=1;

ALRM_MIN = 1;

ALRM_MAX = 10;

ALRMCRIT = 1;

Show "Critical Alarm Summary";

#### When the operator clicks on the text from the pop-up window, this script will execute.  It acknowledges the critical alarm reminder and opens the ‘Critical Alarm Summary’ screen and display the critical alarm(s).

#### Once the critical alarm reminder has been acknowledged, operations have another fifteen minutes to clear the critical alarm.

#### The “Critical Alarm Reminder” text also has an Animation Links => Miscellaneous => Blink animation, shown below:

- Animation Links Blink Text

#### The intent of Step 3 is to generate a visual reminder to operations that a potentially life dangerous situation is still present at the plant.

## Sample PLC Code Related to Critical Alarm Reminder

#### Refer to Section 5 for examples of the PLC source code

## Alarm History - SQL

#### The SQL History uses a Built in ActiveX control for InTouch.  It queries the Alarms and Events SQL database to provide a larger historical record then is available with the default Alarms and Events buffer in InTouch.

#### The Window is shown below.  Programmers are not to modify this window.

- Alarm History - SQL

## InTouch Trends

#### This information is provided for reference to existing applications.  Programmers shall not create new applications with InTouch trending.  Halton Region’s preference is for operation groups to use Historian Trend (Wonderware Historian) trending.

#### All InTouch trends are displayed using a standard trending screen called “InTouch Trends.”

#### The InTouch Trends window uses only indirect tags and is configured to display either four (4) or eight (8) values.  An example of the window is displayed in the figure below.

- InTouch 4 Pen Trend

#### The properties for this window are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | Grey (192/192/192) |
| Window Type | Overlay |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | -1 40 1028 720 |
| Window Scripts | None |

- InTouch Trend Window Properties

#### In order for the InTouch Trends screen to execute properly the four (4) indirect pen tags must be associated with four (4) direct tags.  This script is associated with the button that executes a specific trend:

Animation Links => Touch Pushbuttons => Action Script On Key Up

HT_TREND.Pen1=BXXWW11LIAI_CV.TagID;

HT_NAME1= BXXWW11LIAI_CV.Comment;

HT_UNIT1= BXXWW11LIAI_CV.EngUnits;

HT_TREND.Pen2=BXXBLS1LIAI_CV.TagID;

HT_NAME2= BXXBLS1LIAI_CV.Comment;

HT_UNIT2= BXXBLS1LIAI_CV.EngUnits;

HT_TREND.Pen3=UnusedAnalog1.TagID;

HT_NAME3=UnusedAnalog1.Comment;

HT_UNIT3=UnusedAnalog1.EngUnits;

HT_TREND.Pen4=UnusedAnalog2.TagID;

HT_NAME4=UnusedAnalog2.Comment;

HT_UNIT4=UnusedAnalog2.EngUnits;

HT_TREND.ChartStart=($Date*86400)-HT_START+HTOFFSET;

HT_TREND.ChartLength=HTLENGTH;

Show "InTouch Trends";

HideSelf;

#### Selection between multiple and single axis is performed in the main trends window, below.

- InTouch 4 Axis Selection

#### Each button has a script to set the Histaxis Memory Integer tag to 1 or 2.

#### The four (4) pen colours are as follows;

##### Pen 1	Black	(0/0/0)

##### Pen 2	Red	(255/0/0)

##### Pen 3	Blue	(0/0/255)

##### Pen 4	Green	(0/132/0)

#### A double click on the graph in the middle of the InTouch Trends window will open up a configuration screen as shown below.

- InTouch Trend Configuration

#### No changes to this configuration are necessary.  However, this would be the configuration screen to use to change such characteristics to the InTouch Trend window such as the initial time span, time divisions, value divisions, label placements and the colour and width of the pens.

#### ‘Last Hour’ Button

#### The ‘Last Hour’ button changes the trend so that it displays the trends for the last hour.  The Animation Links => Touch Pushbuttons => Action Script On Key Up is displayed below.

- Last Hour Script

‘Last 24 Hours’ Button

#### The ‘Last 24 Hours’ button changes the trend so that it displays the trends for the last 24 hours. The Animation Links => Touch Pushbuttons => Action Script On Key Up is displayed below.

- Last 24 Hours Script

Last 7 Days

#### The ‘Last 7 Days” button changes the trend so that it displays the trends for the last 7 days. The Animation Links => Touch Pushbuttons => Action Script On Key Up is displayed below.

- Last 7 Days Script

- ‘Print’ Button

#### The ‘Print’ button is configured to print the trend to the default printer. The Animation Links => Touch Pushbuttons => Action Script On Key Up is displayed below.

- Print Script

### 8 Pen Trend

#### The Eight Pen Trend is similar to the four pen trend, except it has been set up to display eight (8) values.  The window is shown below:

- 8 Pen Trend

#### The only difference between a four pen trend and an eight pen trend are the four additional pens.

#### The eight (8) pen colours are as follows;

##### Pen 1	Black	(0/0/0)

##### Pen 2	Red	(255/0/0)

##### Pen 3	Blue	(0/0/255)

##### Pen 4	Green	(0/132/0)

##### Pen 5	Yellow (255/255/0)

##### Pen 6	Cyan	(200/255/255)

##### Pen 7	Magenta (255/0/255)

##### Pen 8	Orange (255/130/0)

#### In order for the InTouch Trends screen to execute properly the eight (8) indirect pen tags must be associated with eight (8) direct tags.  This script is associated with the button that executes a specific trend:

Animation Links => Touch Pushbuttons => Action Script On Key Up

HT_TREND.Pen1=BXXSLP1SIAI_CV.TagID;

HT_NAME1= BXXSLP1SIAI_CV.Comment;

HT_UNIT1= BXXSLP1SIAI_CV.EngUnits;

HT_TREND.Pen2= BXXSLP2SIAI_CV.TagID;

HT_NAME2= BXXSLP2SIAI_CV.Comment;

HT_UNIT2= BXXSLP2SIAI_CV.EngUnits;

HT_TREND.Pen3= BXXSLP3SIAI_CV.TagID;

HT_NAME3= BXXSLP3SIAI_CV.Comment;

HT_UNIT3= BXXSLP3SIAI_CV.EngUnits;

HT_TREND.Pen4= BXXSLP4SIAI_CV.TagID;

HT_NAME4= BXXSLP4SIAI_CV.Comment;

HT_UNIT4= BXXSLP4SIAI_CV.EngUnits;

HT_TREND.Pen5= BXXDIH1FIAI_CV.TagID;

HT_NAME5= BXXDIH1FIAI_CV.Comment;

HT_UNIT5= BXXDIH1FIAI_CV.EngUnits;

HT_TREND.Pen6= BXXDIH1PIAI_CV.TagID;

HT_NAME6= BXXDIH1PIAI_CV.Comment;

HT_UNIT6= BXXDIH1PIAI_CV.EngUnits;

HT_TREND.Pen7= BXXBPF1FIAI_CV.TagID;

HT_NAME7= BXXBPF1FIAI _CV.Comment;

HT_UNIT7= BXXBPF1FIAI _CV.EngUnits;

HT_TREND.Pen8=UnusedAnalog1.TagID;

HT_NAME8=UnusedAnalog1.Comment;

HT_UNIT8=UnusedAnalog1.EngUnits;

HT_TREND.ChartStart=($Date*86400)-HT_START+HTOFFSET;

HT_TREND.ChartLength=HTLENGTH;

Show "InTouch Trends";

HideSelf;

### Unused Pens

#### All Pens must have a tag mapped to them.

#### In applications where not all of the pens are required, the Base application has a built in set of tags called “UnusedAnalog1” And “UnusedAnalog2”.  .  Either of these tags should be inserted into the script to assign the trend pen as unused.

#### In applications where both the four and eight pen trend are used, all eight pens must be in the Action script.  Failure to do so will causes pens 5 – 8 to appear on the four pen trend when operators switch between trends.

## Historian Trends

#### Halton Region also uses Historian Trend trends.  This is the preferred method for visualizing historical data.  Programmers may be required to configure trends for both InTouch and Historian Trend.

#### The InTouch Trends Menu and the Historian Trend Trends menu should be displayed using the same graphics with the same order.  Below is a sample Historian Trend Trends Menu:

- Historian Trend Plant Trends Menu

#### The only difference between this menu and the InTouch trend selection menu should be the scripting behind each trend button.  The name of the trend button should clearly indicate the function of the trend.  Programmers should use names such as Free Chlorine Residual, Finished Water Quality, or Raw Sewage pumps.

#### Before creating trends Programmers should contact the plant and request a list of the trends that operations would like to see.

#### The text on each button is System, Bold, 10 Point Font and black in colour. Programmers should attempt to keep the buttons the same size, aligned in rows and columns.  The order and grouping of the buttons should be kept together when possible.  In the above example, the raw water is the first process and is in the top left hand corner.  All of the chemical trends have also been grouped together.  It is acceptable to move buttons around, so that the trends can be logically ordered.

#### Each button has one Animation Links => Touch Push Buttons => Action script.  The script for each button is slightly different, depending upon the data the trend is providing.  The following example is from the Moore Park Booster station:

#aaHistClientTrend1.ClearTags();

#aaHistClientTrend1.DefaultTagPrecision=3;

#aaHistClientTrend1.DefaultTagFormat=2;

HT_NAME1 = MPSSTN1PIAI_CV.Name;

HT_NAME2 = MPSSTN2PIAI_CV.Name;

HT_NAME3 = MPSSTN3PIAI_CV.Name;

HT_NAME4 = MPSDIH1FIAI_CV.Name;

HT_NAME5 = MPSCHD1CRAI_CV.Name;

HT_NAME6 = MPSHBP1DMAI_CV.Name;

HT_NAME7 = MPSHBP2DMAI_CV.Name;

HT_NAME8 = MPSHBP3DMAI_CV.Name;

#aaHistClientTrend1.AddMultipleTags=1;

#aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME1);

#aaHistClientTrend1.AddMultipleTags=0;

#aaHistClientTrend1.ShowValuesAtCursor=1;

#aaHistClientTrend1.HighlightCurrentTag =1;

#aaHistClientTrend1.CurrentTagPenStyle=0;

#aaHistClientTrend1.CurrentTagColor =204;

#aaHistClientTrend1.CurrentTagTrendType =1;

#aaHistClientTrend1.AddMultipleTags=1;

#aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME2);

#aaHistClientTrend1.AddMultipleTags=0;

#aaHistClientTrend1.ShowValuesAtCursor=1;

#aaHistClientTrend1.HighlightCurrentTag =1;

#aaHistClientTrend1.CurrentTagPenStyle=0;

#aaHistClientTrend1.CurrentTagColor =16711680;

#aaHistClientTrend1.CurrentTagTrendType =1;

#aaHistClientTrend1.AddMultipleTags=1;

#aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME3);

#aaHistClientTrend1.AddMultipleTags=0;

#aaHistClientTrend1.ShowValuesAtCursor=1;

#aaHistClientTrend1.HighlightCurrentTag =1;

#aaHistClientTrend1.CurrentTagPenStyle=0;

#aaHistClientTrend1.CurrentTagColor =26112;

#aaHistClientTrend1.CurrentTagTrendType =1;

#aaHistClientTrend1.AddMultipleTags=1;

#aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME4);

#aaHistClientTrend1.AddMultipleTags=0;

#aaHistClientTrend1.ShowValuesAtCursor=1;

#aaHistClientTrend1.HighlightCurrentTag =1;

#aaHistClientTrend1.CurrentTagPenStyle=0;

#aaHistClientTrend1.CurrentTagColor =0;

#aaHistClientTrend1.CurrentTagTrendType =2;

#aaHistClientTrend1.AddMultipleTags=1;

#aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME5);

#aaHistClientTrend1.AddMultipleTags=0;

#aaHistClientTrend1.ShowValuesAtCursor=1;

#aaHistClientTrend1.HighlightCurrentTag =1;

#aaHistClientTrend1.CurrentTagPenStyle=0;

#aaHistClientTrend1.CurrentTagColor = 3381759;

#aaHistClientTrend1.CurrentTagTrendType =1;

#aaHistClientTrend1.AddMultipleTags=1;

#aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME6);

#aaHistClientTrend1.AddMultipleTags=0;

#aaHistClientTrend1.ShowValuesAtCursor=1;

#aaHistClientTrend1.HighlightCurrentTag =1;

#aaHistClientTrend1.CurrentTagPenStyle=0;

#aaHistClientTrend1.CurrentTagColor =6697983;

#aaHistClientTrend1.CurrentTagTrendType =2;

#aaHistClientTrend1.AddMultipleTags=1;

#aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME7);

#aaHistClientTrend1.AddMultipleTags=0;

#aaHistClientTrend1.ShowValuesAtCursor=1;

#aaHistClientTrend1.HighlightCurrentTag =1;

#aaHistClientTrend1.CurrentTagPenStyle=0;

#aaHistClientTrend1.CurrentTagColor =16776960;

#aaHistClientTrend1.CurrentTagTrendType =2;

#aaHistClientTrend1.AddMultipleTags=1;

#aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME8);

#aaHistClientTrend1.AddMultipleTags=0;

#aaHistClientTrend1.ShowValuesAtCursor=1;

#aaHistClientTrend1.HighlightCurrentTag =1;

#aaHistClientTrend1.CurrentTagPenStyle=0;

#aaHistClientTrend1.CurrentTagColor = 65280;

#aaHistClientTrend1.CurrentTagTrendType =2;

HideSelf;

#### The script can be broken down into 4 steps:

##### Step 1:  Set-up the trend

##### Step 2:  Add the tags to be trended

##### Step 3:  Set each pen

##### Step 4:  Hide the trend menu

#### Step 1 is to setup the trend.  To accomplish this, the following three action scripts are run:

#aaHistClientTrend1.ClearTags();

#aaHistClientTrend1.DefaultTagPrecision=3;

#aaHistClientTrend1.DefaultTagFormat=2;

#### #aaHistClientTrend1.ClearTags() is used to clear all of the tags on the current trend.  This is used when operations select multiple trends using the Historian Trend Trends menu.

#### #aaHistClientTrend1.DefaultTagPrecision=3 is used to set the number of decimal places displayed on the trend.  Depending upon the trend, this value may be changed between 0 and 3.  The default value is 3.

#### #aaHistClientTrend1.DefaultTagFormat=2 is used to set the line weight of the pens used in the trend.  This value is set by Halton Region and is not to be changed.

#### Step 2 is to add the tags to the trend.  This is accomplished with the following action scripts:

HT_NAME1 = MPSSTN1PIAI_CV.Name;

HT_NAME2 = MPSSTN2PIAI_CV.Name;

HT_NAME3 = MPSSTN3PIAI_CV.Name;

HT_NAME4 = MPSDIH1FIAI_CV.Name;

HT_NAME5 = MPSCHD1CRAI_CV.Name;

HT_NAME6 = MPSHBP1DMAI_CV.Name;

HT_NAME7 = MPSHBP2DMAI_CV.Name;

HT_NAME8 = MPSHBP3DMAI_CV.Name;

- This adds the appropriate tags to the trend. HT_NAME1 is the first tag used in the trend.  MPSSTN1PIAI_CV is the tagname for the first trended tag.  The tagnames change on a trend by trend basis.

#### In this example there are eight tags being added to the trend.  Each Historian Trend can have a different number of tags for each trend.  The minimum number of tags to be displayed on any Historian Trend is 1.  The maximum number of tags to be displayed on any Historian Trend is 8.

#### There is no limit to the number of trends any tag can be displayed on.

#### Step 3 is to set each pen on the trend.  This is accomplished using the following action scripts:

#aaHistClientTrend1.AddMultipleTags=1;

#aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME1);

#aaHistClientTrend1.AddMultipleTags=0;

#aaHistClientTrend1.ShowValuesAtCursor=1;

#aaHistClientTrend1.HighlightCurrentTag =1;

#aaHistClientTrend1.CurrentTagPenStyle=0;

#aaHistClientTrend1.CurrentTagColor =204;

#aaHistClientTrend1.CurrentTagTrendType =1;

##### #aaHistClientTrend1.AddMultipleTags=1 is used to set a flag that a tag is being added to the InTouch Trends.  This script is common for all eight pens.

##### #aaHistClientTrend1.AddAnyTag("SCADA1", HT_NAME1) is used to add the tag to the trend.

###### “SCADA1” is the name of the InTouch Historian that the tag resides on.  All Water tags reside on SCADA1.  All Wastewater, Bio-solids and Solid Waste tags reside on SCADA2.  For Wastewater, Bio-solids and Solid Waste trends “SCADA1” is substituted with “SCADA2.”

###### HT_NAME1 is defined in step 2.

##### #aaHistClientTrend1.AddMultipleTags=0 is used to set a flag that the addition of the tag is complete.  This script is common for all eight pens.

##### #aaHistClientTrend1.ShowValuesAtCursor=1 this is used to show the current value of the tag at the cursor position.  This script is common for all eight pens.

##### #aaHistClientTrend1.HighlightCurrentTag =1 this is used to Highlight the Current tag name displayed on the trend.  This script is common for all eight pens.

##### #aaHistClientTrend1.CurrentTagPenStyle=0 this sets the pen style for the trend.  This script is common for all eight pens.  This value should always be set to 0.

##### #aaHistClientTrend1.CurrentTagColor =204 this sets the colour of the tag.  Each pen tag has its own unique colour.  Colours are set by Halton Region and are not to be changed.

##### #aaHistClientTrend1.CurrentTagTrendType =1 this is used to set the type of trend.  A value of 1 sets the trend to best fit.  This is used for analog data such as pressures, levels and analyzers.  A value of 2 sets the pen to a plot data.  This is used to trend a pump running status or a similar discrete signal.

#### As with Step 2, only the number of used pens require scripts.

#### Step 4 closed the Historian Trend menu using the following action script:

HideSelf;

#### The Historian Trend Trends menu is shown below:

- Historian Trend Trend Menu

#### The window properties are as follows:

| Window Properties |  |
| --- | --- |
| Window Colour | White (255/255/255) |
| Window Type | Replace |
| Frame Style | Single |
| Title Bar | Yes |
| Size Controls | No |
| Dimensions: X Location Y Location Width Height | -1 40 1028 620 |
| Window Scripts | On Show |

- Historian Trend Trend Window Properties

#### The on show window script is as follows:

#aaHistClientTrend1.AddServer("SCADA1","wwUser","wwUser");

#aaHistClientTrend1.QueryTimeout =300;

#aaHistClientTrend1.RetrievalOptionsRetrievalStyle = "Cyclic (Historian Trend 9.1)";

#aaHistClientTrend1.RetrievalOptionsValueDeadband = 5;

#### #aaHistClientTrend1.AddServer("SCADA1","wwUser","wwUser").  This action script adds the SCADA1 server to Historian Trend and logs the user on as wwUser with the password of wwUser.  For Wastewater, Bio-solids and Solid Waste HMI applications, “SCADA1” is replaced with “SCADA2.”  Programmers should not need to modify this script.

#### #aaHistClientTrend1.QueryTimeout =300 is used to set the time out value when Historian Trend retrieves data.  The value of 300 is referenced in Seconds.  This allows 300 Seconds for Historian Trend to retrieve the data.  If the data cannot be retrieved within this time period, Historian Trend stops attempting to retrieve the data.  This value is set by Halton Region and is not to be changed

#### #aaHistClientTrend1.RetrievalOptionsRetrievalStyle = "Cyclic (Historian Trend 9.1)" this script is used to notify Historian Trend how to retrieve the data.  The current version of Historian Trend retrieves data differently than previous versions.  Halton Region has set the retrieval method to use the Historian Trend 9.1 method.  This is set by Halton Region and is not to be changed

#### #aaHistClientTrend1.RetrievalOptionsValueDeadband = 5 this sets the dead band value for the trended data displayed.  This value is set by Halton Region and is not to be changed

#### The Historian Trend Trend window is a built in aaHistClientTrend1, the properties are shown below:

- aaHistClientTrend1 Control Name

#### The properties and events are set by Halton Region and Programmers should contact Halton Region if they require more information.

## OI Server Configuration

#### This section should also be read in conjunction with Section 5.

#### Halton Region has standardized on Wonderware Device Integration Servers.  These Servers are only used on the two Polling Nodes for the InTouch application.  The servers are configured as primary and backup servers.

#### Halton Region approves the use of the following OI server for all Rockwell PLCs:

##### OI ABCIP

#### The DASABTCP and ABTCP drivers may be used in some applications to support legacy power monitors.  Programmers are not to configure any new devices using these drivers without approval from Halton Region.

#### Power Monitors are to be added to the IO configuration tree of the PLC for integration with the Power Monitor UDDT.  Programmers shall not directly interface to the power monitor using the OI driver without written permission from Halton Region.

#### The use of any other OI driver requires written approval from Halton Region.

#### When Programmers add a new PLC to an existing HMI application, they must also update the plant’s IO servers to poll the new device.

#### All OI servers are configured as automatic services (Auto Start after Reboot).

#### Each plant’s OI Server will be setup to poll all of the existing PLCs.  Programmers will need to add a new object for the new PLC they are adding.  ControlLogix PLCs are added as “ENB_CLX” objects.  CompactLogix PLCs are added as “ENB_CPLX”.

#### There should be only one connection per PLC, and each connection should only have one Device Group Configured.  If a programmer believes multiple connections or device groups are required they are to make a written request to Halton Region explaining the rationale for this requirement.

### Installing OI servers

#### The SCADA group is responsible for ensuring the latest version of the OI software is installed on the IO Servers.

#### The configuration set filename for each IO Server is to be named based on the specific application.  The active configuration set is automatically saved whenever it is updated.

| Plant | I/O Server | Configuration Set Filename |
| --- | --- | --- |
| Burlington Water Plant | ABCIP | BWPP – OIABCIP |
| Oakville Water Plant | ABCIP | OWPP – OIABCIP |
| Burloak Water Plant | ABCIP | BOWPP – OIABCIP |
| North Water | ABCIP | NORTH-WTR – OIABCIP |
|  | ABTCP | NORTH-WTR – ABTCP |
| Water Distribution | ABCIP | WD – OIABCIP |
|  | ABTCP | WD – ABTCP |
| Skyway WWTP | ABCIP | SKYWAY – OIABCIP |
| South West WWTP | ABCIP | SW WWTP – OIABCIP |
|  | ABTCP | SW WWTP – ABTCP |
| South East WWTP | ABCIP | SE WWTP – OIABCIP |
|  | DASABTCP | SE WWTP – DASABTCP |
| Mid-Halton WWTP | ABCIP | MH WWTP – OIABCIP |
|  | ABTCP | MH WWTP – ABTCP |
| Milton WWTP | ABCIP | MILTON WWTP – OIABCIP |
| Georgetown WWTP | ABCIP | GEO WWTP – OIABCIP |
| Acton WWTP | ABCIP | ACTON WWTP – OIABCIP |
| Wastewater Collection | ABCIP | WWC WWTP – OIABCIP |
|  | DASABTCP | WWC WWTP – DASABTCP |
|  | ABTCP | WWC WWTP – ABTCP |
| Landfill | ABCIP | LANDFILL – OIABCIP |
| Biosolids | ABCIP | BIOSOLIDS – OIABCIP |

- Configuration Set Filenames

### Adding a new ControlLogix Object

#### Under the ABCIP server installed on the primary SCADA Polling Node, under the main plant group, right click on the group and select new “ENB_CLX Object”

- Adding a New CLX Object

#### The name of the object group should be the same as the PLC name, and the same as InTouch Topic and Access Name.

#### The Programmer is required to enter the I.P. address of the new PLC in the Host Name.  The I.P. address is supplied to the Programmer by Halton Region.

#### Halton Region will provide the Programmer with appropriate timeouts and topic update interval times.

| Update Interval Time | Connection Timeout | Reply Timeout |
| --- | --- | --- |
| 1000 mS | 1500 mS | 2 S |
| 1500 mS | 2250 mS | 3 S |
| 2500 mS | 3750 mS | 5 S |
| 3000 mS | 4500 mS | 6 S |
| 3500 mS | 5250 mS | 7 S |
| 4500 mS | 6750 mS | 9 S |
| 5000 mS | 7500 mS | 10 S |

- Connection and Reply Timeout Settings

#### The following figure shows the new object.  The connection timeout value should be entered based upon the above table.

- CLX Object Parameters

#### Next a new Backplane_CLX objet needs to be added.  The backplane object name should be the same as the Object name.  The Backplane_CLX object has no configuration parameters.

#### Next a Logix5000_CLX object needs to be added.  The Logix5000 object name should be the same as the Object Name.

#### The Slot Number is the Slot in which the PLC Processor resides.

#### The Reply timeout should be set to set as shown in the Connection and Reply Timeout Settings table.

#### The MAX CIP Connections should be limited to 4

#### The Optimization should be set for “Optimize for Startup Time”

#### Optimize User Defined Data Types should be Checked off.

#### The tag Database should be set to “Auto Load Tags”, “Auto Synchronize Tags”, and “Use Persisted Tags” This is the default setting.

- Logix5000_CLX Configuration

#### Under the Device Groups tab, Programmers must also add the device group.  The device group name is the same as the Object Name and must match the access name configured In InTouch in order for communications to work.

#### Halton Region will provide the Programmer with the Update Interval time.

- Logix5000_CLX Device Group

#### Once the Update Interval Time is saved, Programmers should click on the Device Object.  The Server Manager will prompt the user that the configuration has been changed, and ask for conformation to save the changes.

#### Once the changes are saved the Programmer must update the DAS Server on the backup polling node.

### Adding a New CompactLogix Object

#### This information is provided for reference purposes only.  Written permission from Halton Region is required for any new CompactLogix installations.

#### In the ABCIP program installed on the primary SCADA Server, under the main plant group, right click on the group and select new “ENB_CPLX Object”

- Adding ENB_CPLX Object

#### The name of the object group should be the same as the PLC name, and the same as InTouch Topic and Access Name.

#### The Programmer is required to enter the I.P. address of the new PLC in the Host Name.  The I.P. address is supplied to the Programmer by Halton Region.

#### The connection timeout should be set as shown in the Connection and Reply Timeout Settings table.

- ENB_CPLX Object Parameters

#### Next a new Backplane_CPLX objet needs to be added.  The Backplane object name should be the same as the Object name.  The Backplane_CPLX object has no configuration parameters.

#### Next a Logix_CPLX object needs to be added.  The Logix object name should be the same as the Object Name.

#### The Slot Number is the Slot in which the PLC Processor resides, for an ENB_CPLX object this is always slot 0.

#### The Reply timeout should be set as shown in the Connection and Reply Timeout Settings table.

#### The MAX CIP Connections should be limited to 4

#### The Optimization should be set for “Optimize for Startup Time”

#### Optimize User Defined Data Types should be Checked off.

#### The tag Database should be set to “Auto Load Tags”, “Auto Synchronize Tags”, and “Use Persisted Tags” This is the default setting.

- Logix_CPLX Configuration

#### Under the Device Groups tab, Programmers must also add the device group.  The device group name is the same as the Object Name and must match the Access name configured in InTouch for communications to work.

#### Halton Region will provide the Programmer with the Update Interval time.

- Logix_CPLX Device Group

#### Once the Update Interval Time is saved, Programmers should click on the Device Object.  The DAServer Manager will prompt the user that the configuration has been changed, and ask for conformation to save the changes.

#### Once the changes are saved the Programmer must update the DAS Server on the backup polling node.

### Adding a Power Monitor 5000 or SLC 5/05 or Object

#### This information is provided for reference purposes only.  Halton Region does not accept the use of SLC 5/05 processors for new installs.  Written permission from Halton Region is required to read data directly from a 5000 series power monitor to an OI server.

#### In the ABCIP program installed on the primary SCADA Server, under the main plant group, right click on the group and select new “SLC500_EN Connection”

- Adding SLC500_TCPIP Object

#### The name of the object group should be the same as the PLC name, and the same as InTouch Topic and Access Name.

#### The Programmer is required to enter the I.P. address of the new PLC in the Host Name.  The I.P. address is supplied to the Programmer by Halton Region.

#### The connection timeout should be as shown in the Connection and Reply Timeout Settings table.

#### Reply Timeout should be set as shown in the Connection and Reply Timeout Settings table.

#### Use CIP Connection should be checked and the Maximum CIP connections should be 4.

- SLC500_TCPIP Object Parameters

#### Under the Device Groups tab, Programmers must also add the device group.  The device group must match the access name configured in InTouch for communications to work.  The device group name is the same as the Object Name.

#### Halton Region will provide the Programmer with the Update Interval time.

- SLC500_TCPIP Device Group

#### Once the Update Interval Time is saved, Programmers should click on the Device Object.  The DAServer Manager will prompt the user that the configuration has been changed, and ask for conformation to save the changes.

#### Once the changes are saved the Programmer must update the IO Server on the backup polling node.

## Working Alone System – Waste Water

### Hours of Operation

#### Saturday, Sunday, Statutory, declared Holidays (7.30 am to 11.30 am) and after regular working hours (4:00 pm to 7:30am).

### Working Alone System Enable

#### A sample window is attached below. Each plant will have different phone numbers but the operation is the same.

- Working Alone Main Window

#### The SCADA system at the plant will be used as an “Auto Attendant”. Plant operator must enable the system at the start of his/her shift. This is done by clicking on the Green <DISABLED> button.

#### Once clicked the button will change to Red, the text will change to ENABLED and the  condition script in will run and open the Work Alone System Enabled window.

- Working Alone System Enabled Pop-up

- Working Alone Enabled Window Script – On True

#### If this window is CLOSED a condition script will open the window in 60 seconds. (note tag shown is for the SouthWest plant): The HMI script for this window is shown below.

- Working Alone Enabled Window Script – While True

#### The script shown below closes the window Work Alone System Enabled closed the window when the Work Alone System is Disabled.

- Working Alone Enabled Window Script – On False

#### Notify Timer Duration will show 120 mins and update the time left before the system will go into alarm. The operator must click the  <Reset Timer> button to reset the timer  and to prevent a Working Alone alarm. At anytime when the  <Reset Timer> is clicked all timers are reset and the dialer alarm is cleared if active.

### Working Alone Warning

#### The SCADA system is pre programmed at two (2) hour countdown timer (within the PLC code). Should the countdown timer expire, (no acknowlegment by operator) this will generate a pop-up reminder prompt.

- Working Alone Warning Pop-up

#### This will give a visual reminder to the operator that they need to acknowledge the system promptly. Once this window is active the <Alarm Time Delay> timer starts. This allows an additional five (5) minutes for the operator to acknowledge the Working Alone System before triggering the dialer alarm.

#### The HMI condituion scripts for this window is shown below (note tag shown is for the SouthWest plant).

- Working Alone Operator Warning Script – On True

#### The condition script below opens the window every 60 seconds while Alarm Time Delay timer is counting down.

- Working Alone Operator Warning Script – While True

#### The condition script below will close the Operator Warning window if the Alarm Time Delay timer is reset.

- Working Alone Operator Warning Script – On False

#### The condition script below will close the Operator Warning window every 30 seconds while the Alarm Time Delay timer is not counting down.

- Working Alone Operator Warning Script – While False

### Working Alone Alarm

#### Should the two (2) hour countdown timer and the five (5) min Alarm Time Delay timer expire then the OPERATOR DOWN ALARM window will appear.

- Working Alone System Alarm Pop-up

#### At this point the alarm dialer channel will activate and begin to call the series of pre-programmed phone numbers as shown in the Default Dialer Call List on the Operator Notification window.

#### Resetting the alarm is a 2 step process. It must first be cleared on the plant HMI, Operator Notification window by clicking the <Reset Timer> button. Then the alarm can be cleared from the dialer by calling the dialer and pressing 9 or locally at the auto dialer interface which is the same way all alarms are cleared.

#### The HMI scripts for this window is shown below for the SouthWest plant.

- Working Alone Operator Alarm Script – While True

#### The script shown above opens the Operator Notification window while the Alarm Time Delay timer is done.

#### The script shown below opens the Operator Notification window every 60 seconds while the Alarm Time Delay timer is done.This is incase the window becomes closed while the Alarm Time Delay timer is done.

- Working Alone Operator Alarm Script – While True

#### The script shown below closes the window Operator Notification when the Alarm Time Delay timer is reset.

- Working Alone Operator Alarm Script – On False

#### The script shown below closes the window Operator Notification every 30 seconds while the Alarm Time Delay timer is not done. This is in case the window becomes opened while the Alarm Time Delay timer is not done.

- Working Alone Operator Alarm Script – While False

### End of Shift

#### At the end of shift the operator will have to disable the system by clicking the Red <Enabled> button. If this is forgotten the system will go into alarm and the dialer will activate according to the Working Alone System description given above.

#### Appendix A - Base Application and Standard Library Files

| # | Document Name |
| --- | --- |
| 1 | InTouch Baseload 2014.Zip and InTouch Baseload 2020.zip – Consultants are required to contact the SCADA group for the latest version |
| 2 | HMI Tag Templates.xlsx – standardized InTouch Tag configurations for common devices |
| 3 |  |
| 4 |  |