Regional Municipality of Halton

SCADA Standards Manual

Section 10 Ancillary Equipment and Programming

SCADA STANDARDS 2022

Table of Contents

SECTION 10 ANCILLARY EQUIPMENT AND PROGRAMMING	1

10.1	Intent of the Section	1

10.2	Programming Guidelines	1

10.3	Power Monitors	1

10.4	Rain Gauges	2

10.5	Pressure Relief Valves	3

10.6	Monitoring Wells	3

10.7	Stand-by Power	3

10.8	Security System Overview	4

Chubb Edwards Security	5

Door Contacts and Key Switches Security	6

Wastewater Treatment and Solid Waste Facilities	6

10.9	Auto Dialers and Alarm Management	7

Auto Dialer Alarm Summary	7

Auto Dialer Channels	8

Enabling and Disabling of Raw Alarms	9

Enabling and Disabling of auto dialer Alarms	9

Enabling/Disabling the Auto Dialer Channel	10

Enabling/Disabling the Auto Dialer	10

10.10	Auto dialer Verification System	10

10.11	Standard Auto Dialer Configuration Settings	11

Network Settings	11

Standard Auto dialer Channel 0 Configuration Parameters	12

Remote Channel Assignment	12

Existing Auto Dialer Channel Assignment	12

Append New Alarms to an Existing Channel	12

Re-use the Existing Channel	13

Add a New Channel	13

Adding a New Auto Dialer	14

10.12	Working Alone System – Wastewater	14

Sequence of Numbers	15

HMI Windows and Operation of System	15

Hours of Operation	15

Working Alone Warning	18

Working Alone Alarm	20

End of Shift	22

10.13	Auto Dialer Programming for the Working Alone System	22

Sample PLC Programming	22

10.14	Burlington Water Purification Plant Inactivity System	25

Burlington Water Plant Auto Dialer System	28

10.15	Burloak Water Purification Plant Inactivity System	32

Burloak Water Plant Auto Dialer System	35

10.10 Oakville Water Purification Plant Inactivity System	38

Oakville Water Plant Auto Dialer System	42

10.16	South Halton Water Plants Alarm Beacons and Audible Alarm Annunciation	44

Oakville Water Plant Critical Alarm Beacons and Audible Notifications	44

Burlington Water Plant Critical Alarm Beacons and Audible Notifications	44

Burloak Water Plant Critical Alarm Beacons and Audible Notifications	44

Table of Figures

Figure 10.2 – Working Alone Dialer Channel Assignment per Plant	15

Figure 10.3 – Working Alone Main Window	16

Figure 10.4 – Typical Verification Site Configuration	17

Figure 10.5 – Working Alone Enabled Window Script- On True	17

Figure 10.6 – Working Alone Enabled Window Script- While True	17

Figure 10.7 – Working Alone Enabled Window Script- On False	18

Figure 10.8 – Work Alone System Warning pop-up	18

Figure 10.9 – Working Alone Operator Warning Script- On True	19

Figure 10.10 – Working Alone Operator Warning Script- While True	19

Figure 10.11 – Working Alone Operator Warning Script- On False	20

Figure 10.12 – Working Alone Operator Warning Script- While False	20

Figure 10.13 – Work Alone System Alarm pop-up	20

Figure 10.14 – Working Alone Operator Alarm Script- While True	21

Figure 10.15 – Working Alone Operator Alarm Script- On False	21

Figure 10.16 - Working Alone Operator Alarm Script- While False	22

Figure 10.17 – Working Alone System Two-Hour Timer Sample PLC Code	22

Figure 10.18 – Working Alone System Five Minute Alarm Timer Sample PLC Code	23

Figure 10.19 – Working Alone System Alarm Time Remaining Sample PLC Code	24

Figure 10.20 - Burlington Water On-False Inactivity Script	25

Figure 10.21 – Burlington Water On-True Inactivity Script	26

Figure 10.22 – Burlington Water While False Inactivity Script	27

Figure 10.23 – Burlington Water While True Inactivity Script	28

Figure 10.24 – Burlington Water Auto Dialer Trigger Mapping	29

Figure 10.25 – Burlington Water Auto Dialer Enable Pop-up	30

Figure 10.26 – Burlington Water Auto Dialer Channel 1 Dial out Logic	30

Figure 10.27 – Burlington Water Auto Dialer Channel 2 Dial out Logic	31

Figure 10.28 – Burloak Water On False Inactivity Script	32

Figure 10.29 – Burloak Water On-True Inactivity Script	33

Figure 10.30 – Burloak Water While False Inactivity Script	34

Figure 10.31 – Burloak Water While True Inactivity Script	35

Figure 10.32 – Burloak Water auto dialer Trigger Mapping	36

Figure 10.33 – Burloak Water Auto Dialer Enable Pop-up	37

Figure 10.34 – Burloak Water auto dialer Channel 1 Dial out Logic	37

Figure 10.35 – Burloak Water Auto Dialer Channel 2 Dial out Logic	38

Figure 10.36 – Oakville Water On-False Inactivity Script	39

Figure 10.37 – Oakville Water On-True Inactivity Script	40

Figure 10.38 – Oakville Water While False Inactivity Script	41

Figure 10.39 – Oakville Water While True Inactivity Script	42

Figure 10.40 – Oakville Water Auto Dialer Enable Pop-up	43

Figure 10.41 – Oakville Water auto dialer Channel 1 Dial out Logic	43

Figure 10.42 – Oakville Water Auto Dialer Channel 2 Dial out Logic	44

Figure 10.43 – Oakville Water Auto Dialer Channel 3 Dial out Logic	44

# SECTION 10 ANCILLARY EQUIPMENT AND PROGRAMMING

## Intent of the Section

#### This intent of this section is to explain how to deploy, utilize and develop programming for equipment or systems that are ancillary to the core SCADA system and components.

#### This document contains guidelines on how to address the need to update or change parameters of existing equipment in the field and how to complete the design and programming for new equipment.

#### This section also includes drawings and specifications detailing the installation of specific equipment.

#### Should consultants identify a discrepancy between this section and other sections of the manual, they should notify Halton Region in writing.

## Programming Guidelines

#### The programming, configuration and maintenance of routers and network switches is performed by Technology Services.  Should consultants require these pieces of equipment adjusted, they should contact the Halton SCADA group.

#### The programming of VFD drives is performed by the Manufacturer, or an authorized representative, during the equipment startup.  During maintenance activates, should consultants require these parameters adjusted, they are required to notify Halton Region in writing. Consultants are required to arrange for qualified personnel to update the VFD parameters.

#### The programming and configuration of field instrumentation is performed by the contractor during startup.  During maintenance activates, should consultants require these parameters adjusted, they are required to notify Halton Region in writing.  Consultants are required to contact Maintenance staff to have the parameters updated and properly documented.

## Power Monitors

#### This section describes the operation of the Power Monitors. The Consultant shall review Section 10 – Ancillary Equipment / Power Monitors for more information on design.

#### A Power Monitor should be installed in each new MCC.

#### The PowerMonitor 5000 should be configured by the MCC Supplier

#### Power monitoring and associated PanelView display should be set-up and configured on the network by the consultant, not the contractor.

#### There must be one (1) power monitor configured to be displayed on a Panel View. The Consultant may choose to use more than 1 power monitor per Panel View if they all exist within the same room. A Panel View can support up to three (3) power monitors.

#### Consultant to set-up and configure PanelView with PowerMonitor 5000 application.

#### To understand how to program the HMI screen see Section 6 HMI Programming.

#### The Region uses Allen Bradley PowerMonitor 5000 units which includes a dedicated Allen Bradley PanelView Component (C400 PanelView) display unit. See the drawings in Section 10 for the appropriate model numbers.

#### Power Monitors data is to be polled by the HMI application through the DASABCIP I/O or OI. ABCIP (under System Platform) server.

#### Power Monitors shall be named utilizing conventions from the tag name convention designating the Site, Power Monitor Fragment and Number of Devices. (See Section 2 Tag Convention for more details)

## Rain Gauges

#### This section describes the use and implementation of the Rain Gauges. The Consultant shall review the drawing in Section 10 – Ancillary Equipment / Rain Gauges for more information on design.

#### Rain Gauges are monitored by SCADA in real-time and values are stored historically onto SCADA1 or SCADA2.

#### Rain Gauges shall utilize code from the Region’s standard PLC Baseload BXX1_V31.ACD

## Pressure Relief Valves

#### This section describes the monitoring of the Pressure Relief Valve(s).  The Consultant shall review the drawings in Section 10 – Ancillary Equipment/Pressure Relief Valve and Standard Operating Procedures for more information on design and configuration.

#### The Pressure Relief Valve(s) are not controlled by SCADA. SCADA is only used to monitor the flow through the valve(s), the pressure on either side of the valve(s) and any other parameter deemed necessary at the time of design.

## Monitoring Wells

#### For details on the design and installation of Monitoring Well, see the drawing in Section 10 - Ancillary Equipment/Monitoring Wells

## Stand-by Power

#### There are three main documents that have information related to the design and implementation of stand-by power by the Region. Those documents are;

##### Consultant Procedure Manual – Facilities

##### Water and Wastewater Facilities Design Manual

##### This SCADA Standards Manual

#### The consultant must comply with all these documents where relevant to the specific project. If there is contradictive information in these documents or the documents are unclear, the consultant is to contact the Regions project team for clarification.

#### This section describes how the Region applies SCADA to Stand-by Power Systems. Stand-by power system are made up of the following components:

##### An engine and control panel (fueled by diesel or natural gas)

##### A transfer scheme (either breakers or an automatic transfer switch)

##### Fuel storage tank and containment system

##### An electrical disconnect associated with the generator

##### A combustion louver

#### Stand-by power systems are not controlled by the facility PLC. They are controlled by the package equipment that is supplied as part of the stand-by power package equipment. For more information on the control scheme, see Section 12 of the Water and Wastewater Facilities Design Manual and the Type III IV WWPS Standard Control Narrative. (4 Pumps) in Section 8 of the SCADA Standards Manual.

#### The Region monitors the status of the stand-by power system using the facilities PLC and SCADA system.

#### Section 8 Wastewater Pumping Stations/Appendix 8C/ - Type III & IV Drawing Templates in these SCADA Standards contains a drawing called P904 Pump Station P and ID Normal Standby Power and several digital input and one digital output drawings. These drawings show which I/O points are to be wired to the SCADA system for all the components that are part of the stand-by power system. This drawing is to be used as a template for the design of any stand-by power systems.

#### Section 8, Wastewater Pumping Stations /Appendix 8A/Standard Control Narrative there is a document called Type III IV WWPS Standard Control Narrative (4 Pumps). This document contains a section on stand-by power systems. This section of the Control Narrative is to be used as a template for the design of any stand-by power systems.

## Security System Overview

#### Halton Region utilizes two types of security systems.  These are:

##### Chubb Edwards Security

##### Door Contacts and Key Switches

### Chubb Edwards Security

#### The Chubb Edwards Security system is used at all Water Treatment and Distribution facilities.

#### Consultants expanding or designing a Water Treatment or Distribution facility must use this system.  The following is a brief description of the Chubb Edwards Security system operation.  Contact Halton Region’s PM for details on the design of the Chubb Edwards Security system.

#### Each Facility has at minimum of one Chubb Edwards Security ACU.  The system contains a unit which controls the door, and a security keypad that is used to arm and disarm the door security.  The entry and exit times are controlled by the keypad.  The keypad sends status contacts to local PLC’s for SCADA to monitor.

#### When personnel wish to access a building door, they must have their key FOB scanned by the security system.  If the FOB is registered with the security system at the plant, the door will open.  The person must then access the keypad to disarm the security system.

#### Once the security system is disarmed, any additional personnel must have a registered FOB to open the building door.

#### All security ACU are connected back to a dedicated security workstation located in the control room of the main treatment plant.  If the system registers an illegal entry, the security workstation will issue an alarm.

#### The illegal entry must be acknowledged at the security workstation before the alarm will clear.

#### The PLC and HMI software programmer are not responsible for the programming of the Chubb Edwards security ACU.  The PLC and HMI software programmers are required to program SCADA software only to monitor the status contacts from the Chubb Edwards security ACU.  Information on programming requirements is presented in Sections 5 and 6.

### Door Contacts and Key Switches Security

#### This type of security is only used at wastewater pumping stations. Refer to Section 8 for details on this type of security system.

### Wastewater Treatment and Solid Waste Facilities

#### When consultants are designing or expanding a Wastewater Treatment or Solid Waste Facility, they should contact Halton Region through the use of a standards deviation memo for direction on the required building security system.

## Auto Dialers and Alarm Management

#### This section describes the operation of the plant auto dialer and the auto dialer channels.  Consultants will also need to refer to Sections 5 and 6 of the SCADA Standards for further information.

#### Section 5 details:

##### Raw Alarms Enablement and Disablement

##### Raw Alarm auto dialer Enablement and Disablement

#### Section 6 details:

##### Alarm Enable/Disable Control

### Auto Dialer Alarm Summary

#### There are 3 main components within the SCADA system that play a role in alarm management. They are the PLC, the InTouch application and the RACO Verbatim Gateway Alarm auto dialer. Each component has a different role in the determination, annunciation, communication, acknowledgement and resetting of alarms. Each PLC determines if there is an alarm within the process or area that it is responsible for.

#### The primary purpose of the PLC is to examine certain conditions as dictated by the programming and make the determination if an alarm exists.

#### The HMI has many purposes, which include the annunciation display and filtering of alarms and their states, controls to allow the operator to acknowledge alarms, determine if an alarm is critical or not and, controls to allow the operator to enable and disable Raw Alarms, auto dialer alarms and the auto dialer itself.

#### The auto dialer is the device that, when initiated by the PLCs, sends alarms out across the phone line to the operators.

#### The generation of an auto dialer alarm is done at the PLC level and not the HMI. This way, if the entire HMI layer was shutdown, the auto dialer alarms will still function and the operator is still notified.

#### The PLC that is responsible for determining the Raw Alarm is also responsible for determining whether the alarm is an auto dialer alarm or not, based on the operator selectable parameters. If it is an auto dialer Alarm, it is evaluated in the ACP program in either the “Alarms_Dialer_Waste” or “Alarms_Dialer_Water” routines.  The auto dialer PLC is generally located in or near the control room at the main Plant; some exception may apply.  It is responsible for reading every PLC in the system, to see if it has an auto dialer Alarm. If there is an auto dialer alarm present, then the appropriate channel on the auto dialer is activated. This channel remains activated until the alarm condition is cleared (not acknowledged but cleared) or the Raw or auto dialer Alarm is disabled though the HMI, or when available, at the PanelView.

#### If the Plant auto dialer PLC fails to communicate with any slave PLC, the communication Alarm timer starts. If the timer elapses, a PLC to PLC communication failure alarm is generated, notifying operations that they have a communications issue.

### Auto Dialer Channels

#### The auto dialer has a number of channels available depending on the model, with a maximum of 96 available channels. Auto dialer alarms are organized into the appropriate channels by first grouping them by location or site. Each individual site or location can have a single PLC or multiple PLCs.

#### Consultants working on existing PLCs are required to modify the existing channel logic.

#### Consultants adding a new PLC to an existing system will be required to contact Halton Region for direction on which Channel to use.

#### In Wastewater Systems, stations without PLCs generally have an associated auto dialer channel.  Consultants should notify Halton Region of this condition, so that the channel can be re-used with the new PLC.

#### As part of design investigation, consultants are required to investigate the auto dialer channels to determine, if there are available spares.  If spare channels are not available, consultants should notify Halton Region for direction on how to proceed.

#### If any channels are added or removed or if there are any changes made to the programing of the dialer itself then the consultant needs to request control of appropriate auto dialer programing document and update the document and return it to the Region.

### Enabling and Disabling of Raw Alarms

#### Within the InTouch application and using the PanelView operations have the ability to enable/disable every Raw Alarm. Although this enable/disable is done using the InTouch application or PanelView the operator is toggling a bit in the PLC code. Once disabled, this alarm will never be generated by the PLC even if the input to the PLC changes state, and therefore will never be annunciated by the InTouch application or PanelView, and will never generate an auto dialer Alarm (if it is one).

#### There are 2 main locations within the InTouch application for enabling and disabling alarms. The first is through the auto dialer Control Windows. This is a series of windows that allows the operator to enable/disable every Raw Alarm in the system. They are organized by PLC (Channel #) or process area.

#### The second location is the Advanced Pop-ups for various device types which are a part of the existing application. These are used to enable/disable standard virtual alarms for every device in the system, such as a HiHi or Fail to Start alarm. For analog devices, if one of these alarms is disabled, a yellow dot appears beside the analog display on the main process window.

#### All functionality described above is also included in the PanelView. The significant difference is that the PanelView’s functionality is specific to the PLC to which it is attached.

### Enabling and Disabling of auto dialer Alarms

#### Within the InTouch application an auto dialer Control window has been created to allow the operator to enable and disable each individual auto dialer Alarm. Although this enable and disable is done using the InTouch application, the operator is toggling a bit in the PLC code. Once disabled, an alarm will never be sent to the auto dialer and the operator will not be notified by the auto dialer.

#### Even with the auto dialer alarm disabled, the corresponding Raw Alarm can still be activated and it will be annunciated on the HMI and PanelView. The operator will still be able to acknowledge and reset the alarm through the HMI and PanelView.

#### Raw alarm enable/disable controls for advanced analog alarms that trigger the auto dialer are not displayed on the auto dialer control window.  Halton Region’s standard is that all advanced analog alarms which generate an auto dialer alarm are to be enabled and disabled using the advanced analog device control pop-up.  When the alarm is disabled it disables both the Raw and auto dialer alarm.

### Enabling/Disabling the Auto Dialer Channel

#### An auto dialer Channel can also be disabled though the SCADA system.  Although this enable and disabled is done using the InTouch application, the operator is toggling a bit in the PLC code.  Once the channel is disabled, the operator will never be notified by the auto dialer of an alarm on that Channel.

#### The PanelView cannot Enable/Disable the auto dialer Channel.  PanelViews are programmed to only poll their local PLC.  Enabling/Disabling of the auto dialer channel is performed in the auto dialer PLC, which does not have a PanelView.

### Enabling/Disabling the Auto Dialer

#### The auto dialer itself can be enabled and disabled. This prevents all auto dialer Alarms from going through to the auto dialer. This is done through the plant auto dialer Control window of the HMI, but the operator is toggling a bit in the PLC.

#### The PanelView cannot Enable/Disable the auto dialer.  PanelViews are programmed to only poll their local PLC.  Enabling/Disabling of the auto dialer is performed in the auto dialer PLC, which does not have a PanelView.

## Auto dialer Verification System

#### For information on how the Auto dialer verification system works, refer to the document called Auto Dialer Verification System Documentation which is kept on Asset Center in the folder called Auto Dialer Programming Document.

#### For information on how the wiring is done for the auto dialer verification system, see the Dialer Verification Wiring which is stored on Asset Center in the folder Auto Dialer Programming Documents\Wastewater Programming and Wiring Diagrams or Auto Dialer Programming Documents\Water Programming and Wiring Diagrams for the respective plant.

## Standard Auto Dialer Configuration Settings

#### The following section should be read in conjunction with the appropriate owner’s manual for the auto dialer being configured. These manuals are stored on Asset Center in the folder called Auto Dialer Programming Documents.

#### In general, consultants will not need to install a new auto dialer, but only program in additional channels or update existing channels.

#### Each auto dialer has its own individual documentation on how the specific auto dialer is programmed. Electronic copies of the documentation are stored in Asset Center in the directory called Auto Dialer Programming Documents/Wastewater Programming and Wiring Diagrams or Auto Dialer Programming Documents/Water Programming and Wiring Diagrams depending on which plant is being referenced. Hardcopies are also kept and posted at the respective plant. If the consultant is making any changes to the dialer that requires that this documentation be updated, then they are responsible to update the electronic version of the documentation AND to update the hardcopy at the facility.

#### The address range which the auto dialer polls, varies from auto dialer to auto dialer. This information can be found in the documentation as described above.

### Network Settings

#### Auto dialers can be configured to communicate on multiple networks.  Halton Region has standardized that Network 2 “NET 2”, is to be the network that is used.

### Standard Auto dialer Channel 0 Configuration Parameters

#### Halton Region has standardized its auto dialer communication configuration parameters.  Channel 0 must be set to the following:

##### DF1

##### 19,200 Baud Rate

##### 8 Data Bits

##### 1 Stop Bit

##### 0 Parity

### Remote Channel Assignment

#### The Raco Verbatim Gateway auto dialer has four on-board local channels and 96 remote channels.  Halton Region has standardized that the four on-board channels are left unused.

### Existing Auto Dialer Channel Assignment

#### If the auto dialer is existing, the Consultant will perform one of three tasks:

##### Append new alarms to an existing channel

##### Re-use an existing channel, or

##### Add a new channel

### Append New Alarms to an Existing Channel

#### Consultants are required to perform this task anytime they update an existing PLC with new alarm logic, and plant operations has determined that the new alarm should trigger the auto dialer.  The steps the consultant is required to take are:

##### Update the existing PLC auto dialer logic in local PLC logic to include the new alarm.

##### Confirm that the auto dialer PLC will poll the existing PLC for the new alarm bit.

##### Update the electronic and hardcopies of the auto dialer configuration documentation, if required.

### Re-use the Existing Channel

#### When consultants are installing a new PLC at an existing Wastewater Pumping Station, the pump station   will already have a channel assigned.

#### Occasionally, a new PLC will be added to an existing process area.  Operations or the SCADA group may prefer to tie the new PLC to the existing auto dialer channel associated to the process area.

#### The steps the consultant is required to take in either case are:

##### Confirm with the Region’s SCADA group and operations staff how the alarms from the new PLC will be managed with regards to the existing auto dialer.

##### Update the plant auto dialer PLC to poll the auto dialer alarm from the new PLC.

##### Ensure that the new auto dialer alarm bit from the new PLC is appended to the existing auto dialer channel logic.

##### Check the alarm and normal message for the channel to ensure that the auto dialer is clearly annunciating all alarms on the channel.  Consultants may need to update the message, depending on the channel operations has selected.

##### Update the electronic and hardcopies of the auto dialer configuration documentation, if required.

### Add a New Channel

#### When consultants add a new PLC to a plant or at a station, there may not be an auto dialer channel assigned for the new location.  Prior to adding a new channel, the consultant should check with operational staff to determine if a new channel is required. The steps the consultant is required to take are:

##### Determine with operations and the SCADA group which available channel to use.  Typically this would be the next available channel unless there was some strong compelling reason to not use the next available channel.

##### Update the plant auto dialer PLC to poll the auto dialer alarm from the new PLC.

##### Program the auto dialer to poll the new alarm bit on the channel.

##### Program the alarm and normal message for the new channel on the auto dialer.

##### Update the auto dialer programming information that is located at the plant.  Halton Region has an electronic copy that the consultant can update.

##### Ensure the new channel is integrated into the auto dialer verification system.

### Adding a New Auto Dialer

#### Consultants should not normally need to add a new auto dialer as part of their project activities. Consultants should contact Halton Region for direction on how to program the new auto dialer and associated PLC.

#### Prior to programming the auto dialer Channels, the consultant is required to have a meeting with the SCADA group and plant operations to organize the channel assignments. After the meeting, all the agreed to changes and configuration should be documented in the.

#### Once Halton Region has provided direction to the consultant on how the auto dialer is to be programmed, the consultant is required to create a new Process Control Narrative created for the new auto dialer and its associated PLC auto dialer and a programming information sheet for the auto dialer.  Halton Region will provide the consultant with a template for their use.

## Working Alone System – Wastewater

#### The following Section describes the operation of the auto dialer for the Working Alone system. For additional information about HMI windows and PLC logic refer to Section 6, 6.1 ‘Working Alone System - Waste Water’.

#### The working alone system is used at all Wastewater plants within Halton. The system is comprised of HMI windows and PLC logic to ensure the protection of workers who are performing their duties, in areas or under conditions, where they are required to work alone.

#### The working alone system will be enabled/disabled by the worker at the start and end of their shift. The system will require acknowledgement, via a pop-up window on the HMI window(s), during the workers shift.

#### A missed acknowledgement will cause a dialer alarm and start the dialer to call a series of pre-programmed phone numbers. Refer to table 10.2 for channel assignment.

### Sequence of Numbers

#### The auto dialer sequence will call to the plant pager, if that is not acknowledged within 2 minutes an alarm will be sent to the following sequence of numbers with a 2-minute pause between each call; Plant cell phone, Plant Supervisor cell phone, and Stand by Supervisor pager. The plant/standby supervisor will attempt to contact the operator. If no response, emergency procedures will be implemented.

Figure 10.2 – Working Alone Dialer Channel Assignment per Plant

| WORKING ALONE DIALER CHANNEL ASSIGNMENT PER PLANT |  |
| --- | --- |
| Plant | Dialer Channel |
| South West WWTP | 6 |
| Acton WWTP | 7 |
| Mid-Halton WWTP | 7 |
| South East WWTP | 25 |
| Milton WWTP | 21 |
| Georgetown WWTP | 3 |
| Skyway WWTP | 5 |

#### The Work Alone System has a dedicated dialer channel and group of phone numbers assigned - the group of numbers is based on the Default Dialer Call List as shown on the Working Alone ‘Operator Notification’ window.

## HMI Windows and Operation of System

### Hours of Operation

Saturday, Sunday, Statutory, Declared Holidays (7.30 am to 11.30 am) and after regular working hours (4:00 pm to 7:30am)

#### A sample window is attached below. Each plant will have different phone numbers but the operation is the same. Refer to Figure 10.3

Figure 10.3 – Working Alone Main Window

#### The SCADA system at the plant will be used as an “Auto Attendant”. Plant operator must enable the system at the start of his/her shift. This is done by clicking on the Green <DISABLED> button.

#### Once clicked the button will change to Red, the text will change to ENABLED and the  Condition Script in Fugure 3 will run and open the Work Alone System Enabled window (Refer to Figure 10.5)

Figure 10.4 – Typical Verification Site Configuration

Figure 10.5 – Working Alone Enabled Window Script- On True

#### If this window is CLOSED a condition script will open the window in 60 seconds  Refer to Figure 10.6 for the condition script. script. (note tag shown is for the SouthWest plant): The HMI scripts for this window is shown below.

Figure 10.6 – Working Alone Enabled Window Script- While True

#### The script shown in Figure 10.7 closes the window  “Work Alone System Enabled” when the Work Alne System is Disabled.

Figure 10.7 – Working Alone Enabled Window Script- On False

#### The Notify Timer Duration will show 120 Mins and update the time left before the system will go into alarm. The operator must click the  <Reset Timer> button to reset the timer  and to prevent a Working Alone alarm. When the  <Reset Timer> is clicked, all timers are reset and the dialer alarm is cleared if active.

### Working Alone Warning

#### The SCADA system is pre programmed at two (2) hour countdown timer (within the PLC code). Should the countdown timer expire,  (no acknowlegment by operator) this will generate a pop-up reminder prompt- Refer to Figure 10.8 below.

Figure 10.8 – Work Alone System Warning pop-up

#### This will give a visual reminder to the operator that they need to acknowledge the system promptly. Once this window is active the <Alarm Time Delay> timer starts. This allows an additional five (5) minutes for the operator to acknowledge the Working Alone System before triggering the dialer alarm.

#### The HMI condituion scripts for this window is shown below (note tag shown is for the South West plant):

Figure 10.9 – Working Alone Operator Warning Script- On True

#### The condition script in figure 10.10 opens the window every 60 seconds while the Alarm Time Delay timer is counting down.

Figure 10.10 – Working Alone Operator Warning Script- While True

#### The condition script in figure 10.11 will close the window Operator Warning if the Alarm Time Delay timer is reset.

Figure 10.11 – Working Alone Operator Warning Script- On False

#### The condition script in figure 10.12 will close the window Operator Warning every 30 seconds while the Alarm Time Delay timer is not counting down.

Figure 10.12 – Working Alone Operator Warning Script- While False

### Working Alone Alarm

#### Should the two (2) hour countdown timer and the five (5) min Alarm Time Delay timer expire, then the OPERATOR DOWN ALARM window will appear- Figure 10.13.

Figure 10.13 – Work Alone System Alarm pop-up

#### At this point, the alarm dialer channel will activate and begin to call the series of pre-programmed phone numbers as shown in the Default Dialer Call List on the winodow Operator Notification (see Figure 10.3).

#### Resetting the alarm is a two-step process. It must first be cleared on the plant HMI, Operator Notification window by clicking the <Reset Timer> button. Then the alarm can be cleared from the dialer by calling the dialer and pressing 9 or locally at the auto dialer interface which is the same way all alarms are cleared.

#### The script shown in figure 10.14 opens the window Operator Notification every 60 seconds while the Alarm Time Delay timer is done.This is in case the window becomes closed while the Alarm Time Delay timer is done.

Figure 10.14 – Working Alone Operator Alarm Script- While True

#### The script shown in figure 10.15 closes the window Operator Notification when the Alarm Time Delay timer is reset.

Figure 10.15 – Working Alone Operator Alarm Script- On False

#### The script shown in figure 16 closes the window Operator Notification every 30 seconds while the Alarm Time Delay timer is not done.This is in case the window becomes opened while the Alarm Time Delay timer is not done.

Figure 10.16 - Working Alone Operator Alarm Script- While False

### End of Shift

#### At the end of shift the operator will have to disable the system by clicking the Red <Enabled> button. If this is forgotten the system will go into alarm and the dialer will activate according to the Working Alone System description given above.

## Auto Dialer Programming for the Working Alone System

#### The auto dialer requires special programming for the Working Alone system and general plant alarming. Each plant has a programming sheet that can be accessed from Asset Center in the folder auto dialer Programming Documents. The Working Alone system has a dedicated channel and uses a group of phone numbers that is different from the other dialer alarms.

### Sample PLC Programming

#### This code is from PLC SWY1 at the South West WWTP:

#### Enable the Working Alone System and star the two-hour timer:

Figure 10.17 – Working Alone System Two-Hour Timer Sample PLC Code

#### When the two-hour timer is done, the five minute warning timer starts and the Operator Warning window is opened on the HMI. When the five minute timer is done, the Operator Alarm window is opened.

Figure 10.18 – Working Alone System Five Minute Alarm Timer Sample PLC Code

#### Calculate the remaining time left before operator acknowledgement and five (5) minute timer:

Figure 10.19 – Working Alone System Alarm Time Remaining Sample PLC Code

## Burlington Water Purification Plant Inactivity System

#### The inactivity timeout at the Burlington Water Plant is programmed to ensure the secure operation of the HMI app and security of those at the Plant.

#### The inactivity timeout system is always active from the moment the HMI application is active in runtime.

#### The Inactivity system is programmed using the Wonderware system variables “$InactivityTimeout” that triggers once the app detects no activity on the SCADA workstation, and “$Operator” string that set to “None” when an operator is logged off automatically or manually.

#### Figure 10.20 demonstrates the On False Inactivity script for Burlington Water Plant. As shown below, once an operator logs in or the Inactivity Timeout is set to false, the script sets the “No Activity Alarm” to false for the individual workstations where the app is deployed.

Figure 10.20 - Burlington Water On-False Inactivity Script

#### Figure 10.21 demonstrates the On True Condition of the Inactivity script. In an event, if either ‘$InactivityTimeout” is set to true or “$Operator” is set to “None”, the On True script will be executed and will set the “No Activity Alarm” for the Workstation that the script is true for.

Figure 10.21 – Burlington Water On-True Inactivity Script

#### Figure 10.22, demonstrates the While False condition of the Inactivity Script. It is set to execute every 30 seconds while the “$InactivityTimeout” or “$Operator = “None” is False. Its purpose is to monitor/set the “No Activity Alarm” for the applicable workstation to false.

Figure 10.22 – Burlington Water While False Inactivity Script

#### Figure 10.23 demonstrates the While True Condition of the Inactivity script. It functions similar to the While False script, except its purpose is to set “No Activity Alarm” true for the applicable workstation every 30 seconds.

Figure 10.23 – Burlington Water While True Inactivity Script

### Burlington Water Plant Auto Dialer System

#### The SCADA control for the auto dialer at the Burlington Water Plant is comprised of a main auto dialer System Enable/Disable for the entire Plant. The auto dialer communicates with the Dialer PLC through a serial connection, hence it needs to be programmed to read the desired Dialer Alarm bits separately.

#### The auto dialer programming for the Burlington Water Plant is in a ControlLogix PLC. The Dialer Alarm triggering bits are mapped under “PLC 2, 5 / SLC Mapping” to be read by the Dialer over the serial connection, as shown in the figure below.

Figure 10.24 – Burlington Water Auto Dialer Trigger Mapping

#### The auto dialer Control screen, as shown in the figure below, allows access to Enable/Disable the dialer or individual channels.

Figure 10.25 – Burlington Water Auto Dialer Enable Pop-up

#### The “Burlington auto dialer Enable/Disable” must be toggled to “Enable” for any alarm to dial out.

#### Channel 1 – “Critical Alarm Dial out Enable”, if enabled, monitors a bit that is set by the HMI. This will cause a dial out if any critical alarm is seen as active for more than 15 minutes, and the status of the Operator Notification system is active, as shown in the figure below.

Figure 10.26 – Burlington Water Auto Dialer Channel 1 Dial out Logic

#### Channel 2 – “Workstation No Activity Dial Out Enable”, when Enabled, is programmed to Dial out if all thin clients at the plant have been recognized as either “Inactive” or have a heartbeat alarm active for longer than 35 minutes and the Operator Notification System Active is true, as shown in the figure below.

Figure 10.27 – Burlington Water Auto Dialer Channel 2 Dial out Logic

## Burloak Water Purification Plant Inactivity System

#### The inactivity timeout at the Burloak Water Plant is programmed to insure the secure operation of the HMI app and security of those at the Plant.

#### The inactivity timeout system is always active from the moment the HMI application is active in runtime.

#### The Inactivity system is programmed using the Wonderware system variables “$InactivityTimeout” that triggers once the app detects no activity on the SCADA workstation, and “$Operator” string that set to “None” when an operator is logged off automatically or manually.

#### Figure 10.28 demonstrates the On False Inactivity script for Burloak Water Plant. As shown below, once an operator logs in or the Inactivity Timeout is set to false, the script sets the “No Activity Alarm” to false for the individual workstations where the app is deployed.

Figure 10.28 – Burloak Water On False Inactivity Script

#### Figure 10.29 demonstrates the On True Condition of the Inactivity script. In an event, if either ‘$InactivityTimeout” is set to true or “$Operator” is set to “None”, the On True script will be executed and will set the “No Activity Alarm” for the Workstation that the script is true for. In addition, it will also navigate to the Overview Screen of the app for some workstations.

Figure 10.29 – Burloak Water On-True Inactivity Script

#### Figure 10.30 demonstrates the While False condition of the Inactivity Script. It is set to execute every 18 seconds while the “$InactivityTimout” or “$Operator = None” is False. Its purpose is to monitor/set the “No Activity Alarm” for the applicable workstation to false.

Figure 10.30 – Burloak Water While False Inactivity Script

#### Figure 10.31 demonstrates the While True Condition of the Inactivity script. It functions similar to the While False script except, its purpose is to set “No Activity Alarm” true for the applicable workstation every 18 seconds. Also like in the “On True” script, when executed this script with navigate the app to the Overview screen every 18 seconds while the condition is active.

Figure 10.31 – Burloak Water While True Inactivity Script

### Burloak Water Plant Auto Dialer System

#### The SCADA control for the auto dialers at the Burloak Water Plant is comprised of a main auto dialer System Enable/Disable for the entire Plant. The auto dialer communicates with the Dialer PLC through a serial connection, hence it needs to be programmed to read the desired Dialer Alarm bits separately.

#### The auto dialer programming for the Burloak Water Plant is in a ControlLogix PLC. The Dialer Alarm triggering bits are mapped under “PLC 2, 3, 5 / SLC Mapping” to be read by the Dialer over the serial connection, as shown in the figure below.

Figure 10.32 – Burloak Water auto dialer Trigger Mapping

#### The auto dialer Control screen, as shown in the figure below, allows access to Enable/Disable the dialer or individual channels.

Figure 10.33 – Burloak Water Auto Dialer Enable Pop-up

#### The “Burloak auto dialer Enable/Disabled” must be toggled to “On” for any alarm to dial out.

#### Channel 1 – “Critical Alarm Dial Out Enable”, if enabled, will dial out if either the critical alarm bit is set by the HMI, a heartbeat communication alarm, related to any other PLC controllers on the network, or the “Server BLXCPU01A For Both Server Down Heartbeat Alarm” is true, for more than 15 minutes, and the Operator Notification system is true, as shown in figure below.

Figure 10.34 – Burloak Water auto dialer Channel 1 Dial out Logic

#### Channel 2 – “Workstation No Activity Dial Out Enable”, when Enabled, is programmed to Dial out if all thin clients at the plant have been recognized as either “Inactive” or have a heartbeat alarm active for longer than 25 minutes and the status of the Operator Notification system is active, as shown in the figure below.

Figure 10.35 – Burloak Water Auto Dialer Channel 2 Dial out Logic

## 10.10 Oakville Water Purification Plant Inactivity System

#### The inactivity timeout at the Oakville Water Plant is programmed to ensure the secure operation of the HMI app and security of those at the Plant.

#### The inactivity timeout system is always active from the moment the HMI application is active in runtime.

#### The Inactivity system is programmed using the Wonderware system variables “$InactivityTimeout” that triggers once the app detects no activity on the SCADA workstation, and “$Operator” string that set to “None” when an operator is logged off automatically or manually.

#### Figure 10.36 demonstrates the On False Inactivity script for Oakville Water Plant. As shown below, once an operator logs in or the Inactivity Timeout is set to false, the script sets the “No Activity Alarm” to false for the individual workstations where the app is deployed.

Figure 10.36 – Oakville Water On-False Inactivity Script

#### Figure 10.37 demonstrates the On True Condition of the Inactivity script. In an event, if either ‘$InactivityTimeout” is set to true or “$Operator” is set to “None”, the On True script will be executed and will set the “No Activity Alarm” for the Workstation that the script is true for. In addition, it will also navigate to the Overview Screen of the app for workstations.

Figure 10.37 – Oakville Water On-True Inactivity Script

#### Figure 10.38 demonstrates the While False condition of the Inactivity Script. It is set to execute every 30 seconds while the “$InactivityTimout” or “$Operator = None” is False. Its purpose is to monitor/set the “No Activity Alarm” for the applicable workstation to false.

Figure 10.38 – Oakville Water While False Inactivity Script

#### Figure 10.39 demonstrates the While True Condition of the Inactivity script. It functions similar to the While False script except, its purpose is to set “No Activity Alarm” true for the applicable workstation every 90 seconds.

Figure 10.39 – Oakville Water While True Inactivity Script

### Oakville Water Plant Auto Dialer System

#### The SCADA control for the auto dialer at the Oakville Plant is comprised of a main auto dialer System enable/disable for the entire Plant. The auto dialer communicates with the Dialer PLC through a serial connection, hence it needs to be programmed to read the desired Dialer Alarm bits separately.

#### The auto dialer Control screen, as shown in the figure below, allows access to Enable/Disable the dialer or individual channels.

Figure 10.40 – Oakville Water Auto Dialer Enable Pop-up

#### The “Oakville auto dialer Enable/Disabled” must be toggled to “On” for any alarm to dial out.

#### Channel 1 – “Critical Alarm Dial Out Enable”, if enabled, monitors a bit that is set by the HMI if any critical alarm are seen as active for more than 15 minutes, and the “Operator Notification System Active” is set to true, as shown in the figure below.

Figure 10.41 – Oakville Water auto dialer Channel 1 Dial out Logic

#### Channel 2 – “Workstation No Activity Dial Out Enable”, when Enabled, is programmed to Dial out if all thin clients at the plant have been recognized as “Inactive” for longer than 10 minutes, and the “Operator Notification System Active” bit is true, as shown in the figure below.

Figure 10.42 – Oakville Water Auto Dialer Channel 2 Dial out Logic

#### Channel 3 – “Plant Communication Alarm Dial Out Enable”, is programmed to dial out in case loss of communication is detected between the Dialer PLC, and any other PLC in the Plant, as well as, both SCADA Servers.

Figure 10.43 – Oakville Water Auto Dialer Channel 3 Dial out Logic

## South Halton Water Plants Alarm Beacons and Audible Alarm Annunciation

#### The South Halton Water plants are the Burlington Water Plant, the Oakville Water Plant and the Burloak Water Plant. Each of these plants can have periods of time where the operator(s) are not at a SCADA control station for extended periods of time. As such, there is a system in place that notifies the operator both visually and through audible means when required. The systems at each plant are similar but not exactly the same. Each system is described below.

### Oakville Water Plant Critical Alarm Beacons and Audible Notifications

#### This section is still to be developed.

### Burlington Water Plant Critical Alarm Beacons and Audible Notifications

#### This section is still to be developed.

### Burloak Water Plant Critical Alarm Beacons and Audible Notifications

#### This section is still to be developed.