Regional Municipality of Halton

SCADA Standards Manual

Section 3 Control Panel Design

SCADASCADA STANDARDS 2022

Table of Contents

SECTION 3 CONTROL PANEL DESIGN	2

3.1	Intent of the Section	2

3.2	Design Guidelines	2

3.3	Standard Drawings	2

3.4	Design Standards	2

Overall Design Standard Guidelines	2

Control Panel Retrofits/Upgraded Panels	4

Control Panels within MCC's	4

Control Panel Sizing	4

3.5	PLC Panel Layout Guidelines	5

Overall Spare Slot Requirements	6

Overall Spare I/O Requirements	7

I/O Card Layout Requirements	8

Strategic Spare Slot Placement	8

Strategic Field Terminal Block Placement	8

Terminal Block Group Labeling	9

Loop Wire Labeling	9

3.6	Tender Specifications	12

Table of Tables

Table 3.1	Control Panel Sizing	5

Table 3.2	Spare Slot Requirements	7

Table 3.3	8   Point Card Spare I/O Requirements	7

Table 3.4	16   Point Card Spare I/O Requirements	7

Table 3.5	Strategic Spare Slot Placement	8

Table 3.6	Wire Label Fragments	10

Table 3.7	Wire Label Examples	11

Table 3.8	Conductor Colour Guide	12

# CONTROL PANEL DESIGN

## Intent of the Section

#### The intent of this section is to identify the SCADA requirements of control panels.  This section must be read in conjunction with the Water, Wastewater and Solid Waste Facilities Design Manual.

#### This section should also be read in conjunction with the other sections of the SCADA Standards Manual.

## Design Guidelines

#### The overall goal of these SCADA standards is to standardize control panels in order to minimize the cost and scope of ongoing operations and maintenance.

#### These design standards also apply to prepackaged panels and the Consultant must ensure that the same standards are enforced.

## Standard Drawings

#### Standard control panel layout and power distribution drawings for panels are contained in the SCADA Standards, Section 1 Appendix 1B. The user should also refer to these drawings when reading this Section.

#### Specific to Wastewater Pumping Stations, standard control panel layout and power distribution drawings are contained in the SCADA Standards, Section 8.

#### The standard loop drawings for the Compact Logix, Control Logix, and SLC’s are also contained in Section 1, Appendix 1B.

#### The wiring diagram drawings have the functionality to dynamically update the rack number & slot number inside the drawings. The rack number & slot number can be assigned from the pull down menu at the top by selecting Rack # / Slot #. The following need to be manually updated, shown below as clouded:

##### Terminal block numbers and fuse sizing,

##### Rack # at the bottom of drawing

##### Circuit breaker number

## Design Standards

### Overall Design Standard Guidelines

#### The use of Master PLC’s should be avoided.  Every PLC should be capable of operating without depending upon another.

#### Halton Region does not use redundant controller configurations.

#### To minimize common points of failure, PLCs should be designed for process areas.  Remote I/O racks should be used where extra cards are needed in a process area to accommodate all I/O points but not to control multiple processes.

#### Prior to designing a new PLC system or remote I/O panel, consultants must check if an existing PLC is already in the process area.  If a PLC exists and there is available free memory in the processor, new instrumentation and controls should be tied into the existing PLC when possible.

#### As a minimum all PLC panels and remote I/O Panels should contain the following.

##### Network ports are required to be mounted outside on the front door of all control panels. The ports need to have an RJ 45 port to communicate with the PLC.

##### Provide a 120 V power receptacle to connect the Laptop.  This power is not backed up by the panel UPS.  The laptop shelf is required to be hinged at the top, fold up, and the shelf height is 40” from the finished floor.  The network port, 120 VAC receptacle and laptop shelf shall be located on the outside of the panel, mounted on the door.

##### A metal document pocket shall be mounted within the enclosure, minimum 300 mm wide.

#### All panels shall be equipped with internal fluorescent or LED lamps and door switch, and 120 VAC convenience power duplex receptacles.

#### The control panel (or remote I/O panel) shall have a dedicated incoming power simplex receptacle to power the UPS.  Refer to the wiring diagram.  The UPS shall be installed and connected to the control panel in a manner that allows maintenance to bypass the UPS without the need for ladders or other special tools. The UPS is to be plugged into dedicated simplex receptacle. The panel power cable going to the UPS is to be plugged into the UPS using a male plug. Therefore, if the UPS fails, this same plug could be removed from the UPS and plugged directly into the receptacle that normally feeds the UPS. The length of cables and locations of the receptacles to be such that the UPS can easily be bypassed.

#### The control panel chassis shall be powered by UPS.  The discrete inputs shall be powered by UPS.  All field instruments and network equipment shall be powered by UPS.

#### All receptacles that are powered from the UPS shall be Orange in colour and have a label saying “Powered by UPS”.

#### All receptacles that are convenience utility power shall be White or Ivory in colour.

#### Dedicated UPS feed receptacles should be brown or beige simplex receptacles.  Where a network communication device is installed in a panel, allow for one receptacle for each network communication device.

#### Wastewater pumping stations and other outlying facilities are required to have shelves for the network router and any additional equipment.  Equipment is not to be stacked.  Multiple shelves are acceptable.

#### Any equipment installed in a PLC panel that cannot be mounted on the back plate is required to be placed on a shelf.

#### All panel-mounted equipment shall be complete with an engraved legend on black lamacoid nameplate having white letters no smaller than 6 mm.  The panel shall have an engraved identification nameplate having letters no smaller than 12 mm. All lamacoids shall be fixed to the panel, not the field device.

#### All equipment and assemblies of equipment shall be CSA approved. Permanently attached CSA labels shall be attached to each assembly and all equipment supplied.

#### The control panel shall be designed to be accessed without the need for Arc Flash training or equipment.

#### Internal panel wiring shall conform to Halton Region standards.  Refer to Water, Wastewater and Solid Waste Facilities design manual for details.

#### PLC hardware selection tables for ControlLogix, CompactLogix and SLC’s are presented in Section 5.

#### In applications where new I/O modules are being added to an existing PLC panel, the preference is that consultants specify the same type of I/O modules that are currently installed within the PLC panel.

#### In applications where a new remote I/O panel is being connected to an existing PLC panel, all modules specified must be chosen from the selection tables presented in Section 5.

#### Halton Region uses 4 – 20 mA for all analog inputs and outputs.

#### All spare I/O points must be wired to terminal blocks or spare interposing relays.

#### I/O Terminal Blocks shall be grouped per card.

#### I/O Terminal Block groups shall be organized within the panel so that similar inputs are grouped together.

#### I/O Terminal block groups shall be organized in logical sequential order. The order shall be Digital Inputs, Digital Outputs, Analog Inputs, and Analog Outputs.

#### Spare I/O terminal blocks shall be strategically added and clearly marked spare.

#### When discrete I/O requires the use of a non-standard card due to voltage requirements, if less than eight points are required, the use of interposing relays is preferred rather than the installing a non-standard card.

#### All I/O for a process device should be terminated in a single device level ring and within a single panel. The separation of device I/O between two panels causes confusion for maintenance and troubleshooting.  Device I/O can be spread across multiple racks within the same PLC panel but cannot be spread between two panels even if one panel is a remote I/O panel in the same ring.

#### Discrete alarm inputs, such as flood alarms, that cause equipment to abort operation should be connected to the same PLC that controls the equipment.

#### All analog loops shall contain as a minimum one “Knife” style terminal block to allow for testing without the need to remove wires.

#### Spare field wires shall be minimized and labeled clearly at both ends and at any point where the wire breaks.  When spare field wires have been installed, they should be landed on terminal blocks within the panel and clearly marked as spare.

#### Installation of PLC panels in areas where more than 120 VAC is accessible will not be accepted.  This includes Vendor packaged equipment.  In cases where Vendor Packages panels do not accommodate this requirement, a separate panel for the PLC must be provided.

### Control Panel Retrofits/Upgraded Panels

#### Control panels should not be overfilled with I/O. The preferred method is to install a new remote I/O panel with a separate remote I/O rack.

#### All retrofit or upgraded panels must meet the minimum spare I/O requirements as stated in other sections.

#### Any existing control panel which is being retrofitted with a new PLC should meet as many of the above listed guidelines as possible.  As a minimum:

##### A network port shall be installed on the front of the door.

##### A 120 VAC power receptacle to connect a laptop (this power is not backed up by the panel) UPS

##### Fold up type Laptop shelf

##### UPS must be provided.

#### When a new PLC is being installed in an existing control panel, it is Halton Region’s preference to replace the entire PLC panel back plate with a new fully wired back plate rather than only changing the PLC.

#### As part of the pre-design process, consultants are required to perform a full field I/O check on all points.  Refer to the Consultants Procedure Manual for details.

#### Never install any power above 120VAC within a control panel.

### Control Panels within MCC's

#### Consultants should avoid installing control panels in MCC sections.  When this is not possible, the preferred method is to design a separate control panel of similar depth that sits directly beside the MCC.  MCC sections do not typically provide enough width to adequately meet the design requirements.

### Control Panel Sizing

#### The following table presents the minimum panel sizing requirements. The rack column represents the number of slots in the ControlLogix chassis.

| Modules* | Rack 1 | Rack 2 | Rack 3 | Rack 4 | Minimum Panel Size (H x W x D) | Number of Doors |
| --- | --- | --- | --- | --- | --- | --- |
| 0-4 | 7 | 0 | 0 | 0 | 1830mm×915mm×610mm (72.06” ×36.06” ×24.06”) | 1 |
| 5-7 | 10 | 0 | 0 | 0 | 1524mm×915mm×610mm (72.06” ×36.06” ×24.06”) | 1 |
| 8-10 | 13 | 0 | 0 | 0 | 1524mm×915mm×610mm (72.06” ×36.06” ×24.06”) | 1 |
| 11-14 | 17 | 0 | 0 | 0 | 1830mm×1220mm×610mm (72.06” ×48.06” ×24.06”) | 2 |
| 15-29 | 17 | 17 | 0 | 0 | 2000mm×1800mm×600mm (78.74” ×70.78” ×23.62”) | 2 |
| 30-44 | 17 | 17 | 17 | 0 | 2184mm×2845mm×508mm (86.12” ×112.00” ×20.12”) | 3 |
| 45-61 | 17 | 17 | 17 | 17 | 2184mm×3785mm×508mm (86.02” ×149.12” ×20.12”) | 3 |

- Control Panel Sizing

*Modules includes the processor, communication cards and all I/O cards

#### When panels with a height of 2184mm (86”) are used, no components are to be installed higher than 1830mm (72”) from the floor

#### The final panel size depends upon:

##### The internal panel components

##### The quantity of each type of I/O

##### The physical location of the panel

#### Consultants should use this table as a guideline; the final panel size is determined by the Consultant.

#### All new panels are required to be a minimum of 508 mm (20”) deep so that the UPS can be installed in the bottom of the panel.  The UPS should not block any terminal blocks while installed within the panel.

#### When a panel is intended to house I/O that will be installed as part of a future phase, expansion, the Consultant must design and specify that the panel is supplied will all future I/O modules, terminal blocks, etc.  This ensures that when the next phase of expansion occurs, the future field I/O only has to be landed on the existing terminal blocks.  It avoids field panel retrofits and on-site Panel FATs.

#### Consultants must not size panels with field terminal blocks mounted on the sidewalls.  The panel should be sized large enough to mount all field terminal blocks on the main backplane.

#### When specifying a panel size, the Consultant is required to confirm that the panel size is listed in more than one vendor’s product catalog.  Halton Region does not approve of Custom sized panels.

## PLC Panel Layout Guidelines

#### The Spare Slots in the PLC racks are to be spread out in a strategic manner that allows for the addition of communications and I/O cards while maintaining the preferred order of the cards. Where the number of spare slots allows, there should be one spare slot between the communication card and the first I/O card and before and after each type of I/O cards. If the number of spare slots does not allow, then as a minimum, the layout listed below must be followed. It is recommended that the Consultant discuss this layout with Halton before the control panel and loop drawings are developed and submitted for review.

#### The consultant must organize all processors, communications cards, and I/O cards in a ControlLogix rack in the following order (left to right):

##### PLC Processor(s)

##### Ethernet IP Modules

##### Other / Third Party Communications Modules

##### Spare Slot(s) (the number of spare slots depends on the total number of spare slots in the panel)

##### Digital Input Modules

##### Spare Slot(s) (the number of spare slots depends on the total number of spare slots in the panel)

##### Digital Output Modules

##### Analog Input Modules

##### Spare Slot(s) (the number of spare slots depends on the total number of spares in the panel)

##### Analog Output Modules

#### Halton Region does not allow the installation of CompactLogix for new installations. This section is only to be used for retrofits of existing CompactLogix installations.

#### The CompactLogix platform PLC processors and I/O cards are din-rail mounted, and snap together into a contiguous row of modules. The consultant must be aware of the power supply distance rating on all I/O modules and PLC processors. Specify, and position power supply module(s) as required. All CompactLogix racks must be mounted horizontally in the Instrument Control Panel.  The consultant must organize all processors, and I/O cards in the following order (left to right):

##### PLC Processor(s)

##### Digital Input Modules

##### Digital Output Modules

##### Analog Input Modules

##### Analog Output Modules

### Overall Spare Slot Requirements

#### The following table demonstrates the required number of spare slots based upon total number of slots available.

| Minimum Number of Slots Required | Maximum Number of Slots Required | Minimum Spare Slots Required | Total Slots Required |
| --- | --- | --- | --- |
| 0 | 4 | 3 | 7 |
| 5 | 7 | 3 | 10 |
| 8 | 10 | 3 | 13 |
| 11 | 14 | 3 | 17 |
| 15 | 29 | 5 | 34 |
| 30 | 44 | 7 | 51 |
| 45 | 61 | 7 | 68 |

- Spare Slot Requirements

#### Halton Region has specific requirements on the placement of spare slots.  Slot placement is discussed further down in, “Strategic Spare Slot Placement.”

#### All spare slots must be filled with Slot Filler cards.

#### The consultant must obtain approval from Halton Region when specifying less than the required number of spare slots, particularly when the strict observance of the spare count marginally adds another remote rack (for example a card count with spares that equals 18 slots).

### Overall Spare I/O Requirements

#### The following tables demonstrate the required number of spare I/O points based upon the number of I/O points per card. To use the following tables, the consultant must first determine the number of required I/O modules.  Next the consultant must reference the following tables based upon the quantity and type of each card to confirm that the total number of spare points are available for each type of card.  As an example if the consultant requires two 16 Point input cards and one 16-point output card, then the consultant must consult the table of both the input and output cards.

| 8 Point Card |  |
| --- | --- |
| Number Of Cards | Total Number of Spare Points |
| 1 | 2 Points |
| 2 | 4 Points |
| 3 | 6 Points |
| 4 | 8 Points |
| 5 | 10 Points |
| 6 | 12 Points |

- 8   Point Card Spare I/O Requirements

| 16 Point Card |  |
| --- | --- |
| Number Of Cards | Total Number of Spare Points |
| 1 | 3 Points |
| 2 | 6 Points |
| 3 | 9 Points |
| 4 | 12 Points |
| 5 | 15 Points |
| 6 | 16 Points |

- 16   Point Card Spare I/O Requirements

#### The spare I/O point placement is based upon the total number of spare points.  As an example if a PLC contains two 16 point cards a total of 6 spare I/O points are required.  These 6 spare points can be spread across the 2 cards as the Consultant deems necessary.

#### Halton Region’s preference is to group similar device I/O together on the same card rather than spread it across two cards.  As an example, all discrete inputs for a pump should be found on the same digital input card.

#### The consultant must obtain approval from Halton Region when specifying less than the required number of spare I/O points, particularly when the strict observance of the spare count marginally adds another card (for example a spare I/O count with spares that equals 17 discrete points).

#### Halton Region has specific requirements on the placement of spare field terminal blocks.  Field terminal block placement is discussed in, “Strategic Field Terminal Block Placement.”

#### Spare I/O points to be distributed strategically across the I/O cards.

### I/O Card Layout Requirements

#### Halton Region has established I/O card layout design principals.  These guidelines minimize process failure, in the event that one I/O card fails.

##### Similar I/O points for individual devices are to be grouped in a consistent order.

##### Similar devices should be spread between I/O cards (Pump 1 on Card 1 and Pump 2 on Card 2).

##### Devices which operate together (such as a pump 1 and pump 1’s valve) should have their I/O grouped on the same card.

##### Devices which are common to multiple pieces of equipment (such as a common flow control valve) should not be tied to the same I/O cards as the devices they are controlling (Pump 1 on Card 1, Pump 2 on Card 2 and Common Flow Control Valve on Card 3).

### Strategic Spare Slot Placement

#### Spare slots need to be strategically placed within the ControlLogix chassis.  Spare slots should be placed between card groups, such that one slot can accommodate any one of two (2) adjacent future I/O modules, without a break in the overall I/O layout.

#### The following table presents an example using a 10 slot chassis.

| Slot | Card |
| --- | --- |
| 0 | 1756-Processor |
| 1 | Communication card |
| 2 | Digital Input |
| 3 | Digital Input |
| 4 | Spare |
| 5 | Digital Output |
| 6 | Analog Input |
| 7 | Analog Input |
| 8 | Spare |
| 9 | Analog Output |

- Strategic Spare Slot Placement

#### In this example, Slot 4 could be used for either a future Digital Input or a Digital Output, and the I/O layout would continue to flow in the same order.  The same is true for Slot 8.  Slot 8 can be used for either an Analog Input or an Analog Output.

### Strategic Field Terminal Block Placement

#### Halton Region has standardized that all PLC panels are to be provided with spare field terminal blocks or interposing relays to accommodate one future I/O module of each type.  The spare terminals and interposing relays are to be placed with similar I/O types to allow for continuous I/O flow.

#### The placement of the spare field terminal blocks and interposing relays should reflect the chassis I/O layout.  When a spare slot separates two different types of I/O modules, the placement of the spare terminal blocks and interposing relays should reflect the possibility that either type of module can be placed in the spare slot.  Spare terminal blocks for the I/O module type to the left of the spare slot should be placed after the last group of field terminal blocks or interposing relays for that module type.  Spare terminal blocks to the right of the spare slot should be placed before the first group of field terminal blocks or interposing relays for that module type.  This allows for continuous I/O flow when either type of I/O module is added to the PLC.

### Terminal Block Group Labeling

#### Field terminal block groups should be labeled by Rack and Slot.  As an example, the Digital Input Terminal Blocks for the card installed in Rack 0 Slot 2, should be labeled as “R0S2.”

#### Spare Terminal block groups for Compact Logix PLC’s are installed in the same manner as ControlLogix.  The spare groups however are not label by Rack and Slot.  As CompactLogix do not have spare slots and have limitations to the number of cards in a Rack, future cards will be installed as the consultant deems necessary.  As such, the spare I/O groups will be label “DI” on one side and “SPARE” on the other.  This provides the flexibility to add cards to the new terminal blocks regardless of the final card placement.

  - Wire Labeling Standards

#### Halton Region’s wire labeling system is built on a scheme that uses the PLC, I/O type, rack, slot point and polarity to build the wire label. This scheme applies to both the internal panel wiring and the field wiring associated with the I/O points with a few exceptions as outlined below.

#### Section 1 contains sample loop drawings which clearly demonstrate the wire labeling system.  Consultants should refer to these drawings as they assist in understanding Halton Region’s wire labeling standards.

#### The wire labels on the loop drawings are linked to the slot and rack numbers so that when the slot and rack number are changed on the drawing, the wire labels automatically update.

#### There are 2 categories of wires in PLC panel. They are I/O loop wires and internal panel wires. The I/O loop wires can be broken into 2 sub-categories. They are internal loop wires and field loop wires. Each one of these categories of wires has its own wire labeling standard although they are very similar with only 1 difference.

#### Internal panel wires are wires that start and end inside the panel but are not part of the I/O loops in the panel.

#### Internal loop wires are wires that are part of the I/O loop. They run from terminal blocks inside the PLC panel to the PLC I/O cards.

#### Field loop wires are wires that are part of the I/O loop. They run from external field devices into the PLC panel and terminate on terminal blocks inside the PLC panel.

### Loop Wire Labeling

#### The Table below outlines how the loop wire labels are generated for both internal loop wires and field loop wires.

|  |  | #### Fragment 1 | #### Fragment 2 | #### Fragment 3 | #### Fragment 4 | #### Fragment 5 | #### Fragment 6 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| #### Signal Type | #### Wire Type | #### PLC Name | #### I/O Type | #### Rack Number | #### Slot Number | #### Point | #### Polarity |
| #### Digital Input | #### Internal | #### N/A | #### I | #### 0, 1, 2, 3 | #### :0 - :XX | #### /0-/16 | #### /A or /B |
|  | #### Field | #### XXX: | #### I | #### 0, 1, 2, 3 | #### :0 - :XX | #### /0-/16 | #### /A or /B |
| #### Digital Output | #### Internal | #### N/A | #### O | #### 0, 1, 2, 3 | #### :0 - :XX | #### /0-/16 | #### /A or /B |
|  | #### Field | #### XXX: | #### O | #### 0, 1, 2, 3 | #### :0 - :XX | #### /0-/16 | #### /A or /B |
| #### Analog Input | #### Internal | #### N/A | #### I | #### 0, 1, 2, 3 | #### :0 - :XX | #### .0-.16 | #### +/- |
|  | #### Field | #### XXX: | #### I | #### 0, 1, 2, 3 | #### :0 - :XX | #### .0-.16 | #### +/- |
| #### Analog Output | #### Internal | #### N/A | #### O | #### 0, 1, 2, 3 | #### :0 - :XX | #### .0-.16 | #### +/- |
|  | #### Field | #### XXX: | #### O | #### 0, 1, 2, 3 | #### :0 - :XX | #### .0-.16 | #### +/- |

- Wire Label Fragments

Where:

###### XXX	Denotes the 3-character code for the PLC name

###### Fragment 1 – is a 3-character code based on the Section 2 Tagname Convention which identifies the name of the PLC. The following ‘:” is used as a separation between fragments 1 and 2.  Note for internal wires, the name of the PLC is not used in the wire label

###### Fragment 2- Identifies Input or Output.  Inputs are identified by “I”; outputs are identified by “O”.

###### Fragment 3- Identifies the Rack Number.

###### Fragment 4- The leading “:” is used as a separation between fragments 3 and 4.  The Number indicates the slot in the rack.

###### Fragment 5- The leading “/”is used as a separation between fragments 4 and 5 for digital I/O, whereas for analog I/O, the leading “.” is used. The number identifies the point on the card.

###### Fragment 6- The leading “/”is used as a separation between fragments 5 and 6. Discrete loops also contain an “A” or “B,” so the whole fragment will read “/A” or “/B”. The “/A” represents the first field wire to the device.  The “/B” represents the second field wire to the device.  The “/A” and “/B” should also align with the polarity wires from the internal panel wiring. Analog loops use a “+” and “-” to indicate polarity.  The “+” identifies the positive wire in the loop.   The “-” identifies the negative wire in the loop.

#### Below are some examples of the different types of wire labels in a control panel.

| #### Signal Type | #### Wire Type | #### Wire Label |
| --- | --- | --- |
| #### Digital Input | #### Internal | #### I0:4/1/A digital input, rack 0, slot 4, point 1, positive or line (L) wire |
|  | #### Field | #### OWJ:I0:4/1/B Oakville high lift PLC, digital input, rack 0, slot 4, point 1, negative or return to PLC panel wire |
| #### Digital Output | #### Internal | #### O0:4/1/A digital input, rack 0, slot 4, point 1, positive or L wire |
|  | #### Field | #### OWJ:O0:4/1/B Oakville high lift PLC, digital input, rack 0, slot 4, point 1, negative or return to PLC panel wire |
| #### Analog Input | #### Internal | #### I1:9.1+ Oakville high lift PLC analog output on rack 1, slot 9, point 1, positive wire |
|  | #### Field | #### OWJ:I3:9.1- Oakville high lift PLC analog output on rack 3, slot 9, point 1, negative wire |
| #### Analog Output | #### Internal | #### O0:9.8+ Oakville high lift PLC analog output on rack 0, slot 9, point 8, positive wire |
|  | #### Field | #### OWJ:O0:9.3- Oakville high lift PLC analog output on rack 0, slot 9, point 3, negative wire |

- Wire Label Examples

#### Halton Region has standardized on a colour coded multi-conductor cable for the DI and DO points. See the related I/O loop drawings in section 1 for more details on the specifics of the cable. Halton Region has standardized on a multi-conductor cable for all analog inputs and outputs. See section I/O loop drawings in Section 1 for cable make and model.

#### Power wires for digital input loops are labeled based upon the circuit breaker they receive power from.

#### Internal panel wiring is the same for both treatment plants and remote stations as the PLC name is not required on internal panel wires.

#### The PLC I/O address is broken up into 5 fragments, indicating the I/O address on the PLC that the point is connected to.

#### A power wire is labeled as the circuit breaker label within the panel.  An example would be CBR101.   This indicates that there is a circuit breaker within the ICP labeled CBR101.

#### The internal panel wire uses the same label at both the field terminal block and on the PLC card.

#### Where field junction boxes are installed, all wires shall be labeled, on both sides of the junction.  Refer to the Water, Wastewater and Solid Waste Facilities Design Manual for more information.

#### All Cable to be Belden 8619 Multi-Conductor – Audio, Control and Instrumentation Cable.

#### Individual Multi-Conductor cables shall be labelled as per corresponding Rack and Slot number. As an example, the Digital Input Terminal Cables for the card installed in Rack 0 Slot 2, should be labeled as ―R0S2. These labels should be attached to the PVC outer jacket of the cable, a maximum of 3 cm beyond the Heat Shrink as described in point #5 below and arranged so that they are visible when the wire duct cover is removed.

#### Individual conductors in the cable are to be labelled as per current Region of Halton Standards.

#### No part of the PVC outer jacket of the cable shall be visible outside of the wire duct. All cables to have the outer jacket removed far enough back so that only the individual conductors extend beyond the wire duct.

#### Cables are to have Heat Shrink placed at both points of the PVC jacket removal. Please use a minimum of 3 cm of heat shrink with 1.5 cm covering the PVC and 1.5 cm covering the conductors.

#### All spare conductors are to be left long enough to reach the furthest reaching terminal block in the group and the furthest reaching terminal on the PLC card. These conductors are to be labelled as “SPARE”. Spare conductors are to be folded back onto the corresponding cable, unstripped, and tie-wrapped to the cable.

#### Colour code chart for both Digital Input and Digital Output Control Logix cards.

| Terminal Number | Conductor Colour |
| --- | --- |
| 0 | Black |
| 1 | White |
| 2 | Red |
| 3 | Green |
| 4 | Orange |
| 5 | Blue |
| 6 | White/Black |
| 7 | Red/Black |
| 8 | Green/Black |
| 9 | Orange/Black |
| 10 | Blue/Black |
| 11 | Black/White |
| 12 | Red/White |
| 13 | Green/White |
| 14 | Blue/White |
| 15 | Black/Red |
| Spare | White/Red |
| Spare | Orange/Red |
| Spare | Blue/Red |

- Conductor Colour Guide

      - Color code for panel wiring shall be as follows:

      - Line and load circuits 120 VAC power - 1 phase	Black (Hot) - White (Neutral)

      - DC Input Field Wiring	Red (Both wires)

      - DC Output Field Wiring	Yellow (Both wires)

      - DC control circuits	Red (+) Dark Blue (-)

      - Analogue Twisted Pairs	Red (+) and Black (-)

      - DC signal grounding conductors	Dark Green

      - Equipment grounding conductors	Light Green

      - Foreign source interlock control circuits	Yellow

      - Intrinsically safe circuits	Light Blue

## Tender Specifications

#### Control Panel Enclosure

##### Enclosures shall be NEMA 12 classification, unless site conditions dictate otherwise, sized as required, and be equipped with a front access door. Enclosures shall be complete with all instruments, meters, control switches, indicating lights, programmable control I/O modules, power supplies, wiring terminals and other devices as required.

##### Enclosures shall be fabricated of high grade cold rolled sheet steel, 12 gauge/2.78 mm

##### All doors and edges shall be neatly turned in and smooth finished. No visible welding seams will be accepted.

##### Enclosures shall be rigidly braced and stiffened to prevent any "bowing" or deformation during shipping or installation.

##### Unless otherwise indicated, doors on freestanding enclosures are to be flush fitting, gasketed, hung on concealed or piano type hinges and provided with a 3-point latch and locking type handle.  Doors on wall-mounted enclosures shall be gasketed and provided with quarter-turn screwdriver latches.

##### Enclosures shall be fitted with an interior, removable 2.7 mm thick steel equipment mounting back-plane.

##### Cutouts for panel-mounted equipment are to be neatly cut, properly aligned and sized so that the hole is completely covered by the front bezel.  Equipment and instrument cases shall preferably be held in place by rear connected fittings. Any front fixing required shall be only by means of chrome-plated machine screws.

##### Enclosures shall be completely dead front type with flush panel mounted equipment having back connection terminals.  Instrument bezels and switch escutcheon plates shall be a matched colour, suitably blending with the colours of the control panel.

##### Panel enclosures shall be smooth, free of sharp edges and blemishes, and thoroughly degreased before finishing.  All interior and exterior surfaces shall receive no less than two (2) coats of an approved undercoat applied over an approved rust-inhibiting prime treatment.  The factory applied finish shall comprise of no less than two (2) coats of a satin-finish, high quality, air-dried enamel having proven durability and resistance to abrasion.

#### Outdoor Site Control Panel Outer Enclosure

##### Outdoor site control panel outer enclosure shall be NEMA 4 classification, unless site conditions dictate otherwise, sized as required, and be equipped with a front access door.

##### Outdoor site control panel outer enclosure material shall be stainless steel, 12 gauge/2.78 mm.

##### Installation of heater is required on outdoor site control panel and meet the requirements in section 3.7.4.f. that will maintain the control panel inside temperature above 4Deg.C.

#### Wall Mounted Enclosures — Steel

##### In addition to the NEMA standards, meet the following requirements:

###### 14-gauge minimum metal thickness

###### Doors shall be rubber-gasketed with continuous hinge.

##### Where enclosures are mounted outside or in unheated areas, provide them with thermostatically controlled heaters that will maintain the inside temperature above 4Deg.C.

#### Wall Mounted Enclosures — Fiberglass

##### In addition to the NEMA standards, must meet the following requirements:

###### Hinge doors on the left side and equip with quick release latches.  Provide fiberglass reinforced polyester latches and hinges.

###### Provide heaters as for wall mounted steel enclosures.

#### Enclosure Options - Based upon the application, not all options are required.  The consultant shall review this list and design their panel in an application specific manner.  The following listing details options that may be required for certain applications.  When uncertain, the consultant shall check with Halton Region for requirements.

##### Window Kits:

###### Provide window kits suitable for NEMA type 4 and type 12 enclosures as specified in the schedule or panel drawing.

###### Provide windows with 0.6 cm clear acrylic with steel frames. Use stainless steel frames and polycarbonate window for NEMA type 4X enclosures.

###### Provide an oil resistant gasket to ensure a watertight seal around the window and window frame.

###### Provide window kits in a variety of sizes ranging from 7.5 cm by 12.5 cm, to 60 cm by 91 cm.

##### Louvers:

###### Include washable aluminum air filters with louvers used for ventilation.

##### Fans:

###### Fans require thermostat control.

###### Provide exhaust ventilation fans, where used, with washable, aluminum air filters and finger guards.

###### Operate fan motors on 115 VAC, 60 Hz power.  Include thermal protection. Use motors rated for 20,000 hours of continuous operations without lubrication or service.

###### Provide intake grilles with filters.

##### Closed Loop Air Conditioners:

###### Provide closed loop cabinet air conditioners as specified in the schedule or panel drawing.

###### Meet the following requirements:

            - Power:	115 VAC, 60 Hz.

            - Mounting:	Vertical on side or back.

            - Capacity:	1,200 to 10,000 BTU per hour as required by the cabinet equipment.

###### Provide special coatings on coils and copper lines to reduce corrosion damage.

##### Heaters for Condensation Control

###### Provide thermostatically controlled, fan-driven heaters for all outdoor enclosures for condensation control unless otherwise specified.

###### Meet the following requirements:

            - Power:	115, VAC, 60 Hz.

            - Rating:	100 Watts for panels smaller than 61 cm by 122 cm.

            - 200 Watts for larger panels

###### Provide thermostats that sense air temperature in the panel and are adjustable from 4 to 25C.

###### Mount heaters near the bottom center of the enclosure.  Do not mount electronic components closer than 15 cm to the heater.

##### Heaters for Freeze Protection

###### Provide thermostatically controlled heaters for freeze protection as specified in the schedule or panel drawing.

###### Meet the following requirements:

            - Power:	115 VAC, 60 Hz.

            - Rating:	100 Watts for panels smaller than 25 cm by 41 cm.

            - 150 Watts for panels smaller than 31 cm by 62 cm

            - 250 Watts for panels smaller than 46 cm by 76 cm

            - 500 Watts for panels smaller than 61 cm by 122 cm

##### Moisture Protection

###### Self-regenerating desiccant or equivalent, in heat-sealed, semi-permeable packet, Humidisorb by A+ Corporation.  Provide the size and number of packets needed to protect the size of panel.

###### Self-regenerating desiccant or equivalent, with vapour corrosion inhibitor in heat-sealed, semi-permeable packet, Humidisorb Plus X-Corrode by A+ Corporation. Provide the size and number of packets needed to protect the size of panel.

##### Drip shields

###### Free standing enclosures mounted outdoors shall have a drip shield.

#### Indicator Lights

##### Indicator lights shall be heavy duty oil-tight type with back mounted screw terminals suitable for operation as indicated on the drawings, and as outlined below:

###### Local Control Panel indicators to be 30.5 mm full face, LED type, push to test function.  Lens colour and engraving as indicated.

#### Pushbuttons and Control Switches

##### Pushbuttons and control switches shall be heavy duty, oil tight type with multi-element stackable contact blocks with side wired screw terminals.  Contact arrangements and configurations as required.

##### Unless indicated otherwise, pushbutton operators shall be momentary contact type, flush head construction; black in colour.  Backlit type pushbuttons shall have lens colour and engraving as required.

##### Rotary operators shall be two, three or four position, maintained or momentary contacts as required.

##### Illuminated operators shall have clearwing style operator toggles, with internal indicating lamp, lamp voltage as required for the application.

##### Each device shall be fitted with an operation identification   plate.

##### Pushbuttons and control operators shall generally be provided as follows:

###### Pushbuttons to be 22.5 mm full-face operator type with engraving as required.

###### Control Switches to be a 30.5 mm two, three or four position multi-pole as required, c/w Type 12 or 13 enclosure, and nameplate escutcheon engraving as required.

##### The following colours shall be used for indication lights:

Running			-	Red

Off				-	Green

Opened			-	Red

Closed			-	Green

Overload			-	Amber

Fault			-	Amber

Control Power Available	-	White

#### Ozone Gas Alarm		-	Blue Relays

##### Interposing Relays for Digital Outputs shall be SPDT.  The relay coil must draw a minimum of 10 mA and must not be able to turn on if less than 3 mA’s is applied to the coil.  Therefore, when 120 VAC is being used for the output, the minimum input impedance should be 12 K Ohms.

##### Control relays shall be of the plug-in, encapsulated type.  Relay pole configurations shall typically be 3PDT.  Relays shall be equipped with internal neon pilot indicators.  Coil voltage shall typically be 120 VAC 60 Hz and contacts shall be rated for 5 Amps.

##### Relay bases shall be of molded unbreakable nylon/plastic construction, configured for screw or DIN rail mounting.  Terminal screws shall permit connection of up to 2 #12 AWG conductors per terminal.

#### Timer Relays

##### Timer relays shall be solid-state digital display, multiple range, programmable operation, and plug-in encapsulated assembly.

##### Timer operating configuration shall be as required. Output contacts shall be DPDT rated 3A, 250 VAC.  Supply voltage shall typically be 120 VAC.

##### Relay bases shall be of molded unbreakable construction, configured for screw or DIN rail mounting.  Terminal screws and pressure pads shall permit connection of up to two #12 AWG conductors per terminal.

#### Power Failure Relay

##### Provide a power failure relay installed in each PLC Panel.  The relay shall be connected to the main power supply to the panel (typically a 120 VAC branch circuit), and shall indicate loss of supply power to the panel, while the panel components operate on the standby UPS.

#### Intrinsically Safe Relay

##### Where required by application, the contactor shall provide intrinsically safe relays.  Relays shall be dual channel.

#### Electronic Digital Indicators

##### Electronic digital indicators shall be provided for panel installation as required, for display of identified process variables or quantities.

##### Indicators shall be powered by 120 VAC, and input signal shall be 4-20 mA.

##### Indicators shall be 3 1/2 digit LED type, minimum height 25 mm numbers, with adjustable decimal point.

#### Current Loop Isolators (I/I)

##### Input signal:		4-20 mA

##### Output Signal:		4-20 mA

##### Input Impedance:		250 ohms maximum

##### Output Load Capability: 	1,000 ohms

##### Power Supply:		120 VAC

##### Accuracy/Linearity:	0.1%/0.1% of span

##### Mounting:			DIN Rail.

#### Intrinsically Safe Barriers

##### Where required, the contractor shall provide intrinsically safe barriers for 4 – 20 mA loops.

#### Loop Power Supplies

##### Loop power supplies shall be provided within control panels for supply of two (2)-wire transmitter analog circuit loops as indicated on the drawing. The quantity of power supplies and separate isolated supply potentials shall be as required for the circuits indicated.

##### Output voltage shall be nominally 24 VDC with a minimum circuit current capability of 2 ADC.  Output shall be regulated and crowbar protected.  Voltage accuracy, regulation noise and ripple shall be within limits to ensure that the powered instruments can be operated to their specified tolerances.  Barrier output terminals shall be provided with circuit number and polarity clearly identified.

##### Input voltage shall be 115 V, 1- ph, 60 Hz AC.

#### Uninterruptable Power Supplies

##### These specifications must be read in conjunction with the approved equipment list to ensure the current approved equipment is specified. In general, the preferred UPS is Eaton Model 9SX.

##### UPS’s which are installed within a panel are to be tower models.  Rack mount UPS’s are to be rack mount models.

##### UPS’s to be supplied with a relay card for PLC monitoring of Low Battery and UPS fault.

##### Halton Region’s guideline is that the UPS should be able to maintain all UPS powered equipment for a minimum of 30 minutes, based upon normal operating power consumption (80% load).

#### When 2000 VA UPS’s are supplied, the Consultant must specify that the simplex UPS feed receptacle be NEMA 5-20R.

#### Control Panel Power Distribution

##### Circuit breaker terminal blocks for sub-circuit power supplies shall be rated as required by the hardware or field devices for manufacturer's recommended protection.

##### Control Panels shall be provided with a 120 VAC supply from circuit distribution panel.

#### Terminal Blocks

##### Terminal blocks shall be provided c/w mounting rails or channels for connection to field device wiring.  Terminals shall be tubular clamp type, 6 mm, rated at 600 volts with the current rating being equal to the maximum current rating of the conductors but not less than 10A.

##### Terminals shall be easily accessible for attachment of field connections.  Each terminal shall be clearly marked with factory pre-marked number and/or letter tag identifiers.  Each field-connecting conductor shall be served by one terminal.

##### Terminal block groups shall be clearly marked with printed group labels.

##### Ground terminal blocks require bonded grounds. Use jumper bars rather than jumper wires between ground blocks.

#### Internal Component Identification

##### Each internal panel device or instrument shall be fitted with a permanent nameplate with the device identification imprinted.  The nameplate shall be located adjacent to the device, on the Panel wall or backplane.  Nameplates may not be placed on components or Panduit covers, as these can be removed or lost.

#### Panel Faceplate Device Identification

##### Panel face devices shall be provided with lamacoid nameplates, black with white lettering.

##### Final nameplate wording, colouring and sizes shall be approved by Halton Region.

#### Surge and Lightning Protection

##### Supply and install in the PLC panel lightning and surge protection equipment to suit incoming Bell Canada lines.

##### Provide proper isolation for any wire which connects between two buildings.

##### RF grounding and bonding to meet all safety requirements; as a source of information, refer to the UL Standard 497B.

#### Transient Voltage Surge Suppressor

##### Each Instrument Control Panel shall have one TVSS installed.

##### Each TVSS shall come equipped with an integrated circuit breaker with external disconnect.

##### The TVSS shall be installed on the main incoming power source from the lighting panel, after the main disconnect circuit breaker, and before any other electrical source.

#### Component Installation

##### The contractor is responsible for the general arrangement of components to be installed.  Equipment shall be mounted to ensure adequate clearance between door mounted and back-plane mounted components with the panel door closed.  All items shall be clearly identified with an engraved lamacoid nameplate securely fastened in place.

##### The UPS should not obstruct terminal blocks, nor prevent access for maintenance and troubleshooting.

##### All internally mounted equipment shall be arranged for ease of access and removal when necessary.  Flexible wiring harnesses with approved terminating connectors at both sides shall be provided for any hinged panel or door-mounted equipment and each shall have 20% spare capacity.

##### The panel shall be provided with a tapped copper bus bar for panel components and shield grounding, plus 20% spare.

##### Relay base and terminal block rails shall be located square to the back plane.  Door mounted instruments shall align horizontally and vertically on edges or centerlines.

##### Fastening of equipment assemblies to the panel back planes shall be by means of appropriately sized drilled and tapped screw holes.  Machine screws only with lock washers are to be used; self-tapping hardware is not acceptable.

##### Provide corrosion protection for each panel.

#### Wiring Methods

##### All discrete field I/O wires must contain 2 wires for the loop.  The practice of running one common wire for each input will not be accepted.  Refer to Halton Region’s template drawings in this section for Halton Region’s wiring standards.

##### All wiring shall be neatly formed and adequately supported.  Wire ducts 3” deep shall be installed beside all terminal strips and PLC I/O.  A primary requirement will be neatness.  No splices will be allowed.  All wiring shall be installed continuous from terminal to terminal.

##### Each wire termination at a stud shall have a fork type crimp-on connector.  All wiring terminating at tubular screw terminals shall be stripped for full insertion into the terminal.  Wiring termination at solder terminals shall be mechanically secure before solder is applied.  Resin type solder shall be used.

##### Wire looms shall be secure and wire forming shall provide enough length to ensure that there will be no mechanical tension on wire terminations.

##### Wires installed at terminal blocks shall be at right angles to the terminal and have adequate spare length to reach up to 4 terminal blocks either side of the termination point.

##### Mechanical checks shall be made to determine if there are any broken parts, wires, mechanical binding, loose screws, and proper soldered connections.  Mechanical tolerances shall be checked on all units including contact grip and wires.

##### Each panel shall be bonded to the building ground system.

##### Isolated DC Ground

###### The analog DC and digital DC power supply "-" connection (0 VDC) shall be connected to a single star ground point referred to as the "Isolated DC Ground" located within the PLC panel.  This is typically implemented using a copper bus bar on insulated stand-offs located near the bottom of the controller cabinet.  This bus bar shall be identified as the "Isolated DC Ground." This bus shall be tied by only one 8 AWG ground wire, which runs directly from the bus bar to the lowest potential building or system ground available (typically the building frame or buried grounding grid.)  Simply tying this ground via the AC System Ground bus bar should be avoided. The grounding cable from the Isolated Ground DC bus bar to this ground point shall not serve any other purpose.

###### Field device enclosures must not be bonded to the Isolated DC Ground.

###### Instrument shields shall not be bonded to the AC ground at the instrument.

###### Instrument shields shall be connected to the “Isolated DC Ground.”

###### Wiring conductors connected to the Isolated DC ground shall be labeled and coloured in accordance with their loop function (i.e., with a "-" suffix as described below), or shall be dark green in colour and labeled as "DC GND."

##### AC System Ground

###### The AC System ground is the principle ground for the SCADA system.  It originates from the supply transformer neutral.

###### This AC System ground is typically implemented using a copper bus bar on non-insulated stand-offs located near the bottom of the controller cabinet.

###### All cabinets and bonding shall be grounded to the AC system ground.

###### Wiring conductors connected to the AC System Ground shall be labeled and coloured in accordance with their loop function (i.e. with a "G" suffix as described below), or shall be light green in colour and labeled as "AC GND."

###### No UPS system shall interrupt the ground.

##### AC Isolated Ground

###### Use of an AC Isolated Ground should be avoided unless the UPS or power conditioner manufacturer installation instructions require it.