Regional Municipality of Halton

SCADA Standards Manual

Section 7 Supplemental SCADA Programming

SCADA STANDARDS 2022

Table of Contents

SECTION 7 SUPPLEMENTAL SCADA PROGRAMMING	1

7.1	Introduction	1

7.2	Burlington Water Purification Plant Custom Features	1

7.3	Burloak Water Purification Plant Custom Features	1

7.4	Oakville Water Purification Plant Custom Features	1

7.5	North Water Custom Features	1

7.6	Water Distribution Custom Features	1

7.7	Acton Wastewater Treatment Plant Custom Features	3

7.8	Oakville South West Wastewater Treatment Plant Custom Features	3

7.9	Oakville South East Wastewater Treatment Plant Custom Features	3

7.10	Mid Halton Wastewater Treatment Plant Custom Features	3

7.11	Georgetown Wastewater Treatment Plant Custom Features	3

7.12	Skyway Wastewater Treatment Plant Custom Features	3

7.13	Waste Collections Custom Features	3

7.14	Biosolids Customs Features	3

7.15	Landfill Custom Features	5

# SUPPLEMENTAL SCADA PROGRAMMING

## Introduction

#### The intent of this document is to identify and describe custom features that are unique to one particular SCADA application or system. This document is organized such that there is a dedicated section for each of the 14 InTouch applications.

#### Should consultants identify a discrepancy between this section and other sections of the SCADA Standards Manual, they should notify Halton Region in writing.

## Burlington Water Purification Plant Custom Features

## Burloak Water Purification Plant Custom Features

## Oakville Water Purification Plant Custom Features

## North Water Custom Features

## Water Distribution Custom Features

#### Reservoir Level Switches

#### Each reservoir in the water distribution system has high and low level capacitance switches that should be set outside the alarm range of the level transmitter. These switches generate alarms and force the value of the level transmitter to its maximum or minimum depending on the active level switch. Additionally, level switches can trigger interlocks for pumping to or from the affected reservoir.

#### PLC Data Extraction

#### The only values that are to be stored in the PLC and extracted are chlorine residuals and all clearwell and reservoir levels. These values are to be recorded every 15 minutes and are stored for 5 days.

#### Pump Override Logic

The purpose of the pump override logic is to force water to move up to the higher pressure zones in the event that the levels in the receiving reservoirs are not calling for a pump to start. For instance, if Headon reservoir is at 80% and the Duty 1 start setpoint at Washburn is at 78% the pump at Washburn will not start. This is a problem if the Washburn Reservoir is nearing its fill capacity as this would cause the BWPP to shut down. In this event, the secondary pump override logic would kick in. This logic states that if the Washburn reservoir is above 90% full and the Headon Reservoir is below 90% full then start a Washburn Zone 3 pump. Continue to pump until either Headon reaches 90% full or Washburn drops to a stop setpoint. There is no standard logic for the pump override logic as each site will have unique process considerations. For instance, Washburn Zone 3 forced start cannot take place if Washburn is in Tyandaga night fill mode. Therefore, a decision must be made to prioritize forced start or night fill mode. These decisions are to be made in conjunction with operations on a site-by-site basis. Below is the setpoint screen for Washburn Pumping Overrides as an example. The setpoint screen must include an explanation of how the system works.

#### Unique Pumping Rules

#### Duty pump 1 and 2 start or stop setpoints can be the same.

#### Two pumps in the same pressure zone cannot start or stop at the same time. If two pumps are called to start simultaneously, one pump will be started immediately, with the second pump starting following a 5-minute (default) delay timer. The delay time remaining is to be displayed in seconds near the pump graphic with text stating the delayed pump start or stop condition. This is only visible when the timer is active. The timer should be adjustable on the Zone setpoint screen by the supervisor only.

#### Additional Text standards

#### The capacity and elevation of every reservoir is to be displayed on the site screen as text. All hypo and diesel tanks are to have their capacities displayed as text only.

#### Consumption Calculations and Lake Based Volume Standards

#### Any time and a site is added or modified these calculations must be added or updated. These calculations are fully described in the South Operation Autodialer PLC PCN.

## Acton Wastewater Treatment Plant Custom Features

## Oakville South West Wastewater Treatment Plant Custom Features

## Oakville South East Wastewater Treatment Plant Custom Features

## Mid Halton Wastewater Treatment Plant Custom Features

## Georgetown Wastewater Treatment Plant Custom Features

## Skyway Wastewater Treatment Plant Custom Features

## Waste Collections Custom Features

## Biosolids Customs Features

#### Biosolids Management Facility Driver Authorization System

#### The Biosolids Management Facility driver authorization system is programmed to collect driver information, flow totals and number of pump starts.

#### The Drivers will login using the RFID readers placed nearby all physical pump controls for each of the tanks. The reader will evaluate if the user is within the database and is authorized for use of the local controls.

#### The Biosolids Management Facility driver authorization system utilizes an array from BFYRT01 to store/retrieve information to SCADA. The information that is stored is Driver Name, Company, and Tag ID.

Figure 10.41 – Biosolids Drivers Information Overview Display

#### The Biosolids Management Facility Driver Information Overview in Figure 10.41 provides a list of all drivers associated with the Biosolids Management Facility. Operations are able to add, edit or delete Driver Profiles, as seen in Figures 10.42 and 10.43.

Figure 10.42 – Biosolids Driver Information Add New Driver Display

#### The Add New Driver display indicated in Figure 10.30 allows users to create additional drivers.

Figure 10.43 – Biosolids Driver Information Add New Driver Logic

#### The Logic displayed within Figure 10.43 is used to add users within the arrays on BFYRT01. It looks at the last available index and based upon the new array from SCADA containing string file of (Driver, Company and Tag ID) the information is stored.

Figure 10.44 – Biosolids Driver Information Edit Driver Display

#### The Edit Driver display indicated in Figure 10.44 allows users to edit profiles of pre-existing drivers.

Figure 10.45 – Biosolids Delete Driver Logic

#### The Logic displayed within Figure 10.45 is used to delete the users within the arrays on BFYRT01. It evaluates which index is have selected on SCADA using the tag BFYID00ZIAO_CT. Based upon the index selected, the logic copies a blank array containing string file of (Driver, Company and Tag ID) to fill in the deleted index.

Figure 10.46 – Biosolids Driver Evaluation Logic

#### The Logic displayed within Figure 10.46 is used to verify active users within the driver database. The users will swipe their RFID tags at the local controls and the logic verifies the Tag ID associated. Once the users are authenticated, local controls are activated.

## Landfill Custom Features