Regional Municipality of Halton

SCADA Standards Manual

Well Monitoring Equipment, Installation, and Commissioning Specifications

SCADA STANDARDS 2022

Table of Contents

SECTION 1 GENERAL REQUIREMENTS

1.1	Introduction	3

1.2	Major Components	3

Indoor installation on a Production Well	4

Outdoor Installation on a Monitoring well	4

1.3	Installation	4

1.4	PLC Code and HMI Graphics Details	4

Appendix A – Lindsay Court Pumping Station InTouch Window	5

SECTION 1 GENERAL REQUIREMENTS

## Introduction

.1 The purpose of this document is to provide the general intent and information required for the supply, installation, PLC programming and HMI graphics associated with measuring the level of an aquifer in the Halton Region. The intent of this document is to provide a degree of consistency among installations of aquifer level measuring equipment. The installation details, PLC programming, HMI configuration, trending, and alarming are to follow the guideline set in this document. While this document is intended to cover most typical installations, some deviations may be required to accommodate special requests or site-specific conditions.

.2 This document assumes that the well has already been constructed and the person performing the PLC and HMI programming is familiar with Halton’s SCADA System Design Standards. Any information that is not part of the standards will be provided in this document.

.3 There are 2 primary types of wells. The first is a well which is drilled and a level-monitoring device has been installed in the well. This type of well is used specifically for monitoring the level of the aquifer under the area of the well and is referred to as a Monitoring Well.

.4 The second type is a Production Well. This type of well has a pump installed in it and the primary purpose is to remove water from the aquifer and pump it through the treatment process and into the distribution system. Equipment can be installed in the production well that allows the level of the well to be monitored.

.5 It is assumed in this document that in either type of well, the level measuring device will be connected into the nearest PLC and the level constantly monitored by the SCADA system.

## Major Components

.1 Below is a list of the major components that are to be included and used in the installation. It is the intent to standardize these installations as much as possible. Doing so will minimize the number of spare parts which need to be stocked, provide the flexibility of interchanging components from one installation to another, and reduce the required knowledge of components from multiple vendors.

.2 Monitoring wells can be located either indoors or outdoors. The outdoor installations require special consideration to make them both weather and vandal resistant.

# Indoor installation on a Production Well

1. Druck Depth/Level Pressure Transmitter Model PTX 1230

2. Eaton Innovative Technologies Surge Protection Device OEM Model

3. 4” x 4” Watertight PVC junction box

4. Analog Input Card appropriate for PLC on site.

# Outdoor Installation on a Monitoring well

1. Druck Depth/Level Pressure Transmitter Model PTX 1235 with internal lightning protection.

2. Eaton Innovative Technologies Surge Protection Device OEM Model.

3. 4” x 4” Watertight PVC junction box.

4. Analog Input Card appropriate for PLC on site.

5. Heavy gauge Steele Lockable well cover large enough to house the 4” x 4” Watertight PVC junction box.

## Installation

.1 The installation must be performed in a manner which provides easy access for removal and replacement of all components with particular attention to the transmitter. It must be able to be removed without removing any other devices, covers, guards etc. and without affecting the operation of the pump or the well.

.2 Cables should be run in protective conduits.

.3 The terminal strips on the Eaton Innovative Technologies Surge Protection Device OEM Model can be used as a termination point for the cables from the transmitter. The surge protector should be mounted on or close to the well to facilitate easy removal of the transmitter.

## PLC Code and HMI Graphics Details

.1 When a manual reading is taken at a monitoring well the distance from the top of the water to the reference point on the monitoring well is measured and not the actual depth of the aquifer. As this measured value increases it indicates that the depth of the water in the aquifer is decreasing and vice versa.

.2 The 4-20 mA signal from the Druck Depth/Level Pressure Transmitter represents the depth of water in the aquifer and not the distance between the top of the water to the to the reference point on the monitoring well. In order to align the value displayed on the HMI with the manual readings that are taken by an operator, the PLC code must invert the 4-20mA signal so that it represents the distance between the top of the water to the to the reference point on the monitoring well. Once the signal has been inverted, the 4-20mA signal can be treated like a typical analog signal and Halton’s standard analog signal PLC code driver applied.

.3 The HMI configuration consists of the following items: standard analog value display, standard analog pop-up, standard advanced analog pop-up, alarming configuration, and historical trending configuration.

.4 The standard analog value display, standard analog pop-up, standard advanced analog pop-ups are all part of Halton’s HMI standards and provide the required alarming functionality. Please refer to Section 6 - HMI Programming of the Halton standards for more detail. There is a further requirement to add a vertical display to the appropriate overview display for the site. In order for the HMI display to match the manual measurements that are taken by the operator, the HMI needs to be configured to display distance from the top of the water to the top of the well and not the depth of water in the well.  Samples of both a Production Well and a Monitoring well are provided for the Lindsay Court Pumping Station in Appendix A.

.5 The tag for the analog value needs to be configured to log data and a historical trend configured. As to whether a new historical trend window needs to be developed or the trend pen added to an existing window, the consultant should contact a member of Halton Region’s SCADA department for direction.

.6 Halton Region’s SCADA department is responsible for the management and maintenance of the associated PLC code and HMI standards. Before development on these is started, the developer should contact the SCADA department to ensure they have the latest standards.

### Appendix A – Lindsay Court Pumping Station InTouch Window